## Sheet1
Court_ID | Court_Name | Property_ID | Comp_ID | Property_Type | Fra_Date_of_Risk | Fra_Location | Fra_Carried_out_by | FormID_Text | Housing_Business_Stream | Housing_Region | Housing_Patch | Asset_Management_Region | Surveyor_Patch | RiskID_Text | FRA_Risk_Status | Risk_Open_or_Closed | Completed_Date_Of_Risk | Fra_Type | FRA_Section | Deadline_DateTime | Risk_RAG | Risk_Owner | Risk_Comments | Detail_of_action_taken_by_risk_owner
1001 | Devonshire Court | DEVONSHIRE_S001 | H21 | Scheme | 2022-09-14 14:26 | FRA_1001140920221424.pdf | BatesT | 1001140920221420 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | 13gk44muicnl81nmn1l | Observation Only | Risk Closed | 44851.4087 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Court Manager | Some flats still have perco closers. Whilst these are ok, they can not be adjusted. If adjustment is needed these should be changed for adjustable closers. | Replacing door closers when needed
1001 | Devonshire Court | DEVONSHIRE_S001 | H21 | Scheme | 2022-09-14 14:26 | FRA_1001140920221424.pdf | BatesT | 1001140920221420 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | 2r6d9wbas01l81nmmy6 | Medium Risk closed | Risk Closed | 44851.4034 | Obs8 | Measures To Limit Fire Spread And Development | 45183 | Medium | Court Manager | Lounge door wedged open on carpet | Shaved bottom of the door
1001 | Devonshire Court | DEVONSHIRE_S001 | H21 | Scheme | 2022-09-14 14:26 | FRA_1001140920221424.pdf | BatesT | 1001140920221420 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | 6nh0hb63g1rl81nnhvk | Low Risk closed | Risk Closed | 44845.603 | Obs6 | Fire Hazards - Elimination & Control | 45549 | Low | Court Manager | Some scooters not pat tested. | Booked pat test
1001 | Devonshire Court | DEVONSHIRE_S001 | H21 | Scheme | 2022-09-14 14:26 | FRA_1001140920221424.pdf | BatesT | 1001140920221420 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | gzgdwhmnlokl81nmmwn | Low Risk closed | Risk Closed | 44845.6075 | Obs7 | Fire Protection Measures | 45549 | Low | Court Manager | Keep locked door open | Locked door
1001 | Devonshire Court | DEVONSHIRE_S001 | H21 | Scheme | 2022-09-14 14:26 | FRA_1001140920221424.pdf | BatesT | 1001140920221420 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | hs2gv4xmxy9l81nmn3t | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45549 | Low | Court Manager | Running man missing by f2, f6 | NULL
1001 | Devonshire Court | DEVONSHIRE_S001 | H21 | Scheme | 2022-09-14 14:26 | FRA_1001140920221424.pdf | BatesT | 1001140920221420 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | lsbgto59vc9l81nmmz4 | Low Risk closed | Risk Closed | 44845.6122 | Obs8 | Measures To Limit Fire Spread And Development | 45549 | Low | Court Manager | Door opposite office not pulling to | Fixed seal
1001 | Devonshire Court | DEVONSHIRE_S001 | H21 | Scheme | 2022-09-14 14:26 | FRA_1001140920221424.pdf | BatesT | 1001140920221420 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | purabuoajeol81nmmzv | Low Risk closed | Risk Closed | 44851.4077 | Obs8 | Measures To Limit Fire Spread And Development | 45549 | Low | Court Manager | Door by f21 not pulling to | rubbing around door work man sorted
1001 | Devonshire Court | DEVONSHIRE_S001 | H21 | Scheme | 2022-09-14 14:26 | FRA_1001140920221424.pdf | BatesT | 1001140920221420 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | r5fbckx1kzl81nmn4r | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45549 | Low | Court Manager | Running man pointing left would be better suited for escape by f30 | NULL
1001 | Devonshire Court | DEVONSHIRE_S001 | H21 | Scheme | 2022-09-14 14:26 | FRA_1001140920221424.pdf | BatesT | 1001140920221420 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | y7r2muxtx5pl81nmn2m | Low Risk to be actioned | Risk Open | NULL | Obs9 | Escape Lighting | 45219 | Low | Surveyor | Escape lighting has on going faults and failures. Upgrade has been recommended. | NULL
1001 | Devonshire Court | DEVONSHIRE_S001 | H21 | Scheme | 2022-09-14 14:26 | FRA_1001140920221424.pdf | BatesT | 1001140920221420 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | yx0waew2url81nmn0n | Low Risk closed | Risk Closed | 44845.6135 | Obs8 | Measures To Limit Fire Spread And Development | 45549 | Low | Court Manager | Keep locked door by 31 open | Locked
1002 | Goodman Court | GOODMAN_S001 | H21 | Scheme | 2022-11-15 15:31 | FRA_1002151120221453.pdf | BatesT | 1002151120221450 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | zwg221y4pamlaic3r1y | Low Risk closed | Risk Closed | 44901.4941 | Obs5 | Evacuation Strategy And Training | 45611 | Low | Court Manager | CM Fire safety manager course is out of date, booked on refresherr. | completed fire training on 30/11/22
1002 | Goodman Court | GOODMAN_S001 | H21 | Scheme | 2022-11-15 15:31 | FRA_1002151120221453.pdf | BatesT | 1002151120221450 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | pj9sc4zor4laic3r2l | Low Risk closed | Risk Closed | 44901.4946 | Obs15 | Management Of Fire Safety | 45611 | Low | Court Manager | Staff training up to date, no records of it in red book. | Staff are now both up to date with training
1002 | Goodman Court | GOODMAN_S001 | H21 | Scheme | 2022-11-15 15:31 | FRA_1002151120221453.pdf | BatesT | 1002151120221450 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | mpaw4kn22elaic3r1a | Observation Only | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Other | Part 6 system could be extended to flat living rooms and beedrooms if false alarms becomes an issue. | NULL
1002 | Goodman Court | GOODMAN_S001 | H21 | Scheme | 2022-11-15 15:31 | FRA_1002151120221453.pdf | BatesT | 1002151120221450 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | 7p4vmrvitrllaidcfg9 | Medium Risk closed | Risk Closed | 44883.4974 | Obs6 | Fire Hazards - Elimination & Control | 45245 | Medium | Court Manager | Excessive storage of items in communal areas are not as neat or managed as they could be. Recomend sort / clear through | social worker collected items left from Christmas fayre on 16.11.22, I cannot take photos as now using Dell.so photo evidence sent in separate email.
1003 | Fulleylove Court | FULLEYLOVE_S001 | H21 | Scheme | 2022-06-15 15:42 | FRA_1003150620221536.pdf | BatesT | 1003150620221530 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | 7d7vjhjydcel4fp4jrp | Low Risk closed | Risk Closed | 44837.4854 | Obs8 | Measures To Limit Fire Spread And Development | 45458 | Low | Court Manager | Lounge door closer missing magnet and propped | Raised works order for completion of work
1003 | Fulleylove Court | FULLEYLOVE_S001 | H21 | Scheme | 2022-06-15 15:42 | FRA_1003150620221536.pdf | BatesT | 1003150620221530 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | era664tnrxml4fp4jqn | Low Risk closed | Risk Closed | 44867.4089 | Obs6 | Fire Hazards - Elimination & Control | 45458 | Low | Court Manager | Some buggies charging in communal area not showing evidence off pat testing. | Arranged all chargers to be PAT tested, now completed
1003 | Fulleylove Court | FULLEYLOVE_S001 | H21 | Scheme | 2022-06-15 15:42 | FRA_1003150620221536.pdf | BatesT | 1003150620221530 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | oxs1uottegl4fp4ju1 | Low Risk closed | Risk Closed | 44867.4117 | Obs15 | Management Of Fire Safety | 45458 | Low | Court Manager | No domestic staff noted in staff fire training | Supported Colleen to complete the training
1003 | Fulleylove Court | FULLEYLOVE_S001 | H21 | Scheme | 2022-06-15 15:42 | FRA_1003150620221536.pdf | BatesT | 1003150620221530 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | qi51ikdhkjl4fp4jsl | Low Risk closed | Risk Closed | 44775.5542 | Obs10 | Fire Safety And Notices | 45458 | Low | Court Manager | Running man sign required in buggy store | Sign replaced
1004 | Nicholson Court (Tideswell) | NICHOLSONTID_S001 | H21 | Scheme | 2021-12-07 16:00 | FRA_1004071220211528.pdf | BatesT | 1004071220211520 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | sjw9pge5dqnkww9kp6d | Low Risk closed | Risk Closed | 44657.3627 | Obs6 | Fire Hazards - Elimination & Control | 45267 | Low | Court Manager | Cable route from binstore to switch room needs additional fire stopping. | Repair requested for next contractor visit. Repair now carried out.
1004 | Nicholson Court (Tideswell) | NICHOLSONTID_S001 | H21 | Scheme | 2021-12-07 16:00 | FRA_1004071220211528.pdf | BatesT | 1004071220211520 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | tssz82secw8kww9vrxg | Low Risk closed | Risk Closed | 44592.5886 | Obs8 | Measures To Limit Fire Spread And Development | 45267 | Low | Court Manager | Flat door 21 doesn't fully pull to | Door has now been adjusted.
1004 | Nicholson Court (Tideswell) | NICHOLSONTID_S001 | H21 | Scheme | 2021-12-07 16:00 | FRA_1004071220211528.pdf | BatesT | 1004071220211520 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | ccs1lkd7mu3kwwa6dss | Observation Only | Risk Closed | 44578.6256 | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | Staff training and false alarms being logged online but not in red book. Recommend this is documented in red book also. | Going forward CM to log false alarms in red folder as well as logging on Erica.
1004 | Nicholson Court (Tideswell) | NICHOLSONTID_S001 | H21 | Scheme | 2021-12-07 16:00 | FRA_1004071220211528.pdf | BatesT | 1004071220211520 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | 7boyf2a7yurkww9ou2c | Observation Only | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Mobility scooter only one onsite within first 12 months of purchase. Pat testing required at 12 months. | NULL
1005 | Waltham House | WALTHAMHOUS_S001 | H21 | Scheme | 2022-10-04 16:09 | FRA_1005041020221449.pdf | BatesT | 1005041020221440 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | 0rrdmnavoool8uah93n | Observation Only | Risk Closed | 44853.5086 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Note only, no charging equipment available within scooter store | Reminded residents not to use it as a junk store
1005 | Waltham House | WALTHAMHOUS_S001 | H21 | Scheme | 2022-10-04 16:09 | FRA_1005041020221449.pdf | BatesT | 1005041020221440 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | 9wtglcu2h5vl8ub47ut | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45569 | Low | Court Manager | Cross corridor doors not closing fully, by F2, F18 and f37 | NULL
1005 | Waltham House | WALTHAMHOUS_S001 | H21 | Scheme | 2022-10-04 16:09 | FRA_1005041020221449.pdf | BatesT | 1005041020221440 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | nm9oh0b04nal8ub0c0e | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45569 | Low | Court Manager | Lounge door not pulling to. | NULL
1005 | Waltham House | WALTHAMHOUS_S001 | H21 | Scheme | 2022-10-04 16:09 | FRA_1005041020221449.pdf | BatesT | 1005041020221440 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | jx9fgwodnjl8ub0tf7 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45228 | Low | Court Manager | Incorrect fire action notice by gf privacy door. | NULL
1005 | Waltham House | WALTHAMHOUS_S001 | H21 | Scheme | 2022-10-04 16:09 | FRA_1005041020221449.pdf | BatesT | 1005041020221440 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | k0z2dnzlqqnl8uajqj5 | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45569 | Low | Court Manager | Scooter store cluttered and should be cleared back to mobility aids only | NULL
1005 | Waltham House | WALTHAMHOUS_S001 | H21 | Scheme | 2022-10-04 16:09 | FRA_1005041020221449.pdf | BatesT | 1005041020221440 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | i7puj7s2r6l8uaobfk | Low Risk to be actioned | Risk Open | NULL | Obs11 | Fire Fighting Equipment | 45569 | Low | Court Manager | Hanging bracket on extinguisher bin store first floor damaged, can not be set in correct position. Needs repair and/or relocating if necessary | NULL
1005 | Waltham House | WALTHAMHOUS_S001 | H21 | Scheme | 2022-10-04 16:09 | FRA_1005041020221449.pdf | BatesT | 1005041020221440 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | h5818znpparl8ub5n4p | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45569 | Low | Court Manager | Top floor "cleaners" cupboard unlocked. | NULL
1005 | Waltham House | WALTHAMHOUS_S001 | H21 | Scheme | 2022-10-04 16:09 | FRA_1005041020221449.pdf | BatesT | 1005041020221440 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | fmrd5gkh8bl8uazb3w | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45569 | Low | Court Manager | Office free swing faulty so door being propped open. Needs repair. | NULL
1005 | Waltham House | WALTHAMHOUS_S001 | H21 | Scheme | 2022-10-04 16:09 | FRA_1005041020221449.pdf | BatesT | 1005041020221440 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | z59vrbzkm3l8ub34x3 | Low Risk closed | Risk Closed | 44853.5097 | Obs8 | Measures To Limit Fire Spread And Development | 45569 | Low | Court Manager | Riser cupboards x2 marked "Keep locked" unlocked | Locked the doors
1005 | Waltham House | WALTHAMHOUS_S001 | H21 | Scheme | 2022-10-04 16:09 | FRA_1005041020221449.pdf | BatesT | 1005041020221440 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | xw6nozsisafl8ub6ikv | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45569 | Low | Court Manager | Commercial kitchen very cluttered, could hinder escape routes. | NULL
1011 | Handyside Court | HANDYSIDE_S001 | H21 | Scheme | 2022-10-04 12:32 | FRA_1011041020221231.pdf | BatesT | 1011041020221230 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | ylig7t8h1kl8u4efvp | Low Risk closed | Risk Closed | 44841.6075 | Obs8 | Measures To Limit Fire Spread And Development | 45569 | Low | Court Manager | Kitchen cleaning cupboard door has dropped. Needs easing and ajusting. | Door eased and adjusted 6.10.2022
1011 | Handyside Court | HANDYSIDE_S001 | H21 | Scheme | 2022-10-04 12:32 | FRA_1011041020221231.pdf | BatesT | 1011041020221230 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | wky9rn7drtl8u4efye | Low Risk closed | Risk Closed | 44841.6058 | Obs8 | Measures To Limit Fire Spread And Development | 45569 | Low | Court Manager | General issue with flat doors dropping, recomend all be checked, ease and adjust | All doors checked, missing grub screws replaced, all screws tightened. Doors checked afterwards.
1011 | Handyside Court | HANDYSIDE_S001 | H21 | Scheme | 2022-10-04 12:32 | FRA_1011041020221231.pdf | BatesT | 1011041020221230 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | e4mrkekq0sml8u4efxf | Low Risk closed | Risk Closed | 44841.6066 | Obs8 | Measures To Limit Fire Spread And Development | 45569 | Low | Court Manager | Addition of a door guard to first floor of conservatory has compromised protection between floors. Recomend either remove door guard or fit automated closer to ground floor and rezone. | Door guard removed.
1011 | Handyside Court | HANDYSIDE_S001 | H21 | Scheme | 2022-10-04 12:32 | FRA_1011041020221231.pdf | BatesT | 1011041020221230 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | 3cfb5hquyp7l8u4efwo | Low Risk closed | Risk Closed | 44841.6049 | Obs8 | Measures To Limit Fire Spread And Development | 45569 | Low | Court Manager | Kichen office door is propped open | Door kept closed. Spoke with the staff.
1012 | Dayton Court | DAYTON_S001 | H21 | Scheme | 2022-06-07 14:00 | FRA_1012070620221328.pdf | BatesT | 1012070620221320 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | m7gaod6gpml4451v61 | Observation Only | Risk Closed | 44778.7497 | Obs14 | Access By Emergency Services | NULL | N/A | Other | Note only - site is extremely compact, undercroft and extensive parking will make access by fire pumps more challenging. Fire evac point is only relevant for communal areas as stayput with early warning in place. | n/a observation only
1012 | Dayton Court | DAYTON_S001 | H21 | Scheme | 2022-06-07 14:00 | FRA_1012070620221328.pdf | BatesT | 1012070620221320 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | o9sj7o4qvlel4451v51 | Low Risk closed | Risk Closed | 44739.5645 | Obs4 | The Occupant - Information Provided By The Court Manager | 45450 | Low | Court Manager | 2 outstanding person centered | Completed PCFRA Initial Checklists to identify level of risk for residents of Flats 12 and 15
1012 | Dayton Court | DAYTON_S001 | H21 | Scheme | 2022-06-07 14:00 | FRA_1012070620221328.pdf | BatesT | 1012070620221320 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | zmpk1kb171l445f49s | Low Risk closed | Risk Closed | 44736.5001 | Obs8 | Measures To Limit Fire Spread And Development | 45450 | Low | Court Manager | Section of smoke seal missing to f9 door | Works order raised to Grant Defer and work completed 23rd June 2022
1018 | Sunnyfield Court | SUNNYFIELD_S001 | H21 | Scheme | 2022-01-26 15:14 | FRA_1018260120221304.pdf | BatesT | 1018260120221300 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | o48a1zfuzkmkyvod8jr | Low Risk closed | Risk Closed | 44606.5146 | Obs6 | Fire Hazards - Elimination & Control | 45317 | Low | Court Manager | Remove plug in fresheners - can be a risk if allowed to run dry. | Removed plug ins
1018 | Sunnyfield Court | SUNNYFIELD_S001 | H21 | Scheme | 2022-01-26 15:14 | FRA_1018260120221304.pdf | BatesT | 1018260120221300 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | oorsy8n6fzkyvl8s33 | Medium Risk closed | Risk Closed | 44602.4867 | Obs8 | Measures To Limit Fire Spread And Development | 44952 | Medium | Court Manager | F61 appears to be spredding into existing corridor. Is current level of posessions managed? | 4th Feb 2022. Discussed with tenants. Agreed to return items inside their property except wardrobe. Agreed to discuss during fire audit
1018 | Sunnyfield Court | SUNNYFIELD_S001 | H21 | Scheme | 2022-01-26 15:14 | FRA_1018260120221304.pdf | BatesT | 1018260120221300 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | p6syogu4xskyvk7g37 | Observation Only | Risk Open | NULL | Obs1 | The Building | NULL | N/A | Other | Existing compartmentation in good condition however follwing a type 4 survey there are areas found where this can be improved. This is currently being carried out by The Bell Group who are currently onsite. | NULL
1018 | Sunnyfield Court | SUNNYFIELD_S001 | H21 | Scheme | 2022-01-26 15:14 | FRA_1018260120221304.pdf | BatesT | 1018260120221300 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | szaepzmmqzkyvk7g47 | Medium Risk closed | Risk Closed | 44602.485 | Obs5 | Evacuation Strategy And Training | 44952 | Medium | Court Manager | New cm to complete fire safety management course. | Course completed 17th Jan 2022
1018 | Sunnyfield Court | SUNNYFIELD_S001 | H21 | Scheme | 2022-01-26 15:14 | FRA_1018260120221304.pdf | BatesT | 1018260120221300 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | fzjksx7trypkyvk7g7p | Medium Risk closed | Risk Closed | 44638.6623 | Obs8 | Measures To Limit Fire Spread And Development | 44952 | Medium | Court Manager | Door to stairwell at f9 & f5 not shutting on magnet release | Completed during routine servicing
1018 | Sunnyfield Court | SUNNYFIELD_S001 | H21 | Scheme | 2022-01-26 15:14 | FRA_1018260120221304.pdf | BatesT | 1018260120221300 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | h8tnefcnbk5kyvlbo2c | Medium Risk closed | Risk Closed | 44606.6991 | Obs8 | Measures To Limit Fire Spread And Development | 44952 | Medium | Court Manager | Storage up against electrical units should be avoided. | Items have been removed
1018 | Sunnyfield Court | SUNNYFIELD_S001 | H21 | Scheme | 2022-01-26 15:14 | FRA_1018260120221304.pdf | BatesT | 1018260120221300 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | i4k2xd5nnokyvk7g57 | Medium Risk closed | Risk Closed | 44596.4631 | Obs6 | Fire Hazards - Elimination & Control | 44616 | Medium | Court Manager | No evidence of pat testing of buggies charged in scooter store. This must be done annually. | ADC completed testing on 3rd Feb 2022
1018 | Sunnyfield Court | SUNNYFIELD_S001 | H21 | Scheme | 2022-01-26 15:14 | FRA_1018260120221304.pdf | BatesT | 1018260120221300 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | 27k1j6mdzzrjkyvojwyy | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44952 | Medium | Court Manager | Some flats have issues with latches stopping doors shutting. Recommend all are checked. | NULL
1018 | Sunnyfield Court | SUNNYFIELD_S001 | H21 | Scheme | 2022-01-26 15:14 | FRA_1018260120221304.pdf | BatesT | 1018260120221300 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | 5baahug8ozkyvk7g91 | Low Risk closed | Risk Closed | 44602.4875 | Obs15 | Management Of Fire Safety | 45317 | Low | Court Manager | Fire responsibility matrix missing from red folder. Needs completing and adding back in. | Added 26TH JAN 2022
1018 | Sunnyfield Court | SUNNYFIELD_S001 | H21 | Scheme | 2022-01-26 15:14 | FRA_1018260120221304.pdf | BatesT | 1018260120221300 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | 5timk7hfzfkkyvk7g67 | High Risk Closed | Risk Closed | 44606.5198 | Obs6 | Fire Hazards - Elimination & Control | 44677 | High | Court Manager | Materials stored in switch room | Removed combustible materials
1018 | Sunnyfield Court | SUNNYFIELD_S001 | H21 | Scheme | 2022-01-26 15:14 | FRA_1018260120221304.pdf | BatesT | 1018260120221300 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | 63fp5hbv2ebkyvk7qra | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45317 | Low | Court Manager | Slave doors at f10 & f12 marked as keep shut, should be keep locked. Signage to be corrected | NULL
1018 | Sunnyfield Court | SUNNYFIELD_S001 | H21 | Scheme | 2022-01-26 15:14 | FRA_1018260120221304.pdf | BatesT | 1018260120221300 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | erxtbwib386kyvkvdgq | Low Risk closed | Risk Closed | 44606.6983 | Obs8 | Measures To Limit Fire Spread And Development | 45317 | Low | Court Manager | Shop door propped open | Spoke to shop owner, agreed to remove door wedge
1018 | Sunnyfield Court | SUNNYFIELD_S001 | H21 | Scheme | 2022-01-26 15:14 | FRA_1018260120221304.pdf | BatesT | 1018260120221300 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | c3mmcqki306kyvl73eh | Low Risk closed | Risk Closed | 44638.6617 | Obs8 | Measures To Limit Fire Spread And Development | 45317 | Low | Court Manager | Magnet at stairwell at f59 | Completed during serving of dors
1018 | Sunnyfield Court | SUNNYFIELD_S001 | H21 | Scheme | 2022-01-26 15:14 | FRA_1018260120221304.pdf | BatesT | 1018260120221300 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | 9ug9f4ksjtbkyvk7g6z | Low Risk closed | Risk Closed | 44609.3906 | Obs8 | Measures To Limit Fire Spread And Development | 45317 | Low | Court Manager | Pantry door in kitchen is propped open, recommend it be shut / locked as per sign when kitchen is unmanned. | Spoke to kitchen staff agreed to not wedge door open
1020 | Lacemaker Court | LACEMAKER_S001 | H21 | Scheme | 2022-11-04 15:59 | FRA_1020041120221543.pdf | BatesT | 1020041120221540 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 6 | 88n0f2lgw0fla2o1na8 | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45234 | Medium | Court Manager | Hair dresser equipment needs pat testing | NULL
1020 | Lacemaker Court | LACEMAKER_S001 | H21 | Scheme | 2022-11-04 15:59 | FRA_1020041120221543.pdf | BatesT | 1020041120221540 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 6 | dhu0ageyhjela2o1n9c | Medium Risk Overdue | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44876 | Medium | Court Manager | No evidence of servicing of fire curtain. | NULL
1020 | Lacemaker Court | LACEMAKER_S001 | H21 | Scheme | 2022-11-04 15:59 | FRA_1020041120221543.pdf | BatesT | 1020041120221540 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 6 | f2h47sehkpcla2o1nhn | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45234 | Medium | Court Manager | Activity cupboard closer has been removed. Either needs reinstating or changing to "Keep locked" | NULL
1020 | Lacemaker Court | LACEMAKER_S001 | H21 | Scheme | 2022-11-04 15:59 | FRA_1020041120221543.pdf | BatesT | 1020041120221540 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 6 | 4h0b4xomfy5la2o1nc2 | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45600 | Low | Court Manager | Door from laundry not closing | NULL
1020 | Lacemaker Court | LACEMAKER_S001 | H21 | Scheme | 2022-11-04 15:59 | FRA_1020041120221543.pdf | BatesT | 1020041120221540 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 6 | 1r95okjxdl4la2o1nb6 | Observation Only | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Sight of catering firms fire risk assessment would be useful | NULL
1020 | Lacemaker Court | LACEMAKER_S001 | H21 | Scheme | 2022-11-04 15:59 | FRA_1020041120221543.pdf | BatesT | 1020041120221540 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 6 | hz951jm7uvhla2o1nr0 | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45240 | Low | Court Manager | Fire break doorway, 1st floor between entrance lobby and corridors has no fire door signage. | NULL
1020 | Lacemaker Court | LACEMAKER_S001 | H21 | Scheme | 2022-11-04 15:59 | FRA_1020041120221543.pdf | BatesT | 1020041120221540 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 6 | hqwp0uqitjnla2o1nto | Low Risk Overdue | Risk Open | NULL | Obs15 | Management Of Fire Safety | 44875 | Low | Court Manager | Emergency lighting logs within red book sporadic. | NULL
1020 | Lacemaker Court | LACEMAKER_S001 | H21 | Scheme | 2022-11-04 15:59 | FRA_1020041120221543.pdf | BatesT | 1020041120221540 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 6 | izucc30y2ujla2o1ncw | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45600 | Low | Court Manager | Fridge being stored in binstore | NULL
1020 | Lacemaker Court | LACEMAKER_S001 | H21 | Scheme | 2022-11-04 15:59 | FRA_1020041120221543.pdf | BatesT | 1020041120221540 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 6 | hf108bwip8sla2o1ne1 | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45240 | Low | Court Manager | Room with electrical switch gear is also being used as xmas decoration storage, Combining ignition source with fuel. Whilst there is reasonable distance betweeen the two, consideration should be given to moving stored material to another location if available. | NULL
1020 | Lacemaker Court | LACEMAKER_S001 | H21 | Scheme | 2022-11-04 15:59 | FRA_1020041120221543.pdf | BatesT | 1020041120221540 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 6 | fm6r81nkjcala2o1no8 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45600 | Low | Court Manager | 44 not pulling to | NULL
1020 | Lacemaker Court | LACEMAKER_S001 | H21 | Scheme | 2022-11-04 15:59 | FRA_1020041120221543.pdf | BatesT | 1020041120221540 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 6 | jyg6ekl1dnla2o1nkz | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45240 | Low | Court Manager | A number of the double fire break communal corridor doors are reliant on the "slave" door closing faster than the main door. Whilst this is checked monthly, additional alterations could be made to ensure that the doors shut correctly in either order. Alternatively the "slave" doors could be converted to keep locked as opposed to automatic. | NULL
1020 | Lacemaker Court | LACEMAKER_S001 | H21 | Scheme | 2022-11-04 15:59 | FRA_1020041120221543.pdf | BatesT | 1020041120221540 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 6 | t5e1rdlghjla2o1njz | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45234 | Medium | Court Manager | Clarification if window lights close from entrance area. Are these serviced with aov's? Is servicing up to date? | NULL
1020 | Lacemaker Court | LACEMAKER_S001 | H21 | Scheme | 2022-11-04 15:59 | FRA_1020041120221543.pdf | BatesT | 1020041120221540 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 6 | tlfs55ga8ula2o1ns0 | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45240 | Low | Court Manager | Unknown door on first floor has no fire door signage. | NULL
1020 | Lacemaker Court | LACEMAKER_S001 | H21 | Scheme | 2022-11-04 15:59 | FRA_1020041120221543.pdf | BatesT | 1020041120221540 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 6 | tnjxu2wdnunla2o1nir | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45600 | Low | Court Manager | Kitchen to diner door needs easing | NULL
1020 | Lacemaker Court | LACEMAKER_S001 | H21 | Scheme | 2022-11-04 15:59 | FRA_1020041120221543.pdf | BatesT | 1020041120221540 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 6 | rmwl3prtq4la2o1nuk | Low Risk Overdue | Risk Open | NULL | Obs15 | Management Of Fire Safety | 44875 | Low | Court Manager | Fire Fighting Equipment Logs very sporadic within red book | NULL
1020 | Lacemaker Court | LACEMAKER_S001 | H21 | Scheme | 2022-11-04 15:59 | FRA_1020041120221543.pdf | BatesT | 1020041120221540 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 6 | oz5jfku3adqla2o1ng6 | Medium Risk Overdue | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44875 | Medium | Development | A type 4 risk assessment has shown some failures of the fire compartmentation dating back to the building's construction. These have been detailed and need to be resolved via the original constructor or other means. | NULL
1020 | Lacemaker Court | LACEMAKER_S001 | H21 | Scheme | 2022-11-04 15:59 | FRA_1020041120221543.pdf | BatesT | 1020041120221540 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 6 | p6czgpnudmgla2o1nwp | Low Risk Overdue | Risk Open | NULL | Obs15 | Management Of Fire Safety | 44875 | Low | Court Manager | Staff training not in date in red book | NULL
1020 | Lacemaker Court | LACEMAKER_S001 | H21 | Scheme | 2022-11-04 15:59 | FRA_1020041120221543.pdf | BatesT | 1020041120221540 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 6 | qmpu4qrbndpla2o1nq0 | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45240 | Low | Court Manager | Some incorrect fire evacuation notices in place, need to be removed, currently showing conflicting information. | NULL
1020 | Lacemaker Court | LACEMAKER_S001 | H21 | Scheme | 2022-11-04 15:59 | FRA_1020041120221543.pdf | BatesT | 1020041120221540 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 6 | o85fnil9a5la2o1nvn | Medium Risk Overdue | Risk Open | NULL | Obs15 | Management Of Fire Safety | 44510 | Medium | Court Manager | No logs of fires or false alarms in red book | NULL
1020 | Lacemaker Court | LACEMAKER_S001 | H21 | Scheme | 2022-11-04 15:59 | FRA_1020041120221543.pdf | BatesT | 1020041120221540 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 6 | zv0acm6cx4la2o1n7l | Medium Risk Overdue | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44875 | Medium | Court Manager | Some buggies missing pat testing. | NULL
1020 | Lacemaker Court | LACEMAKER_S001 | H21 | Scheme | 2022-11-04 15:59 | FRA_1020041120221543.pdf | BatesT | 1020041120221540 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 6 | wlqp46b5ijdla2o1n6j | Low Risk to be actioned | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | 45600 | Low | Court Manager | No available key for red box at entry area. | NULL
1020 | Lacemaker Court | LACEMAKER_S001 | H21 | Scheme | 2022-11-04 15:59 | FRA_1020041120221543.pdf | BatesT | 1020041120221540 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 6 | ygd7s504uala2o1nm3 | Medium Risk Overdue | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44524 | Medium | Court Manager | Fire door by F35 not shutting correctly. | NULL
1020 | Lacemaker Court | LACEMAKER_S001 | H21 | Scheme | 2022-11-04 15:59 | FRA_1020041120221543.pdf | BatesT | 1020041120221540 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 6 | ysc1kn1t73lla2o1nn9 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45600 | Low | Court Manager | F35 door snagging on carpet | NULL
1021 | Thomas Fields | THOMASFIELDS_S001 | H21 | Scheme | 2022-07-11 13:40 | FRA_1021110720221338.pdf | BatesT | 1021110720221330 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | z7d8r8yowjcl5gqdfwi | Low Risk closed | Risk Closed | 44839.5955 | Obs7 | Fire Protection Measures | 45484 | Low | Court Manager | Doors being propped in staff room. Recommended fitting hold open magnets. | W/O ref 1567024 actioned and new door magnets installed on the 05/10/2022
1021 | Thomas Fields | THOMASFIELDS_S001 | H21 | Scheme | 2022-07-11 13:40 | FRA_1021110720221338.pdf | BatesT | 1021110720221330 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 9 | l5lrmljslcll5gqd6j4 | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45484 | Low | Court Manager | Storage of Xmas decks in tv switch room, recommend moving. | NULL
1023 | Claremont House | CLAREMONT_S001 | H21 | Scheme | 2022-06-07 12:09 | FRA_1023070620221126.pdf | BatesT | 1023070620221120 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | lm5zet8jlnl4411ji7 | Low Risk closed | Risk Closed | 44727.3892 | Obs8 | Measures To Limit Fire Spread And Development | 45450 | Low | Surveyor | All flat doors tested have intumescent painted over. | Checked with development. No issue.
1023 | Claremont House | CLAREMONT_S001 | H21 | Scheme | 2022-06-07 12:09 | FRA_1023070620221126.pdf | BatesT | 1023070620221120 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | n8pswz0fqkkl440p5ov | Low Risk closed | Risk Closed | 44719.5543 | Obs8 | Measures To Limit Fire Spread And Development | 45450 | Low | Court Manager | Door to lounge is being propped open. Recomend converting to free swing. | Removed door stops and have emailed TECS for a quote for a free swing to be fitted.
1023 | Claremont House | CLAREMONT_S001 | H21 | Scheme | 2022-06-07 12:09 | FRA_1023070620221126.pdf | BatesT | 1023070620221120 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | ga2fuoujpwul440p4xx | Medium Risk closed | Risk Closed | 44719.5549 | Obs7 | Fire Protection Measures | 45084 | Medium | Court Manager | Scooter stored on corridor | Spoke to resident last year about the storage of scooters. He now stores his scooter in the buggy room.
1023 | Claremont House | CLAREMONT_S001 | H21 | Scheme | 2022-06-07 12:09 | FRA_1023070620221126.pdf | BatesT | 1023070620221120 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | 317twm0mufil440p4wy | Low Risk closed | Risk Closed | 44720.5901 | Obs6 | Fire Hazards - Elimination & Control | 45450 | Low | Court Manager | No evidence of pat testing on scooter chargers. | residents have PAT tested their battery's straight away.
1023 | Claremont House | CLAREMONT_S001 | H21 | Scheme | 2022-06-07 12:09 | FRA_1023070620221126.pdf | BatesT | 1023070620221120 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | 43t79r8ron5l440p4zp | Low Risk closed | Risk Closed | 44720.5883 | Obs8 | Measures To Limit Fire Spread And Development | 45450 | Low | Court Manager | Fire door closer pulling frame apart | Handyman visited today and have replaced short screws with longer screws to prevent the frame being pulled out. completed 8.6.22
1023 | Claremont House | CLAREMONT_S001 | H21 | Scheme | 2022-06-07 12:09 | FRA_1023070620221126.pdf | BatesT | 1023070620221120 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | vgazi0n0uyl440p4yz | Low Risk closed | Risk Closed | 44719.5557 | Obs8 | Measures To Limit Fire Spread And Development | 45450 | Low | Court Manager | Meter room marked keep locked open | water meter cupboards have now been locked
1201 | John Shoobridge Court | JOHNSHOO_S001 | H21 | Scheme | 2022-05-23 12:51 | FRA_1201230520221108.pdf | fowlerb1 | 1201230520221100 | Retirement Housing | South West | Dorset | South | South Patch 2 | 77aadudii3cl3ilwyap | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45069 | Medium | Surveyor | Buggies being stored by main front door | NULL
1201 | John Shoobridge Court | JOHNSHOO_S001 | H21 | Scheme | 2022-05-23 12:51 | FRA_1201230520221108.pdf | fowlerb1 | 1201230520221100 | Retirement Housing | South West | Dorset | South | South Patch 2 | 0un9poqhh4cfl3il075n | Observation Only | Risk Closed | 44719.588 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel and zone plan | For information only
1201 | John Shoobridge Court | JOHNSHOO_S001 | H21 | Scheme | 2022-05-23 12:51 | FRA_1201230520221108.pdf | fowlerb1 | 1201230520221100 | Retirement Housing | South West | Dorset | South | South Patch 2 | ffz1bvj7n4l3ilzueo | Low Risk closed | Risk Closed | 44761.4577 | Obs8 | Measures To Limit Fire Spread And Development | 45435 | Low | Court Manager | Property smells of cigarettes due to resident in flat 20 in entrance and others across the first floor. | No Action taken as tenants allowed to smoke in flats. Reminded not to smoke in communal areas
1201 | John Shoobridge Court | JOHNSHOO_S001 | H21 | Scheme | 2022-05-23 12:51 | FRA_1201230520221108.pdf | fowlerb1 | 1201230520221100 | Retirement Housing | South West | Dorset | South | South Patch 2 | d8hfv9pxd4l3imhcmi | Medium Risk closed | Risk Closed | 44761.569 | Obs10 | Fire Safety And Notices | 45069 | Medium | Court Manager | Missing assembly point details | Updated Notices
1201 | John Shoobridge Court | JOHNSHOO_S001 | H21 | Scheme | 2022-05-23 12:51 | FRA_1201230520221108.pdf | fowlerb1 | 1201230520221100 | Retirement Housing | South West | Dorset | South | South Patch 2 | frfmuva91asl3il3e9b | Observation Only | Risk Closed | 44719.5878 | Obs1 | The Building | NULL | N/A | Surveyor | Cladding | For information only
1201 | John Shoobridge Court | JOHNSHOO_S001 | H21 | Scheme | 2022-05-23 12:51 | FRA_1201230520221108.pdf | fowlerb1 | 1201230520221100 | Retirement Housing | South West | Dorset | South | South Patch 2 | u0gdaqt50kkl3inrnuw | Medium Risk closed | Risk Closed | 44761.46 | Obs14 | Access By Emergency Services | 45069 | Medium | Court Manager | New location required for the assembly point | Old sign taken down. New one put up by Wessex. Residents advised of new Assembly point via newsletter.
1202 | Charles Keightley Court | CHARLESKEIG_S001 | H21 | Scheme | 2022-07-07 07:35 | FRA_1202070720220722.pdf | fowlerb1 | 1202070720220720 | Retirement Housing | South West | Dorset | South | South Patch 2 | tsw9ogaodrl5an622v | Medium Risk closed | Risk Closed | 44756.5515 | Obs10 | Fire Safety And Notices | 45114 | Medium | Court Manager | Fire action notices required to exits at front and side of communal block. | Fire Action notices in place - replacements required after Make Over
1202 | Charles Keightley Court | CHARLESKEIG_S001 | H21 | Scheme | 2022-07-07 07:35 | FRA_1202070720220722.pdf | fowlerb1 | 1202070720220720 | Retirement Housing | South West | Dorset | South | South Patch 2 | uj4tg9e3vil5an621d | Observation Only | Risk Closed | 44832.4424 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel for information only | Information only
1203 | Lawrance Court | LAWRANCE_S001 | H21 | Scheme | 2022-05-16 11:35 | FRA_1203160520220951.pdf | fowlerb1 | 1203160520220950 | Retirement Housing | South West | Dorset | South | South Patch 2 | tw3yni83x2l38l1zoe | Medium Risk closed | Risk Closed | 44736.5129 | Obs10 | Fire Safety And Notices | 45062 | Medium | Court Manager | Additional fire action notices are required and the assembly point location stated | New fire notices ordered and placed on all exits
1203 | Lawrance Court | LAWRANCE_S001 | H21 | Scheme | 2022-05-16 11:35 | FRA_1203160520220951.pdf | fowlerb1 | 1203160520220950 | Retirement Housing | South West | Dorset | South | South Patch 2 | mo3eefb5ql38j7ca2 | Low Risk closed | Risk Closed | 44741.8936 | Obs6 | Fire Hazards - Elimination & Control | 45428 | Low | Court Manager | Residents have a gas bbq with the cylinder stored in the communal shed - sign required for information | Gas bottle flammable sign placed on shed door
1203 | Lawrance Court | LAWRANCE_S001 | H21 | Scheme | 2022-05-16 11:35 | FRA_1203160520220951.pdf | fowlerb1 | 1203160520220950 | Retirement Housing | South West | Dorset | South | South Patch 2 | dcequ293m6l38ixmh8 | Low Risk closed | Risk Closed | 44698.5189 | Obs6 | Fire Hazards - Elimination & Control | 45428 | Low | Court Manager | No external communal smoking | Residents do not want a dedicated smoking area
1203 | Lawrance Court | LAWRANCE_S001 | H21 | Scheme | 2022-05-16 11:35 | FRA_1203160520220951.pdf | fowlerb1 | 1203160520220950 | Retirement Housing | South West | Dorset | South | South Patch 2 | amalf8g011ul38iqmdo | Observation Only | Risk Closed | 44719.5874 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Surveyor | Electric meters | For information only
1203 | Lawrance Court | LAWRANCE_S001 | H21 | Scheme | 2022-05-16 11:35 | FRA_1203160520220951.pdf | fowlerb1 | 1203160520220950 | Retirement Housing | South West | Dorset | South | South Patch 2 | 7u3qiyhtsx2l38iedm8 | Observation Only | Risk Closed | 44719.5876 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel | For information only
1204 | Reginald Noble Court | REGINALDNOBL_S001 | H21 | Scheme | 2022-06-15 10:56 | FRA_1204150620221017.pdf | mayesd | 1204150620221010 | Retirement Housing | South West | Dorset | South | South Patch 2 | 3ghf09b8ffcl4fefgzj | Low Risk closed | Risk Closed | 44739.764 | Obs8 | Measures To Limit Fire Spread And Development | 45458 | Low | Court Manager | Small section of intumescent brush required on communal compartment door by the main entrance | Completed
1204 | Reginald Noble Court | REGINALDNOBL_S001 | H21 | Scheme | 2022-06-15 10:56 | FRA_1204150620221017.pdf | mayesd | 1204150620221010 | Retirement Housing | South West | Dorset | South | South Patch 2 | bllg9zt8jpl4fej7ld | Medium Risk closed | Risk Closed | 44778.4314 | Obs12 | Automatic Fire Systems i.e. Suppression System | 45092 | Medium | Court Manager | Vented windows on mag locks on each level. Although Julie checks them as a part of the weekly test a formal maintenance check is also required | COMPLETED on the 7th June 2022.
1204 | Reginald Noble Court | REGINALDNOBL_S001 | H21 | Scheme | 2022-06-15 10:56 | FRA_1204150620221017.pdf | mayesd | 1204150620221010 | Retirement Housing | South West | Dorset | South | South Patch 2 | e8z97yritr9l4feccap | Low Risk closed | Risk Closed | 44791.7007 | Obs8 | Measures To Limit Fire Spread And Development | 45458 | Low | Court Manager | Fire stopping where pipes penetrate in electrical cupboard next to Lounge | Job has been completed 18th August 2022.
1204 | Reginald Noble Court | REGINALDNOBL_S001 | H21 | Scheme | 2022-06-15 10:56 | FRA_1204150620221017.pdf | mayesd | 1204150620221010 | Retirement Housing | South West | Dorset | South | South Patch 2 | jdyidhbersl4fea3cs | Medium Risk closed | Risk Closed | 44735.3577 | Obs8 | Measures To Limit Fire Spread And Development | 45092 | Medium | Court Manager | Flat 10 Drop down threshold required | JOB COMPLETED Wessex attended site and completed threshold.
1204 | Reginald Noble Court | REGINALDNOBL_S001 | H21 | Scheme | 2022-06-15 10:56 | FRA_1204150620221017.pdf | mayesd | 1204150620221010 | Retirement Housing | South West | Dorset | South | South Patch 2 | hx73edtq287l4fedxd6 | Medium Risk closed | Risk Closed | 44791.701 | Obs8 | Measures To Limit Fire Spread And Development | 45092 | Medium | Court Manager | Fire stopping required in electrical cupboard on lower ground floor adjacent to lift | Job has been completed 18th August 2022.
1204 | Reginald Noble Court | REGINALDNOBL_S001 | H21 | Scheme | 2022-06-15 10:56 | FRA_1204150620221017.pdf | mayesd | 1204150620221010 | Retirement Housing | South West | Dorset | South | South Patch 2 | i36d69d1zkl4fe5pv6 | Low Risk closed | Risk Closed | 44746.5656 | Obs7 | Fire Protection Measures | 45458 | Low | Court Manager | Break glass cover required on lower ground floor | JOB COMPLETED.
1212 | Weld Court | WELD_S001 | H21 | Scheme | 2022-05-26 11:33 | FRA_1212260520220956.pdf | fowlerb1 | 1212260520220950 | Retirement Housing | South West | Dorset | South | South Patch 2 | g793rxvsc5ol3mt4pu6 | Observation Only | Risk Closed | 44719.5881 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel for information only | For information only
1212 | Weld Court | WELD_S001 | H21 | Scheme | 2022-05-26 11:33 | FRA_1212260520220956.pdf | fowlerb1 | 1212260520220950 | Retirement Housing | South West | Dorset | South | South Patch 2 | gljnfqq1vul3mtxsyf | Observation Only | Risk Closed | 44719.5883 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Surveyor | Electric meter cupboard for information only | For information only
1212 | Weld Court | WELD_S001 | H21 | Scheme | 2022-05-26 11:33 | FRA_1212260520220956.pdf | fowlerb1 | 1212260520220950 | Retirement Housing | South West | Dorset | South | South Patch 2 | r6xayvb85l9l3muaf2q | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45072 | Medium | Court Manager | Bin store adjacent front door | NULL
1212 | Weld Court | WELD_S001 | H21 | Scheme | 2022-05-26 11:33 | FRA_1212260520220956.pdf | fowlerb1 | 1212260520220950 | Retirement Housing | South West | Dorset | South | South Patch 2 | 8asllr51d53l3mu7x4x | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45072 | Medium | Court Manager | Gas barbecue being used, but the gas cylinder is stored off site - this must monitored on an on going basis. | NULL
1213 | Sidney Smith Court | SIDNEYSMIT_S001 | H21 | Scheme | 2022-08-18 11:04 | FRA_1213180820221003.pdf | fowlerb1 | 1213180820221000 | Retirement Housing | South West | Dorset | South | South Patch 2 | 5h6vhulxmxql6yuokhg | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45185 | Low | Court Manager | More appropriate smoking shelter to be implemented | NULL
1213 | Sidney Smith Court | SIDNEYSMIT_S001 | H21 | Scheme | 2022-08-18 11:04 | FRA_1213180820221003.pdf | fowlerb1 | 1213180820221000 | Retirement Housing | South West | Dorset | South | South Patch 2 | z15l5auw0kbl6yv88v4 | Observation Only | Risk Open | NULL | Obs10 | Fire Safety And Notices | NULL | N/A | Court Manager | Fire action notices for information only | NULL
1213 | Sidney Smith Court | SIDNEYSMIT_S001 | H21 | Scheme | 2022-08-18 11:04 | FRA_1213180820221003.pdf | fowlerb1 | 1213180820221000 | Retirement Housing | South West | Dorset | South | South Patch 2 | zphwt88znfhl6yu6gua | Observation Only | Risk Closed | 44832.443 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel for information only | Information only
1217 | Cory Road | CORYROAD_S001 | H21 | Scheme | 2022-01-17 11:22 | FRA_1217170120220917.pdf | BoardP | 1217170120220910 | Retirement Housing | South West | Devon Cornwall and South West Somerset | South | South Patch 9 | ff7agb2josqkyikcmao | Low Risk closed | Risk Closed | 44761.3643 | Obs14 | Access By Emergency Services | 45308 | Low | Court Manager | CM to arrange new fire assembly point sign for car park | Installed new fire assembly point sign
1219 | Foyle Bank - Westhaven Court | FOYLEBANK_S001 | H21 | Scheme | 2022-04-06 12:18 | FRA_1219060420221057.pdf | fowlerb1 | 1219060420221050 | Extra Care | Extra Care South | EC South 4 | South | South Patch 2 | 1c2pj0r1b18l1neyrb2 | Observation Only | Risk Closed | 44719.5853 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Surveyor | Commercial kitchen | For information only
1219 | Foyle Bank - Westhaven Court | FOYLEBANK_S001 | H21 | Scheme | 2022-04-06 12:18 | FRA_1219060420221057.pdf | fowlerb1 | 1219060420221050 | Extra Care | Extra Care South | EC South 4 | South | South Patch 2 | rqfherkw1aml1ngxwps | Observation Only | Risk Closed | 44719.5852 | Obs13 | Other Relevant Fixed Systems | NULL | N/A | Surveyor | Aov - for information only | For information only
1219 | Foyle Bank - Westhaven Court | FOYLEBANK_S001 | H21 | Scheme | 2022-04-06 12:18 | FRA_1219060420221057.pdf | fowlerb1 | 1219060420221050 | Extra Care | Extra Care South | EC South 4 | South | South Patch 2 | tnnz277ixtol1nedi8i | Observation Only | Risk Closed | 44719.5856 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire alarm service certificate | For information only
1219 | Foyle Bank - Westhaven Court | FOYLEBANK_S001 | H21 | Scheme | 2022-04-06 12:18 | FRA_1219060420221057.pdf | fowlerb1 | 1219060420221050 | Extra Care | Extra Care South | EC South 4 | South | South Patch 2 | gw0mnliwsb8l1ned4hp | Observation Only | Risk Closed | 44719.5859 | Obs1 | The Building | NULL | N/A | Surveyor | Balconies - for information only | For information only
1219 | Foyle Bank - Westhaven Court | FOYLEBANK_S001 | H21 | Scheme | 2022-04-06 12:18 | FRA_1219060420221057.pdf | fowlerb1 | 1219060420221050 | Extra Care | Extra Care South | EC South 4 | South | South Patch 2 | iua5aneqv5l1nerpzk | Observation Only | Risk Closed | 44719.5849 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Surveyor | Bin store for information only | No action required
1219 | Foyle Bank - Westhaven Court | FOYLEBANK_S001 | H21 | Scheme | 2022-04-06 12:18 | FRA_1219060420221057.pdf | fowlerb1 | 1219060420221050 | Extra Care | Extra Care South | EC South 4 | South | South Patch 2 | k6c1wsg06sel1ngkuce | Observation Only | Risk Closed | 44719.5857 | Obs10 | Fire Safety And Notices | NULL | N/A | Surveyor | Fire action notice | For information only
1219 | Foyle Bank - Westhaven Court | FOYLEBANK_S001 | H21 | Scheme | 2022-04-06 12:18 | FRA_1219060420221057.pdf | fowlerb1 | 1219060420221050 | Extra Care | Extra Care South | EC South 4 | South | South Patch 2 | v8f6ev3mr2ol1neulsd | Observation Only | Risk Closed | 44719.5862 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Surveyor | Buggy store | For information only
1302 | Festing Court | FESTING_S001 | H21 | Scheme | 2022-01-26 14:34 | FRA_1302240120221150.pdf | whitek2 | 1302240120221150 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 8 | zs99uryi81ikyvn6v23 | Medium Risk closed | Risk Closed | 44656.4382 | Obs15 | Management Of Fire Safety | 44952 | Medium | Court Manager | High number of false alarms requires investigation and act upon the findings and actions | Reviewed reoccurring incidents and updated new PCFRA for those residents. Monitoring.
1302 | Festing Court | FESTING_S001 | H21 | Scheme | 2022-01-26 14:34 | FRA_1302240120221150.pdf | whitek2 | 1302240120221150 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 8 | leh2py96ljkysmoznp | Medium Risk closed | Risk Closed | 44623.5986 | Obs8 | Measures To Limit Fire Spread And Development | 44950 | Medium | Court Manager | Number of flat doors not latching adjust door closers | Joiner adjusted to close independently and fully
1302 | Festing Court | FESTING_S001 | H21 | Scheme | 2022-01-26 14:34 | FRA_1302240120221150.pdf | whitek2 | 1302240120221150 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 8 | u7dfzbd59kkkysmozlx | High Risk Closed | Risk Closed | 44617.408 | Obs7 | Fire Protection Measures | 44675 | High | Court Manager | Laundry door hinge pin snapped need replacing so as door can close | Hinge replaced
1302 | Festing Court | FESTING_S001 | H21 | Scheme | 2022-01-26 14:34 | FRA_1302240120221150.pdf | whitek2 | 1302240120221150 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 8 | 1ygmwnxmsi3kysmp0bv | High Risk Closed | Risk Closed | 44617.4114 | Obs7 | Fire Protection Measures | 44675 | High | Court Manager | Lounge door | Hinges and closer overhauled to close efficiently
1302 | Festing Court | FESTING_S001 | H21 | Scheme | 2022-01-26 14:34 | FRA_1302240120221150.pdf | whitek2 | 1302240120221150 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 8 | 8nao3wq4scokysmozmm | High Risk Closed | Risk Closed | 44617.4145 | Obs7 | Fire Protection Measures | 44675 | High | Court Manager | Fire door catching on bottom not closing ease bottom edge adjacent to flats 1 & 2 | Door adjusted to close easily
1304 | Avon Court | AVON_S001 | H21 | Scheme | 2022-01-17 14:15 | FRA_1304170120221402.pdf | whitek2 | 1304170120221400 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 8 | vmv28k2xx5qkyirayby | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45308 | Low | Court Manager | Portable appliances in guest room no evidence of recent PAT testing | NULL
1306 | Castlestead View | CASTLESTEADVIEW_S001 | H21 | Scheme | 2022-11-01 09:21 | FRA_1306291020221604.pdf | taylors1 | 1306291020221600 | Extra Care | Extra Care North | EC North 4 | North | North Patch 1 | vss98w28wcbl9wrr7bl | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45596 | Low | Court Manager | Adjust cross corridor door opposite flat 38 to close | NULL
1306 | Castlestead View | CASTLESTEADVIEW_S001 | H21 | Scheme | 2022-11-01 09:21 | FRA_1306291020221604.pdf | taylors1 | 1306291020221600 | Extra Care | Extra Care North | EC North 4 | North | North Patch 1 | w6nvasp0r2l9wr3hcj | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45230 | Medium | Court Manager | Excessive gap to refuse door closing edge | NULL
1306 | Castlestead View | CASTLESTEADVIEW_S001 | H21 | Scheme | 2022-11-01 09:21 | FRA_1306291020221604.pdf | taylors1 | 1306291020221600 | Extra Care | Extra Care North | EC North 4 | North | North Patch 1 | wun4prsgc7gl9wrktwx | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45230 | Medium | Court Manager | Excessive gap to cross corridor door adjacent to flat 40 and damage around all hinge recesses full door set required | NULL
1306 | Castlestead View | CASTLESTEADVIEW_S001 | H21 | Scheme | 2022-11-01 09:21 | FRA_1306291020221604.pdf | taylors1 | 1306291020221600 | Extra Care | Extra Care North | EC North 4 | North | North Patch 1 | 82r2oyhn944l9wso364 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45596 | Low | Court Manager | Door blade to replace on cross corridor door opposite lift lobby on floor 0 water damage to top edge | NULL
1306 | Castlestead View | CASTLESTEADVIEW_S001 | H21 | Scheme | 2022-11-01 09:21 | FRA_1306291020221604.pdf | taylors1 | 1306291020221600 | Extra Care | Extra Care North | EC North 4 | North | North Patch 1 | 18ahexv1l9qjl9wsj31y | Low Risk closed | Risk Closed | 44876.7246 | Obs8 | Measures To Limit Fire Spread And Development | 45596 | Low | Court Manager | Missing screw from centre hinge to meter room | Screw was fitted
1306 | Castlestead View | CASTLESTEADVIEW_S001 | H21 | Scheme | 2022-11-01 09:21 | FRA_1306291020221604.pdf | taylors1 | 1306291020221600 | Extra Care | Extra Care North | EC North 4 | North | North Patch 1 | 7d9achduscvl9wrxof7 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45596 | Low | Court Manager | Door blade to cross corridor door replace water damage to top edges adjacent to flat 25 door not closing fully | NULL
1306 | Castlestead View | CASTLESTEADVIEW_S001 | H21 | Scheme | 2022-11-01 09:21 | FRA_1306291020221604.pdf | taylors1 | 1306291020221600 | Extra Care | Extra Care North | EC North 4 | North | North Patch 1 | ttfvq733mg9l9wqahht | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45230 | Medium | Court Manager | Excessive gap to service cupboard doors x 2 sets on second floor | NULL
1306 | Castlestead View | CASTLESTEADVIEW_S001 | H21 | Scheme | 2022-11-01 09:21 | FRA_1306291020221604.pdf | taylors1 | 1306291020221600 | Extra Care | Extra Care North | EC North 4 | North | North Patch 1 | r59uzn59blsl9wqwlkx | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45230 | Medium | Court Manager | Cross corridor door adjacent to flat 60 not closing fully excessive gap on hinge side | NULL
1306 | Castlestead View | CASTLESTEADVIEW_S001 | H21 | Scheme | 2022-11-01 09:21 | FRA_1306291020221604.pdf | taylors1 | 1306291020221600 | Extra Care | Extra Care North | EC North 4 | North | North Patch 1 | nxtyepn1sfl9wrazao | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45596 | Low | Court Manager | Damaged to frame of cross corridor door adjacent to flat 21 around middle hinge | NULL
1306 | Castlestead View | CASTLESTEADVIEW_S001 | H21 | Scheme | 2022-11-01 09:21 | FRA_1306291020221604.pdf | taylors1 | 1306291020221600 | Extra Care | Extra Care North | EC North 4 | North | North Patch 1 | q9hlslingql9ws61pr | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45596 | Low | Court Manager | Damage to cross corridor door adjacent to flat 4 | NULL
1306 | Castlestead View | CASTLESTEADVIEW_S001 | H21 | Scheme | 2022-11-01 09:21 | FRA_1306291020221604.pdf | taylors1 | 1306291020221600 | Extra Care | Extra Care North | EC North 4 | North | North Patch 1 | ozum6v7pyshl9wr7iou | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45230 | Medium | Court Manager | Replace smoke seals to cross corridor door adjacent to flat 48 coated with gloss paint | NULL
1306 | Castlestead View | CASTLESTEADVIEW_S001 | H21 | Scheme | 2022-11-01 09:21 | FRA_1306291020221604.pdf | taylors1 | 1306291020221600 | Extra Care | Extra Care North | EC North 4 | North | North Patch 1 | jj0x923r49ol9wqp8m1 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45596 | Low | Court Manager | Repair to ceiling inside second floor cupboard adjacent to seating area around sprinkler head | NULL
1306 | Castlestead View | CASTLESTEADVIEW_S001 | H21 | Scheme | 2022-11-01 09:21 | FRA_1306291020221604.pdf | taylors1 | 1306291020221600 | Extra Care | Extra Care North | EC North 4 | North | North Patch 1 | hzluxrr8exkl9wqt9sb | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45230 | Medium | Court Manager | Excessive gap to cross corridor door adjacent to flat 56 | NULL
1306 | Castlestead View | CASTLESTEADVIEW_S001 | H21 | Scheme | 2022-11-01 09:21 | FRA_1306291020221604.pdf | taylors1 | 1306291020221600 | Extra Care | Extra Care North | EC North 4 | North | North Patch 1 | hu2kkbgot0nl9wqjg07 | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45230 | Medium | Court Manager | Door leading onto stair lobby opposite flat 64 requires easing to close | NULL
1307 | Poppy Dene | POPPYDENE_S001 | H21 | Scheme | 2022-05-06 15:35 | FRA_1307060520221348.pdf | whitek2 | 1307060520221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | hz0h9rzyv5dl2ufwyoa | Low Risk closed | Risk Closed | 44693.6592 | Obs8 | Measures To Limit Fire Spread And Development | 45418 | Low | Court Manager | Flat 52 not latching door closer requires adjusting | Vistry contractor completed yesterday
1307 | Poppy Dene | POPPYDENE_S001 | H21 | Scheme | 2022-05-06 15:35 | FRA_1307060520221348.pdf | whitek2 | 1307060520221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | jij24ijrxzcl2uhl03k | Low Risk closed | Risk Closed | 44693.6556 | Obs7 | Fire Protection Measures | 45418 | Low | Court Manager | 2nd floor corridor doors near flat 52 not meeting in middle to form smoke seal requires adjustment | Vistry contractor completed yesterday
1307 | Poppy Dene | POPPYDENE_S001 | H21 | Scheme | 2022-05-06 15:35 | FRA_1307060520221348.pdf | whitek2 | 1307060520221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | lv5bj9kbai8l2ui7irn | Medium Risk closed | Risk Closed | 44783.6091 | Obs6 | Fire Hazards - Elimination & Control | 45052 | Medium | Court Manager | Catering kitchen position of salamander grill very poor too high and requires operative to lean over gas rings would recommend its removal or if possible relocation | Restaurant manager to risk assess this as there us nowhere else for this to go and they want to keep using it.
1307 | Poppy Dene | POPPYDENE_S001 | H21 | Scheme | 2022-05-06 15:35 | FRA_1307060520221348.pdf | whitek2 | 1307060520221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | mn231jx14ral2uhsglg | Medium Risk closed | Risk Closed | 44693.651 | Obs7 | Fire Protection Measures | 45052 | Medium | Court Manager | 1st floor corridor doors near meeting room not closing to form a smoke seal requires adjustment | Vistry contractor completed yesterday
1307 | Poppy Dene | POPPYDENE_S001 | H21 | Scheme | 2022-05-06 15:35 | FRA_1307060520221348.pdf | whitek2 | 1307060520221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | qj06syy8hurl2ui56wo | Medium Risk closed | Risk Closed | 44693.6506 | Obs7 | Fire Protection Measures | 45052 | Medium | Court Manager | Ground floor door near flat 6 not meeting in middle to form smoke seal requires adjustment | Vistry contractor completed yesterday
1307 | Poppy Dene | POPPYDENE_S001 | H21 | Scheme | 2022-05-06 15:35 | FRA_1307060520221348.pdf | whitek2 | 1307060520221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | qytzlcynl5l2uhjbmb | Medium Risk closed | Risk Closed | 44693.6508 | Obs7 | Fire Protection Measures | 45052 | Medium | Court Manager | 2nd floor corridor doors near flat 58 not meeting in middle to form smoke seal requires adjustment | Vistry contractor completed yesterday
1307 | Poppy Dene | POPPYDENE_S001 | H21 | Scheme | 2022-05-06 15:35 | FRA_1307060520221348.pdf | whitek2 | 1307060520221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | 0tay9wssidofl2uguth4 | Medium Risk closed | Risk Closed | 44693.6553 | Obs7 | Fire Protection Measures | 45052 | Medium | Court Manager | 2nd floor corridor doors near flat 70 catching on carpet adjust | Vistry contractor completed yesterday
1307 | Poppy Dene | POPPYDENE_S001 | H21 | Scheme | 2022-05-06 15:35 | FRA_1307060520221348.pdf | whitek2 | 1307060520221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | 0d0a8hzieduvl2uhwu2u | High Risk Closed | Risk Closed | 44693.6552 | Obs7 | Fire Protection Measures | 44779 | High | Court Manager | Ground floor fire door leading to evacuation staircase adjacent to laundry room closer not operating correctly and jamming on architrave REQUIRES URGENT repair | Vistry contractor completed yesterday
1307 | Poppy Dene | POPPYDENE_S001 | H21 | Scheme | 2022-05-06 15:35 | FRA_1307060520221348.pdf | whitek2 | 1307060520221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | 2sxfa16xotcl2uhq5m7 | Medium Risk closed | Risk Closed | 44693.6589 | Obs7 | Fire Protection Measures | 45052 | Medium | Court Manager | 2nd floor refuse room door leading from corridor catching on vinyl floor requires adjustment | Vistry contractor completed yesterday
1307 | Poppy Dene | POPPYDENE_S001 | H21 | Scheme | 2022-05-06 15:35 | FRA_1307060520221348.pdf | whitek2 | 1307060520221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | 8euag6cixojl2ui1a04 | Low Risk closed | Risk Closed | 44693.6555 | Obs7 | Fire Protection Measures | 45418 | Low | Court Manager | Ground floor door near lift lobby and flat 12 auto stay not working | Vistry contractor completed yesterday
1307 | Poppy Dene | POPPYDENE_S001 | H21 | Scheme | 2022-05-06 15:35 | FRA_1307060520221348.pdf | whitek2 | 1307060520221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | adr66xyonhl2uhgsuq | Medium Risk closed | Risk Closed | 44693.6504 | Obs7 | Fire Protection Measures | 45052 | Medium | Court Manager | 2nd floor corridor doors near flat 65 catching on carpet adjust bottom of door | Vistry contractor completed yesterday
1307 | Poppy Dene | POPPYDENE_S001 | H21 | Scheme | 2022-05-06 15:35 | FRA_1307060520221348.pdf | whitek2 | 1307060520221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | eptv27oo55rl2uhuqct | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45418 | Low | M&E Team | Ground floor laundry room un-vented water storage tank ensure annual service | NULL
1307 | Poppy Dene | POPPYDENE_S001 | H21 | Scheme | 2022-05-06 15:35 | FRA_1307060520221348.pdf | whitek2 | 1307060520221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | erfs7kysoxl2uhoqnn | Medium Risk closed | Risk Closed | 44693.6587 | Obs7 | Fire Protection Measures | 45052 | Medium | Court Manager | 2nd floor refuse room hatch missing from ceiling replace | Vistry contractor completed yesterday
1307 | Poppy Dene | POPPYDENE_S001 | H21 | Scheme | 2022-05-06 15:35 | FRA_1307060520221348.pdf | whitek2 | 1307060520221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | dmy4qviazbol2ufokcf | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45418 | Low | Court Manager | Store combustible materials in suitable metal cabinet | NULL
1307 | Poppy Dene | POPPYDENE_S001 | H21 | Scheme | 2022-05-06 15:35 | FRA_1307060520221348.pdf | whitek2 | 1307060520221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | d1x9ahlwbkrl2ui3f8h | Medium Risk closed | Risk Closed | 44693.6498 | Obs7 | Fire Protection Measures | 45052 | Medium | Court Manager | Ground floor door near flat 4 not meeting in the middle to form smoke seal requires adjustment | Vistry contractor completed 11.05.22
1307 | Poppy Dene | POPPYDENE_S001 | H21 | Scheme | 2022-05-06 15:35 | FRA_1307060520221348.pdf | whitek2 | 1307060520221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | vx6akdmi9yl2ugxyc1 | Medium Risk closed | Risk Closed | 44693.6559 | Obs7 | Fire Protection Measures | 45052 | Medium | Court Manager | 2nd floor corridor doors near flat 69 not meeting in middle to form smoke seal requires adjustment | Vistry contractor completed yesterday
1307 | Poppy Dene | POPPYDENE_S001 | H21 | Scheme | 2022-05-06 15:35 | FRA_1307060520221348.pdf | whitek2 | 1307060520221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | zm6uebky72ll2uhmrkl | Medium Risk closed | Risk Closed | 44693.6502 | Obs7 | Fire Protection Measures | 45052 | Medium | Court Manager | 2nd floor staircase 1 door catching on carpet requires adjustment | Vistry contractor completed 11.05.22
1314 | Walton Court | WALTON_S001 | H21 | Scheme | 2022-01-17 09:00 | FRA_1314170120220837.pdf | taylors1 | 1314170120220830 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 1 | b01difq634lkyifpx08 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45308 | Low | Court Manager | Adjust closing side rebate lath so do closes tight into frame fire door at bottom of staircase opposite flat 11 | NULL
1314 | Walton Court | WALTON_S001 | H21 | Scheme | 2022-01-17 09:00 | FRA_1314170120220837.pdf | taylors1 | 1314170120220830 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 1 | 20clp0qz8ptkyifpx13 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45308 | Low | Court Manager | Replace closing edge cold smoke seal to cross corridor door adjacent to flat 24 | NULL
1314 | Walton Court | WALTON_S001 | H21 | Scheme | 2022-01-17 09:00 | FRA_1314170120220837.pdf | taylors1 | 1314170120220830 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 1 | 571rqa47icakyifpx1r | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45308 | Low | Court Manager | Replace cold smoke seal to cross corridor door adjacent to flat 18 paint on brush | NULL
1314 | Walton Court | WALTON_S001 | H21 | Scheme | 2022-01-17 09:00 | FRA_1314170120220837.pdf | taylors1 | 1314170120220830 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 1 | oox70up4n6hkyifpx33 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45308 | Low | Court Manager | Replace cold smoke seal to cross corridor door adjacent to flat 5 | NULL
1314 | Walton Court | WALTON_S001 | H21 | Scheme | 2022-01-17 09:00 | FRA_1314170120220837.pdf | taylors1 | 1314170120220830 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 1 | i9kde7lw8vpkyifpx2g | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45308 | Low | Court Manager | Replace cold smoke seal to cross corridor door adjacent to flat 11 paint on brush | NULL
1401 | Gavin Astor Court | GAVINASTO_S001 | H21 | Scheme | 2022-05-06 13:54 | FRA_1401060520221149.pdf | mayesd | 1401060520221140 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 1 | os13r76jcs8l2ubm03j | Medium Risk closed | Risk Closed | 44693.6309 | Obs7 | Fire Protection Measures | 45052 | Medium | Court Manager | Overhead closers required on the laundry and lounge door by the guest room | Overhead Closers have now been fitted to these doors
1401 | Gavin Astor Court | GAVINASTO_S001 | H21 | Scheme | 2022-05-06 13:54 | FRA_1401060520221149.pdf | mayesd | 1401060520221140 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 1 | 39s0jn43wqyl2ubedhf | Observation Only | Risk Closed | 44700.5766 | Obs5 | Evacuation Strategy And Training | NULL | N/A | Court Manager | Daniel is a new Court manager and is due to undertake training ASAP | All Fire Training completed
1401 | Gavin Astor Court | GAVINASTO_S001 | H21 | Scheme | 2022-05-06 13:54 | FRA_1401060520221149.pdf | mayesd | 1401060520221140 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 1 | 1l17pj7icidl2ubedkd | Low Risk closed | Risk Closed | 44902.4675 | Obs8 | Measures To Limit Fire Spread And Development | 45418 | Low | Court Manager | Flat 19 requires a section of smoke seal fitted | Contractor attended
1401 | Gavin Astor Court | GAVINASTO_S001 | H21 | Scheme | 2022-05-06 13:54 | FRA_1401060520221149.pdf | mayesd | 1401060520221140 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 1 | 8rz1jsea4x5l2ubedju | Medium Risk closed | Risk Closed | 44767.603 | Obs8 | Measures To Limit Fire Spread And Development | 45052 | Medium | Court Manager | Flat 14 closer has become detached and requires re fixing | Fire door needed replacing and new closer has been fitted.
1401 | Gavin Astor Court | GAVINASTO_S001 | H21 | Scheme | 2022-05-06 13:54 | FRA_1401060520221149.pdf | mayesd | 1401060520221140 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 1 | v4sq477xxtil2ubedj9 | Medium Risk closed | Risk Closed | 44701.6042 | Obs8 | Measures To Limit Fire Spread And Development | 45052 | Medium | Court Manager | Flat 9 Smoke seal required | The Smoke Seal has now been fitted
1401 | Gavin Astor Court | GAVINASTO_S001 | H21 | Scheme | 2022-05-06 13:54 | FRA_1401060520221149.pdf | mayesd | 1401060520221140 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 1 | uvyzn14h6ajl2ubedid | Medium Risk closed | Risk Closed | 44694.4664 | Obs6 | Fire Hazards - Elimination & Control | 45052 | Medium | Court Manager | Emergency light test switch cover plate requires replacement in stairwell for flats 8 and 9 | New fitting added by Booker and Best
1402 | Farren Court | FARREN_S001 | H21 | Scheme | 2022-10-03 11:30 | FRA_1402300920221249.pdf | LingF | 1402300920221240 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 1 | zfwftdk2ngal8ofakzm | Observation Only | Risk Closed | 44854.7704 | Obs1 | The Building | NULL | N/A | Surveyor | General elevation view | Info
1402 | Farren Court | FARREN_S001 | H21 | Scheme | 2022-10-03 11:30 | FRA_1402300920221249.pdf | LingF | 1402300920221240 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 1 | 9616vvju1h7l8oggaka | Observation Only | Risk Closed | 44837.6078 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Court Manager | Fire panel and zone chart | Took a photo of the fire panel and zone chart.
1402 | Farren Court | FARREN_S001 | H21 | Scheme | 2022-10-03 11:30 | FRA_1402300920221249.pdf | LingF | 1402300920221240 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 1 | 968ixk4wjc7l8skuevf | Observation Only | Risk Closed | 44837.6146 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | CM has undertaken PCFRA for all residents with scoring matrix not identifying any high risk occupants. | Ensured that all Residents have a PCFRA Checklist and PCFRA Full (if required). No high risks.
1402 | Farren Court | FARREN_S001 | H21 | Scheme | 2022-10-03 11:30 | FRA_1402300920221249.pdf | LingF | 1402300920221240 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 1 | p2s5ekudzhl8og8503 | Low Risk closed | Risk Closed | 44854.7704 | Obs8 | Measures To Limit Fire Spread And Development | 45199 | Low | Surveyor | Fire officer raised deficiencies around fire rating of elec meter boxes _ to be upgraded to fd30s. | Info
1402 | Farren Court | FARREN_S001 | H21 | Scheme | 2022-10-03 11:30 | FRA_1402300920221249.pdf | LingF | 1402300920221240 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 1 | uc8j0xd6fxl8og54ty | Low Risk closed | Risk Closed | 44852.4504 | Obs8 | Measures To Limit Fire Spread And Development | 45565 | Low | Court Manager | Fire stopping required around pipes within main elec intake _ both ends of pipe | Booker and Best applied fire stopping sealant to the areas required. Applied inside the electrical cupboard and in the laundry.
1402 | Farren Court | FARREN_S001 | H21 | Scheme | 2022-10-03 11:30 | FRA_1402300920221249.pdf | LingF | 1402300920221240 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 1 | iyseu4j4mvl8ogvmos | Low Risk closed | Risk Closed | 44840.5784 | Obs6 | Fire Hazards - Elimination & Control | 45565 | Low | Court Manager | Store cupboards General _ reduce/remove flammable Items and have a managed policy around items being stored | Wrote to all Residents in Blocks 55-61 and 63-69. See letter which is also kept with FRA in fire folder.
1403 | Nicholson Court (Langney) | NICHOLSONLAN_S001 | H21 | Scheme | 2022-05-23 14:50 | FRA_1403230520221446.pdf | mayesd | 1403230520221440 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | ngsz9vinxdl3is8m9n | Low Risk closed | Risk Closed | 44748.3884 | Obs10 | Fire Safety And Notices | 45435 | Low | Court Manager | Fire exit right sign required on first floor | FIRE EXIT SIGN PURCHASED AND POSITIONED AS ADVISED.
1403 | Nicholson Court (Langney) | NICHOLSONLAN_S001 | H21 | Scheme | 2022-05-23 14:50 | FRA_1403230520221446.pdf | mayesd | 1403230520221440 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | e9kdx0sr168l3is8m8i | Low Risk closed | Risk Closed | 44748.3891 | Obs8 | Measures To Limit Fire Spread And Development | 45435 | Low | Court Manager | AOVs require repair and is expected to occur within the next 3 months | NEW AOV SYSTEM NOW IN SITU. WORKS ALREADY SCHEDULED PRIOR TO CFRA
1404 | Duke Bernard Court | DUKEBERN_S001 | H21 | Scheme | 2022-04-28 16:00 | FRA_1404280420221538.pdf | mayesd | 1404280420221530 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | 4erx61sqvfal2j4fdpn | Medium Risk closed | Risk Closed | 44705.6463 | Obs8 | Measures To Limit Fire Spread And Development | 45044 | Medium | Court Manager | Flat 60's front door does not fully close and requires some minor adjustment | Door has been adjusted and now closes fully as required.
1404 | Duke Bernard Court | DUKEBERN_S001 | H21 | Scheme | 2022-04-28 16:00 | FRA_1404280420221538.pdf | mayesd | 1404280420221530 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | tk2lnr3z4yl2j47vv2 | Medium Risk closed | Risk Closed | 44705.6482 | Obs7 | Fire Protection Measures | 45044 | Medium | Court Manager | The lounge external door is quite stiff to operate. This requires adjustment to enable smooth operation | Door no longer stiff after adjustment and now operates smoothly.
1404 | Duke Bernard Court | DUKEBERN_S001 | H21 | Scheme | 2022-04-28 16:00 | FRA_1404280420221538.pdf | mayesd | 1404280420221530 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | z90o9ee91bcl2j4icf8 | Medium Risk closed | Risk Closed | 44705.6472 | Obs8 | Measures To Limit Fire Spread And Development | 45044 | Medium | Court Manager | There is a gap between the floor and the bottom of the flat front door above the acceptable tolerance on the following doors , 67, 45, 60, 46, 47, 49, 50, 57 and store cupboard 4. A drop down bar similar to what has been used at other locations in the court is required | Drop down bars have been fitted on all listed doors as recommended.
1405 | Ellis Gordon Court | ELLISGORD_S001 | H21 | Scheme | 2022-09-27 11:34 | FRA_1405260920221827.pdf | LingF | 1405260920221820 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | uot5ldm14crl8j1ohw8 | Observation Only | Risk Closed | 44833.4487 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | F6 _ suffers with hearing loss and reduced mobility would require assistance to evacuate. does not cook, has frequent care support, no flashing beacons in flat to alert of alarm activation. F9_ suffers with mental impairment and mental health issues, doesn't cook food delivered. F28_ impaired mobility, mental impairment, tries to cook will require assistance to evacuate. | Done
1405 | Ellis Gordon Court | ELLISGORD_S001 | H21 | Scheme | 2022-09-27 11:34 | FRA_1405260920221827.pdf | LingF | 1405260920221820 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | ow2oj4ge9ohl8j22vk0 | Observation Only | Risk Closed | 44833.4511 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Court Manager | Scheme does not have smoke control systems, travel distances are within permitted levels | Noted
1405 | Ellis Gordon Court | ELLISGORD_S001 | H21 | Scheme | 2022-09-27 11:34 | FRA_1405260920221827.pdf | LingF | 1405260920221820 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | omdo47pvml8k1rr6w | Low Risk closed | Risk Closed | 44833.452 | Obs8 | Measures To Limit Fire Spread And Development | 45562 | Low | Court Manager | Cross corridor doors adj F5 _ gap requires to be closed down using extended brush strips | Arrangements being made with contractor
1405 | Ellis Gordon Court | ELLISGORD_S001 | H21 | Scheme | 2022-09-27 11:34 | FRA_1405260920221827.pdf | LingF | 1405260920221820 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | q6j06szxcmal8j1sftn | Medium Risk closed | Risk Closed | 44853.5438 | Obs4 | The Occupant - Information Provided By The Court Manager | 45195 | Medium | Court Manager | CM and ROM to undertake PCFRA on all residents, current occupancy profile within the red fire box is not up to date. | Done
1405 | Ellis Gordon Court | ELLISGORD_S001 | H21 | Scheme | 2022-09-27 11:34 | FRA_1405260920221827.pdf | LingF | 1405260920221820 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | fni27xf0ew9l8k1tuy9 | Medium Risk closed | Risk Closed | 44833.4498 | Obs8 | Measures To Limit Fire Spread And Development | 45196 | Medium | Court Manager | Store 1 currently being used as a workshop, extension cables have been brought in to the room, evidence of power tools being used, | Arrangements have been for all the store room keys, electrical cupboards, plant room to be changed this week
1405 | Ellis Gordon Court | ELLISGORD_S001 | H21 | Scheme | 2022-09-27 11:34 | FRA_1405260920221827.pdf | LingF | 1405260920221820 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | 4ybfolhbjydl8k1qonb | Low Risk closed | Risk Closed | 44833.4506 | Obs8 | Measures To Limit Fire Spread And Development | 45562 | Low | Court Manager | Ensure all electric distribution cupboards remain locked. | This has been completed
1405 | Ellis Gordon Court | ELLISGORD_S001 | H21 | Scheme | 2022-09-27 11:34 | FRA_1405260920221827.pdf | LingF | 1405260920221820 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | 7qb6ou3vxc6l8j25xpd | Low Risk closed | Risk Closed | 44832.6145 | Obs14 | Access By Emergency Services | 45561 | Low | Court Manager | Key missing for the boiler room, not within key safe or safe box adjacent to the door. | I can confirm that the key for the boiler room is now within the key safe adjacent to the front entrance
1405 | Ellis Gordon Court | ELLISGORD_S001 | H21 | Scheme | 2022-09-27 11:34 | FRA_1405260920221827.pdf | LingF | 1405260920221820 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | 9qeopqzpxk7l8k1syba | Low Risk closed | Risk Closed | 44833.4529 | Obs8 | Measures To Limit Fire Spread And Development | 45562 | Low | Court Manager | Missing intu strips on basement store/activity room door | Forward to surveyor for action
1405 | Ellis Gordon Court | ELLISGORD_S001 | H21 | Scheme | 2022-09-27 11:34 | FRA_1405260920221827.pdf | LingF | 1405260920221820 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | 9m3owam48qil8j29nga | Low Risk closed | Risk Closed | 44833.4483 | Obs15 | Management Of Fire Safety | 45561 | Low | Court Manager | Following handover new CM to review the content of the fire folder and ensure information is current | Done
1407 | Cheriton Court | JBCHERITON_S001 | H21 | Scheme | 2022-10-20 14:24 | FRA_1407201020221241.pdf | LingF | 1407201020221240 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | b79o6m9b6yl9h0nvau | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45219 | Medium | Court Manager | Flat door wedged open | NULL
1407 | Cheriton Court | JBCHERITON_S001 | H21 | Scheme | 2022-10-20 14:24 | FRA_1407201020221241.pdf | LingF | 1407201020221240 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | b8pf9bx18l4l9gzuniu | Observation Only | Risk Open | NULL | Obs1 | The Building | NULL | N/A | Court Manager | Front elevation view showing extent of cladding | NULL
1407 | Cheriton Court | JBCHERITON_S001 | H21 | Scheme | 2022-10-20 14:24 | FRA_1407201020221241.pdf | LingF | 1407201020221240 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | gmluxb5otrvl9h29pey | Low Risk to be actioned | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | 45585 | Low | Court Manager | Residential profile within fire box appears to be out of date, ensure accurate information, All occupants identified as low risk with no support required to evac. | NULL
1407 | Cheriton Court | JBCHERITON_S001 | H21 | Scheme | 2022-10-20 14:24 | FRA_1407201020221241.pdf | LingF | 1407201020221240 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | gis2c1kwr0cl9h15i7a | Low Risk to be actioned | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | 45585 | Low | Court Manager | No communal detection within guestroom | NULL
1407 | Cheriton Court | JBCHERITON_S001 | H21 | Scheme | 2022-10-20 14:24 | FRA_1407201020221241.pdf | LingF | 1407201020221240 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | h4pp425vjidl9h17x32 | Observation Only | Risk Closed | 44876.4305 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Surveyor | Single storey flat roof extension to the Rear appears to be an open roof void separated from main residential areas by masonry construction | Information only
1407 | Cheriton Court | JBCHERITON_S001 | H21 | Scheme | 2022-10-20 14:24 | FRA_1407201020221241.pdf | LingF | 1407201020221240 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | pmyaidw8sql9h13v9h | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45219 | Medium | Court Manager | No door closer on guestroom door | NULL
1407 | Cheriton Court | JBCHERITON_S001 | H21 | Scheme | 2022-10-20 14:24 | FRA_1407201020221241.pdf | LingF | 1407201020221240 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | nrabrd91q1pl9h0jy2s | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45219 | Medium | Court Manager | Flat door closers (perko chain type) are showing signs of deterioration, a number failed to close into the frame. Doors left unlocked were able to swing in the draught due to loss of power. | NULL
1407 | Cheriton Court | JBCHERITON_S001 | H21 | Scheme | 2022-10-20 14:24 | FRA_1407201020221241.pdf | LingF | 1407201020221240 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | rw1goqebhpl9gzt5t5 | Observation Only | Risk Open | NULL | Obs1 | The Building | NULL | N/A | Court Manager | Rear elevation | NULL
1407 | Cheriton Court | JBCHERITON_S001 | H21 | Scheme | 2022-10-20 14:24 | FRA_1407201020221241.pdf | LingF | 1407201020221240 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | s1icszrbbrel9h1tnp8 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45585 | Low | Court Manager | Fire stopping required around 1st floor elec cupboard cupboard ceiling, using intumescent putty and ablative mineral slab close down gaps | NULL
1407 | Cheriton Court | JBCHERITON_S001 | H21 | Scheme | 2022-10-20 14:24 | FRA_1407201020221241.pdf | LingF | 1407201020221240 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | zvytq5cj2fdl9h0xsoc | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45585 | Low | Court Manager | Damaged caused to fire compartmentation, remove plastic panels and replace with rockwool compressed mineral quilt ablative slab mechanically fixed and point with mastic | NULL
1408 | Granville Court (Eastbourne) | JBGRANVILLE_S001 | H21 | Scheme | 2022-10-20 12:00 | FRA_1408201020221015.pdf | LingF | 1408201020221010 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | z2w3xsts03ll9gvvgvb | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45585 | Low | Court Manager | Stairwell door 1st floor not closing into frame fully | NULL
1408 | Granville Court (Eastbourne) | JBGRANVILLE_S001 | H21 | Scheme | 2022-10-20 12:00 | FRA_1408201020221015.pdf | LingF | 1408201020221010 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | yuo88v5f1zl9gxqil5 | Observation Only | Risk Open | NULL | Obs13 | Other Relevant Fixed Systems | NULL | N/A | Court Manager | Typical AOV window | NULL
1408 | Granville Court (Eastbourne) | JBGRANVILLE_S001 | H21 | Scheme | 2022-10-20 12:00 | FRA_1408201020221015.pdf | LingF | 1408201020221010 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | xkx2efz7gj9l9gwh8zl | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45585 | Low | Court Manager | Remove flammable Items from 2nd flr Tunstall cupboard | NULL
1408 | Granville Court (Eastbourne) | JBGRANVILLE_S001 | H21 | Scheme | 2022-10-20 12:00 | FRA_1408201020221015.pdf | LingF | 1408201020221010 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | tt3pvhjznyql9gvelrg | Observation Only | Risk Closed | 44876.4304 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel in test mode due to PPM underway | Info only
1408 | Granville Court (Eastbourne) | JBGRANVILLE_S001 | H21 | Scheme | 2022-10-20 12:00 | FRA_1408201020221015.pdf | LingF | 1408201020221010 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | meofvwyx1tml9gx8prf | Low Risk to be actioned | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | 45585 | Low | Court Manager | Resident profile within fire box appears to be out of date | NULL
1408 | Granville Court (Eastbourne) | JBGRANVILLE_S001 | H21 | Scheme | 2022-10-20 12:00 | FRA_1408201020221015.pdf | LingF | 1408201020221010 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | a53iiwp8qtjl9gx0gor | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45585 | Low | Court Manager | Flame retardant sheeting within lift | NULL
1408 | Granville Court (Eastbourne) | JBGRANVILLE_S001 | H21 | Scheme | 2022-10-20 12:00 | FRA_1408201020221015.pdf | LingF | 1408201020221010 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | f0qfw2jshqll9gxic3o | Low Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45585 | Low | Court Manager | Update occupancy profile | NULL
1408 | Granville Court (Eastbourne) | JBGRANVILLE_S001 | H21 | Scheme | 2022-10-20 12:00 | FRA_1408201020221015.pdf | LingF | 1408201020221010 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | cratrcyt65ll9gx3lzt | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | Information within fire box indicated all occupants to be low risk. | NULL
1408 | Granville Court (Eastbourne) | JBGRANVILLE_S001 | H21 | Scheme | 2022-10-20 12:00 | FRA_1408201020221015.pdf | LingF | 1408201020221010 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | 18p3obdf1lal9gulnri | Observation Only | Risk Open | NULL | Obs1 | The Building | NULL | N/A | Court Manager | General elevation view showing extent of cladding and balcony structures | NULL
1408 | Granville Court (Eastbourne) | JBGRANVILLE_S001 | H21 | Scheme | 2022-10-20 12:00 | FRA_1408201020221015.pdf | LingF | 1408201020221010 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | 235gwj85fufl9gwynre | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45585 | Low | Court Manager | Allow to refix loose or damaged sections of flame retardant sheeting within lift motor room | NULL
1501 | Howard Vyse Court | HOWARDVYSE_S001 | H21 | Scheme | 2022-08-09 11:08 | FRA_1501090820221007.pdf | CooneyE | 1501090820221000 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | 9hqxll8lgdwl6lz677s | Observation Only | Risk Closed | 44788.3697 | Obs14 | Access By Emergency Services | NULL | N/A | Other | For info : small parking area | info only. No actions required
1501 | Howard Vyse Court | HOWARDVYSE_S001 | H21 | Scheme | 2022-08-09 11:08 | FRA_1501090820221007.pdf | CooneyE | 1501090820221000 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | 8tg93owi1kll6lyuhip | Medium Risk closed | Risk Closed | 44875.5447 | Obs8 | Measures To Limit Fire Spread And Development | 45147 | Medium | Court Manager | Flats accessed via staircase ( 17 of) all require intumescent seals to doors/fire door hinges/intumescent letterplates and o/h door closers refixed as necessary | All 16x Fire doors fitted with the intumescent fire strip. Work completed 10/11/22.
1501 | Howard Vyse Court | HOWARDVYSE_S001 | H21 | Scheme | 2022-08-09 11:08 | FRA_1501090820221007.pdf | CooneyE | 1501090820221000 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | jpdqy52rvyl6lz1n0m | Low Risk closed | Risk Closed | 44874.3746 | Obs8 | Measures To Limit Fire Spread And Development | 45513 | Low | Court Manager | Electrical intake cupboard in communal lounge: Fireline board/intumescent seal around emergency light and holes above meter | Decorator instructed to carry out this work. Repair done and completed.
1501 | Howard Vyse Court | HOWARDVYSE_S001 | H21 | Scheme | 2022-08-09 11:08 | FRA_1501090820221007.pdf | CooneyE | 1501090820221000 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | i1qpssd91oql6lyrpbt | Observation Only | Risk Closed | 44788.3696 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Other | For info: Residents can smoke with thier own flats | info only. No actions required
1501 | Howard Vyse Court | HOWARDVYSE_S001 | H21 | Scheme | 2022-08-09 11:08 | FRA_1501090820221007.pdf | CooneyE | 1501090820221000 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | wan9k15scml6lz7irb | Observation Only | Risk Closed | 44788.3695 | Obs15 | Management Of Fire Safety | NULL | N/A | Other | For info: Testing recorded digital in house system - Pebbles - and part hard copy back up in file | info only. No actions required
1502 | Creasy Court | CREASY_S001 | H21 | Scheme | 2022-08-23 09:07 | FRA_1502230820220838.pdf | CooneyE | 1502230820220830 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | hksc5myxafkl75wc9e7 | Observation Only | Risk Open | NULL | Obs15 | Management Of Fire Safety | NULL | N/A | Other | For info : Testing information logged via in house digital system - Pebbles - with hard copy back up in file | NULL
1502 | Creasy Court | CREASY_S001 | H21 | Scheme | 2022-08-23 09:07 | FRA_1502230820220838.pdf | CooneyE | 1502230820220830 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | h1qjeaikqnhl75w3hfx | Low Risk closed | Risk Closed | 44817.5307 | Obs6 | Fire Hazards - Elimination & Control | 45527 | Low | Court Manager | Renew cleaning cupboard fire door inc. hinges and intumescent strips | Contractor supplied and fitted new door including hinges and intumescent strips
1502 | Creasy Court | CREASY_S001 | H21 | Scheme | 2022-08-23 09:07 | FRA_1502230820220838.pdf | CooneyE | 1502230820220830 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | gqpa2p6kps7l75wjmqo | Observation Only | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Other | For info : Flat 34 has oxygen cylinders for medical needs | NULL
1502 | Creasy Court | CREASY_S001 | H21 | Scheme | 2022-08-23 09:07 | FRA_1502230820220838.pdf | CooneyE | 1502230820220830 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | fz8juzdq8xpl75w9qxx | Observation Only | Risk Open | NULL | Obs15 | Management Of Fire Safety | NULL | N/A | Other | For info : Residents can smoke within properties | NULL
1502 | Creasy Court | CREASY_S001 | H21 | Scheme | 2022-08-23 09:07 | FRA_1502230820220838.pdf | CooneyE | 1502230820220830 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | k3xygp1gcf9l75waust | Observation Only | Risk Open | NULL | Obs15 | Management Of Fire Safety | NULL | N/A | Other | For info : Residents are requested to formally acknowledge fure policy at sign up | NULL
1502 | Creasy Court | CREASY_S001 | H21 | Scheme | 2022-08-23 09:07 | FRA_1502230820220838.pdf | CooneyE | 1502230820220830 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | 1lcuo8m300dl75w1nb0 | Low Risk closed | Risk Closed | 44817.5316 | Obs6 | Fire Hazards - Elimination & Control | 45527 | Low | Court Manager | Renew fire door inc. hinges and intumescent strips to electrical intake cupboard by 28-42 staircase. | Contractor supplied and fitted new fire door including hinges and intumescent strips to electrical intake room by 28-42 staircase
1515 | Heseltine Court | HESELTINE_S001 | H21 | Scheme | 2022-08-08 08:04 | FRA_1515080820220754.pdf | CooneyE | 1515080820220750 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | 1k5txp1hi0ajl6keml64 | Low Risk closed | Risk Closed | 44851.58 | Obs8 | Measures To Limit Fire Spread And Development | 45512 | Low | Court Manager | F24 : S/f surface mounted drop down smoke seal to bottom of front door | WO submitted
1515 | Heseltine Court | HESELTINE_S001 | H21 | Scheme | 2022-08-08 08:04 | FRA_1515080820220754.pdf | CooneyE | 1515080820220750 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | jwb2599j659l6keffqc | Low Risk closed | Risk Closed | 44851.5814 | Obs6 | Fire Hazards - Elimination & Control | 45163 | Low | Court Manager | Bicycles under staircase leading to fire exit potential trip hazard if knocked over | Still waiting for shed, purchased by kerb appeal fund to be put up,WO submitted, have been struggling to get a carpenter
1515 | Heseltine Court | HESELTINE_S001 | H21 | Scheme | 2022-08-08 08:04 | FRA_1515080820220754.pdf | CooneyE | 1515080820220750 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | n6e69b7gzmnl6kejudn | Low Risk closed | Risk Closed | 44851.5807 | Obs8 | Measures To Limit Fire Spread And Development | 45512 | Low | Court Manager | F30 : O/h front door to fully close | WO submitted, have been struggling to get a carpenter
1515 | Heseltine Court | HESELTINE_S001 | H21 | Scheme | 2022-08-08 08:04 | FRA_1515080820220754.pdf | CooneyE | 1515080820220750 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | hkxozslgcbjl6keikay | Low Risk closed | Risk Closed | 44851.5805 | Obs8 | Measures To Limit Fire Spread And Development | 45512 | Low | Court Manager | F34: O/h front door to fully self close | WO submitted, have been struggling to get a carpenter
1515 | Heseltine Court | HESELTINE_S001 | H21 | Scheme | 2022-08-08 08:04 | FRA_1515080820220754.pdf | CooneyE | 1515080820220750 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | vz15db86nal6keffrk | Observation Only | Risk Closed | 44788.3695 | Obs16 | Testing And Maintenance | NULL | N/A | Other | For info : Testing records digitally recorded via in house system - Pebbles- with hard copy back up in file | info only. No actions required
1515 | Heseltine Court | HESELTINE_S001 | H21 | Scheme | 2022-08-08 08:04 | FRA_1515080820220754.pdf | CooneyE | 1515080820220750 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | yt59j6wchhfl6kekiuo | Low Risk closed | Risk Closed | 44851.5809 | Obs8 | Measures To Limit Fire Spread And Development | 45512 | Low | Court Manager | F3 : O/h front door to fully self close | WO submitted, have been struggling to get a carpenter
1516 | Prail Court | PRAIL_S001 | H21 | Scheme | 2022-04-05 17:45 | FRA_1516050420221500.pdf | CooneyE | 1516050420221500 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | i4ccbw0b7e9l1md222y | Low Risk closed | Risk Closed | 44705.453 | Obs7 | Fire Protection Measures | 45387 | Low | Court Manager | Cabling in communal roof void by office penetrates fire wall , and should have intumescent putties applied. | putty put in place
1516 | Prail Court | PRAIL_S001 | H21 | Scheme | 2022-04-05 17:45 | FRA_1516050420221500.pdf | CooneyE | 1516050420221500 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | l78aofc83ddl1mdeksc | Observation Only | Risk Closed | 44778.7477 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Other | Residents can smoke within their flats | n/a observation only
1516 | Prail Court | PRAIL_S001 | H21 | Scheme | 2022-04-05 17:45 | FRA_1516050420221500.pdf | CooneyE | 1516050420221500 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | asgu2q3whyl1md4q8f | Low Risk closed | Risk Closed | 44705.4523 | Obs7 | Fire Protection Measures | 45387 | Low | Court Manager | Cabling to 1st floor cleaning cupboard to roof void requires intumescent putty to seal | putty put in place
1516 | Prail Court | PRAIL_S001 | H21 | Scheme | 2022-04-05 17:45 | FRA_1516050420221500.pdf | CooneyE | 1516050420221500 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | crlzm0t9eoel1md6voy | Observation Only | Risk Closed | 44778.7476 | Obs16 | Testing And Maintenance | NULL | N/A | Other | For info : Records kept in file and company digital system | n/a observation only
1517 | Banks Court | BANKS_S001 | H21 | Scheme | 2022-08-17 20:47 | FRA_1517170820222025.pdf | CooneyE | 1517170820222020 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | 3aa5wy7u66kl6y0njpt | Observation Only | Risk Closed | 44791.3773 | Obs14 | Access By Emergency Services | NULL | N/A | Other | For info Testing recorded via in house digital software - Pebbles - with hard copy back up within file | info only
1517 | Banks Court | BANKS_S001 | H21 | Scheme | 2022-08-17 20:47 | FRA_1517170820222025.pdf | CooneyE | 1517170820222020 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | i4n5zdo5k6l6y0m4va | Observation Only | Risk Closed | 44791.3772 | Obs14 | Access By Emergency Services | NULL | N/A | Other | For info Access to rear block of 16-36 narrow, and car park full. Limited space. | info only
1517 | Banks Court | BANKS_S001 | H21 | Scheme | 2022-08-17 20:47 | FRA_1517170820222025.pdf | CooneyE | 1517170820222020 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | udk7w4qnstol6y0q12c | Low Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45521 | Low | Court Manager | S/f intumescent putty around cable ceiling to store cupboard beside F25 | NULL
1517 | Banks Court | BANKS_S001 | H21 | Scheme | 2022-08-17 20:47 | FRA_1517170820222025.pdf | CooneyE | 1517170820222020 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | o43szjz68qgl6y0spli | Low Risk closed | Risk Closed | 44791.3023 | Obs15 | Management Of Fire Safety | 45521 | Low | Court Manager | Remove oxygen sticker to flat 1 communal corridor door if not required. | Sticker will remain in place due to the tenant having oxygen cylinders just in side of flat 1 main door.
1517 | Banks Court | BANKS_S001 | H21 | Scheme | 2022-08-17 20:47 | FRA_1517170820222025.pdf | CooneyE | 1517170820222020 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | y3vjsc7whtel6y0enmg | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45521 | Low | Court Manager | PAT testing required to 2 no Buggy batteries | NULL
1519 | Gordon Roughley Court | GORDONROUG_S001 | H21 | Scheme | 2022-07-25 10:03 | FRA_1519250720220918.pdf | CooneyE | 1519250720220910 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | vds3vgk122rl60i8jmo | Medium Risk closed | Risk Closed | 44768.5106 | Obs8 | Measures To Limit Fire Spread And Development | 45132 | Medium | Court Manager | F32 - O/h door closer to fully shut door | 26.7.22 door closer adjusted by handyperson who was on site
1519 | Gordon Roughley Court | GORDONROUG_S001 | H21 | Scheme | 2022-07-25 10:03 | FRA_1519250720220918.pdf | CooneyE | 1519250720220910 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | nx9hja7kaxnl60ib7ap | Low Risk closed | Risk Closed | 44778.6434 | Obs8 | Measures To Limit Fire Spread And Development | 45498 | Low | Court Manager | F16 - Door closes very heavily. Adjust to lighter close. | Handyman adjusted
1519 | Gordon Roughley Court | GORDONROUG_S001 | H21 | Scheme | 2022-07-25 10:03 | FRA_1519250720220918.pdf | CooneyE | 1519250720220910 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | nqqpu8653xl60hudmi | Observation Only | Risk Closed | 44778.7512 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Other | For info : Residents can smoke within individual flats | n/a observation only
1519 | Gordon Roughley Court | GORDONROUG_S001 | H21 | Scheme | 2022-07-25 10:03 | FRA_1519250720220918.pdf | CooneyE | 1519250720220910 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | ileaosfcm5l60icyfv | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45498 | Low | Other | H21 to confirm competent person arrangements for monthly testing of P50 fire extinguishers | NULL
1519 | Gordon Roughley Court | GORDONROUG_S001 | H21 | Scheme | 2022-07-25 10:03 | FRA_1519250720220918.pdf | CooneyE | 1519250720220910 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | 7svyrjirr3al60i08q3 | Medium Risk Overdue | Risk Open | NULL | Obs9 | Escape Lighting | 44789 | Medium | Surveyor | Emergency lights unable to be individually tested. Wiring to be investigated. | NULL
1519 | Gordon Roughley Court | GORDONROUG_S001 | H21 | Scheme | 2022-07-25 10:03 | FRA_1519250720220918.pdf | CooneyE | 1519250720220910 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | ebpcy3onovcl60i3qs1 | Observation Only | Risk Closed | 44778.7512 | Obs14 | Access By Emergency Services | NULL | N/A | Other | For info: front of Court has limited parking space | n/a observation only
1519 | Gordon Roughley Court | GORDONROUG_S001 | H21 | Scheme | 2022-07-25 10:03 | FRA_1519250720220918.pdf | CooneyE | 1519250720220910 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | a8mzhed7dorl60i5yiy | Observation Only | Risk Closed | 44768.51 | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | Testing recording via in house digital software -Pebbles- with some paper back up within fire file | As stated all information recorded on Pebbles
1519 | Gordon Roughley Court | GORDONROUG_S001 | H21 | Scheme | 2022-07-25 10:03 | FRA_1519250720220918.pdf | CooneyE | 1519250720220910 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | 8mn27ngcel60i9yhb | Medium Risk closed | Risk Closed | 44768.511 | Obs8 | Measures To Limit Fire Spread And Development | 45132 | Medium | Court Manager | F20 - O/h door closer to fully close door | Door closer adjusted by handyperson
1523 | Carne Rasch - Francis - Drake Courts | FRANCIS_S001 | H21 | Scheme | 2022-08-04 09:00 | FRA_1523040820220853.pdf | CooneyE | 1523040820220850 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | b3lk6y1js4l6eqrn8t | Observation Only | Risk Closed | 44778.7517 | Obs16 | Testing And Maintenance | NULL | N/A | Other | Residents required to formally acknowledge fire policy at sign up | n/a observation only
1523 | Carne Rasch - Francis - Drake Courts | FRANCIS_S001 | H21 | Scheme | 2022-08-04 09:00 | FRA_1523040820220853.pdf | CooneyE | 1523040820220850 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | bhsbbtl5v4l6eqrn5s | Low Risk closed | Risk Closed | 44804.6794 | Obs10 | Fire Safety And Notices | 45508 | Low | Court Manager | Francis Ct : Bin chamber door beside Flat 1 requires intumescent seal between wall/frame | WO riased and work completed by contractor
1523 | Carne Rasch - Francis - Drake Courts | FRANCIS_S001 | H21 | Scheme | 2022-08-04 09:00 | FRA_1523040820220853.pdf | CooneyE | 1523040820220850 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | 3xdk59wc3z2l6eqrn6s | Low Risk closed | Risk Closed | 44804.6802 | Obs10 | Fire Safety And Notices | 45508 | Low | Court Manager | Francis Ct : Renew storage room fire door beside Flat 1 with fire hinges / intumescent strips | Wo raised and completed by contractor
1523 | Carne Rasch - Francis - Drake Courts | FRANCIS_S001 | H21 | Scheme | 2022-08-04 09:00 | FRA_1523040820220853.pdf | CooneyE | 1523040820220850 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | mqesci75hhll6eqrn7s | Observation Only | Risk Closed | 44778.7519 | Obs15 | Management Of Fire Safety | NULL | N/A | Other | Testing digitally recorded via in house 'Pebbles' system , and partly hardcopied within file | n/a observation only
1523 | Carne Rasch - Francis - Drake Courts | FRANCIS_S001 | H21 | Scheme | 2022-08-04 09:00 | FRA_1523040820220853.pdf | CooneyE | 1523040820220850 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | nau1034hn2hl6eqrn3w | Observation Only | Risk Closed | 44778.7518 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Other | For info : Residents are allowed to smoke within their flats | n/a observation only
1523 | Carne Rasch - Francis - Drake Courts | FRANCIS_S001 | H21 | Scheme | 2022-08-04 09:00 | FRA_1523040820220853.pdf | CooneyE | 1523040820220850 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | w6r3da6ybkl6eqvtpj | Medium Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45142 | Medium | Court Manager | Francis Ct : Confirm that detectors in bin chamber and electrical intake cupboard are connected to Fire Alarm panel | NULL
1523 | Carne Rasch - Francis - Drake Courts | FRANCIS_S001 | H21 | Scheme | 2022-08-04 09:00 | FRA_1523040820220853.pdf | CooneyE | 1523040820220850 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | yhguc7k7uwl6eqrn4u | Low Risk closed | Risk Closed | 44805.6108 | Obs10 | Fire Safety And Notices | 45508 | Low | Court Manager | Carne Rasch Ct : Resite fire extinguisher from electrical intake cupboard to bin room next door | moved extingusher as requested to bin chamber
1580 | Hawthorns | HAWTHORNS_S001 | H21 | Scheme | 2022-02-11 08:04 | FRA_1580110220220733.pdf | CooneyE | 1580110220220730 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | xiw4ks9klockzi4531z | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 44968 | Medium | Court Manager | New emergency light required to ground floor of block 14 -18 | NULL
1580 | Hawthorns | HAWTHORNS_S001 | H21 | Scheme | 2022-02-11 08:04 | FRA_1580110220220733.pdf | CooneyE | 1580110220220730 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | kf1hwd16t3qkzi4cb70 | Medium Risk to be actioned | Risk Open | NULL | Obs16 | Testing And Maintenance | 44968 | Medium | Court Manager | Confirmation of Alarm triggerring to relevant Fire Zone Plan Chart to be sought by Ct Manager | NULL
1580 | Hawthorns | HAWTHORNS_S001 | H21 | Scheme | 2022-02-11 08:04 | FRA_1580110220220733.pdf | CooneyE | 1580110220220730 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | 5mk3m2flzvekzi42j77 | Observation Only | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Unable to confirm if day to day repair contractors complete hot works permit | NULL
1580 | Hawthorns | HAWTHORNS_S001 | H21 | Scheme | 2022-02-11 08:04 | FRA_1580110220220733.pdf | CooneyE | 1580110220220730 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 7 | 0uv9cca5voukzi3xgft | Medium Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 44968 | Medium | Court Manager | New Ct Manager to be attend relevant in house Fire Safey Warden training | NULL
1603 | Ross Willis Court | ROSSWILL_S001 | H21 | Scheme | 2021-12-24 12:17 | FRA_1603241220211204.pdf | AhmadW | 1603241220211200 | Retirement Housing | Mid South | Glos Oxford and South Bucks | South | South Patch 8 | x5trnjdbaahkxkcy560 | Medium Risk closed | Risk Closed | 44574.4983 | Obs8 | Measures To Limit Fire Spread And Development | 44919 | Medium | Court Manager | Flat 14 door requires adjystment on the closer | Handyman has adjusted the door closer
1603 | Ross Willis Court | ROSSWILL_S001 | H21 | Scheme | 2021-12-24 12:17 | FRA_1603241220211204.pdf | AhmadW | 1603241220211200 | Retirement Housing | Mid South | Glos Oxford and South Bucks | South | South Patch 8 | x5trnjdbaahkxkcy560 | Medium Risk closed | Risk Closed | 44606.4878 | Obs8 | Measures To Limit Fire Spread And Development | 44919 | Medium | Court Manager | Flat 14 door requires adjystment on the closer | This was requested twice by surveyor. Actioned - work order 1512113
1604 | Goode Court | GOODE_S001 | H21 | Scheme | 2022-02-04 14:38 | FRA_1604040220221406.pdf | AhmadW | 1604040220221400 | Retirement Housing | Mid South | Glos Oxford and South Bucks | South | South Patch 8 | c595ehb0u0ekz8heewz | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45326 | Low | Court Manager | Corridor door by guest room - magnetic release button not working | NULL
1605 | Morris Court | MORRIS_S001 | H21 | Scheme | 2022-01-20 13:59 | FRA_1605200120221321.pdf | AhmadW | 1605200120221320 | Retirement Housing | Mid South | Glos Oxford and South Bucks | South | South Patch 8 | hk40eq7rkojkyn0qonu | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 44946 | Medium | Court Manager | Corridor fire door by flat 14 not closing fully. | NULL
1607 | Cambrian Green Court | CAMBRIANGREEN_S001 | H21 | Scheme | 2022-02-01 16:10 | FRA_1607010220221606.pdf | AhmadW | 1607010220221600 | Extra Care | Extra Care Central | EC Central 1 | South | South Patch 8 | w4jzhvnc9nkz4bbx6x | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45323 | Low | Court Manager | Following corridor doors to be adjusted Between lift and flat 20 | NULL
1613 | Falcon Court | FALCON_S001 | H21 | Scheme | 2022-06-27 11:32 | FRA_1613270620221006.pdf | AhmadW | 1613270620221000 | Extra Care | Extra Care Central | EC Central 1 | South | South Patch 8 | ujvst23jh4l4wlf3b9 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45470 | Low | Court Manager | Seals around the glazing in lounge fire doors requires replacement. Beading and glazing to be removed from 2 no sets of doors to lounge. Reseal with intumescent "putty" and refit glazing and beads. | NULL
1615 | Edward Jenner Court | EDWARDJENNER_S001 | H21 | Scheme | 2022-10-17 15:32 | FRA_1615171020221408.pdf | fowlerb1 | 1615171020221400 | Extra Care | Extra Care Central | EC Central 1 | South | South Patch 2 | ugoj7azxt2jl9ct41ws | Observation Only | Risk Closed | 44852.3468 | Obs1 | The Building | NULL | N/A | Surveyor | There is no fire resistance provided by the balconies - this is for information only. | For information only
1615 | Edward Jenner Court | EDWARDJENNER_S001 | H21 | Scheme | 2022-10-17 15:32 | FRA_1615171020221408.pdf | fowlerb1 | 1615171020221400 | Extra Care | Extra Care Central | EC Central 1 | South | South Patch 2 | tuicr5yihxl9cumtv3 | Medium Risk closed | Risk Closed | 44861.6186 | Obs10 | Fire Safety And Notices | 45216 | Medium | Court Manager | Fire action notices required to staircase doors - existing shown for information only | Put signs up as advised by Brent Fowler surveyor
1615 | Edward Jenner Court | EDWARDJENNER_S001 | H21 | Scheme | 2022-10-17 15:32 | FRA_1615171020221408.pdf | fowlerb1 | 1615171020221400 | Extra Care | Extra Care Central | EC Central 1 | South | South Patch 2 | oz4zjl7cdgcl9curn7a | Observation Only | Risk Closed | 44852.3452 | Obs11 | Fire Fighting Equipment | NULL | N/A | Surveyor | FFE for information only | For information only
1615 | Edward Jenner Court | EDWARDJENNER_S001 | H21 | Scheme | 2022-10-17 15:32 | FRA_1615171020221408.pdf | fowlerb1 | 1615171020221400 | Extra Care | Extra Care Central | EC Central 1 | South | South Patch 2 | 8ypfnp9bhz6l9ctrgl1 | Observation Only | Risk Closed | 44852.3453 | Obs7 | Fire Protection Measures | NULL | N/A | Surveyor | Refer to fire safety strategy document in the O&M files - for information only | For
1702 | Albuhera Close | ALBUHERACLOS_S001 | H21 | Scheme | 2022-08-18 09:40 | FRA_1702180820220901.pdf | CooneyE | 1702180820220900 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | 0xmsklcuwzkml6ys2cr1 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45522 | Low | Court Manager | S/f hinges and intumescent strips to bin chamber doors x 4 | NULL
1702 | Albuhera Close | ALBUHERACLOS_S001 | H21 | Scheme | 2022-08-18 09:40 | FRA_1702180820220901.pdf | CooneyE | 1702180820220900 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | 1map8ourgthl6yrrm2x | Medium Risk closed | Risk Closed | 44792.5175 | Obs8 | Measures To Limit Fire Spread And Development | 44798 | Medium | Court Manager | S/f door closer to communal kitchen door | door closer fitted
1702 | Albuhera Close | ALBUHERACLOS_S001 | H21 | Scheme | 2022-08-18 09:40 | FRA_1702180820220901.pdf | CooneyE | 1702180820220900 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | 7lgxjozrwwgl6yrt2rl | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45163 | Low | Court Manager | 3 no sliding doors in communal lounge designated as fire exits. Rear door to used as fire exit with availability of appropriate single action latch release mechanism/new door installation to be investigated. | NULL
1702 | Albuhera Close | ALBUHERACLOS_S001 | H21 | Scheme | 2022-08-18 09:40 | FRA_1702180820220901.pdf | CooneyE | 1702180820220900 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | ogilrp65wil6yrxus1 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45522 | Low | Court Manager | Clear stairwells of combustibles near flats 33 & 36 | NULL
1702 | Albuhera Close | ALBUHERACLOS_S001 | H21 | Scheme | 2022-08-18 09:40 | FRA_1702180820220901.pdf | CooneyE | 1702180820220900 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | ugx21yisdeml6ys7jf2 | Low Risk closed | Risk Closed | 44825.6428 | Obs8 | Measures To Limit Fire Spread And Development | 45522 | Low | Court Manager | S/f closer to guest room lobby door | completed on handyman
1702 | Albuhera Close | ALBUHERACLOS_S001 | H21 | Scheme | 2022-08-18 09:40 | FRA_1702180820220901.pdf | CooneyE | 1702180820220900 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | s2r017lte6l6ys9glm | Low Risk closed | Risk Closed | 44851.5978 | Obs10 | Fire Safety And Notices | 45522 | Low | Court Manager | Indicate fire assembly points on all Fire Notices | double checked and all correct
1702 | Albuhera Close | ALBUHERACLOS_S001 | H21 | Scheme | 2022-08-18 09:40 | FRA_1702180820220901.pdf | CooneyE | 1702180820220900 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | rvuge0w6qhpl6ysbm4d | Observation Only | Risk Open | NULL | Obs14 | Access By Emergency Services | NULL | N/A | Other | For info : Access via front of Court restricted with full car park | NULL
1702 | Albuhera Close | ALBUHERACLOS_S001 | H21 | Scheme | 2022-08-18 09:40 | FRA_1702180820220901.pdf | CooneyE | 1702180820220900 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | gpu8aih1jtbl6ysdpv5 | Observation Only | Risk Open | NULL | Obs15 | Management Of Fire Safety | NULL | N/A | Other | For info : Testing recorded digitally via in house software - Pebbles- with hard copy back up in file | NULL
1702 | Albuhera Close | ALBUHERACLOS_S001 | H21 | Scheme | 2022-08-18 09:40 | FRA_1702180820220901.pdf | CooneyE | 1702180820220900 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | murqc76pojgl6ysffja | Observation Only | Risk Open | NULL | Obs15 | Management Of Fire Safety | NULL | N/A | Other | Ct Manager arranges regular visits from local fire brigade, who are available to address concerns from residents | NULL
1702 | Albuhera Close | ALBUHERACLOS_S001 | H21 | Scheme | 2022-08-18 09:40 | FRA_1702180820220901.pdf | CooneyE | 1702180820220900 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | w3wq7urzqtl6yrzf67 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45522 | Low | Court Manager | S/f fire hinges and intumescent strips to electrical intake cupboard doors near flats 16, 20 & 45 | NULL
1702 | Albuhera Close | ALBUHERACLOS_S001 | H21 | Scheme | 2022-08-18 09:40 | FRA_1702180820220901.pdf | CooneyE | 1702180820220900 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | wd8mfs7nbnl6yrwjlx | Low Risk closed | Risk Closed | 44825.6429 | Obs8 | Measures To Limit Fire Spread And Development | 45522 | Low | Court Manager | Remove fire exit signs to 2 no sliding doors in communal lounge | removed on handyman visit
1704 | Kenneth Chambers Court | KENNETHCHAM_S001 | H21 | Scheme | 2022-05-04 15:29 | FRA_1704040520221458.pdf | CooneyE | 1704040520221450 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | vxx0yq1tzzrl2ro5hb8 | Observation Only | Risk Closed | 44778.7481 | Obs15 | Management Of Fire Safety | NULL | N/A | Other | All tests completed within fire file, and digitally lodged via in house 'Pebbles' system | n/a observation only
1704 | Kenneth Chambers Court | KENNETHCHAM_S001 | H21 | Scheme | 2022-05-04 15:29 | FRA_1704040520221458.pdf | CooneyE | 1704040520221450 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | 4lys7r0tuecl2ro3m2n | Observation Only | Risk Closed | 44778.7481 | Obs14 | Access By Emergency Services | NULL | N/A | Other | Small car park area | n/a observation only
1709 | Stoneleigh Court | STONELEIGH_S001 | H21 | Scheme | 2022-08-24 10:29 | FRA_1709240820220939.pdf | CooneyE | 1709240820220930 | Retirement Housing | London Kent | North and East London | Central | Central Patch 8 | 39w2sxa93wcl77dqbsk | Low Risk closed | Risk Closed | 44854.6525 | Obs6 | Fire Hazards - Elimination & Control | 45528 | Low | Court Manager | PAT test required to 2 no buggy batteries | PAT testing has been carried out at Stoneleigh Court today 20/10/2022. 3 mobility scooter chargers have been tested.
1709 | Stoneleigh Court | STONELEIGH_S001 | H21 | Scheme | 2022-08-24 10:29 | FRA_1709240820220939.pdf | CooneyE | 1709240820220930 | Retirement Housing | London Kent | North and East London | Central | Central Patch 8 | cdrrdbttj6il77efqey | Low Risk closed | Risk Closed | 44834.7383 | Obs6 | Fire Hazards - Elimination & Control | 45528 | Low | Court Manager | Fixed sockets required to office to pevent excessive extension lead use | WO 1566194 raised and work now completed
1709 | Stoneleigh Court | STONELEIGH_S001 | H21 | Scheme | 2022-08-24 10:29 | FRA_1709240820220939.pdf | CooneyE | 1709240820220930 | Retirement Housing | London Kent | North and East London | Central | Central Patch 8 | dtniv9qrxaql77dz3z7 | Medium Risk closed | Risk Closed | 44820.578 | Obs8 | Measures To Limit Fire Spread And Development | 45162 | Medium | Court Manager | FB door lock to electrical intake cupboard near flat 8 faulty and to be renewed | WO 1558907 raised 26/08/22 and work completed on 19/09/22
1709 | Stoneleigh Court | STONELEIGH_S001 | H21 | Scheme | 2022-08-24 10:29 | FRA_1709240820220939.pdf | CooneyE | 1709240820220930 | Retirement Housing | London Kent | North and East London | Central | Central Patch 8 | gr1mx1uoviil77eauja | Medium Risk to be actioned | Risk Open | NULL | Obs12 | Automatic Fire Systems i.e. Suppression System | 45162 | Medium | M&E Team | Unable to confirm servicing of automatic communal kitchen shutter | NULL
1709 | Stoneleigh Court | STONELEIGH_S001 | H21 | Scheme | 2022-08-24 10:29 | FRA_1709240820220939.pdf | CooneyE | 1709240820220930 | Retirement Housing | London Kent | North and East London | Central | Central Patch 8 | nqwq9chjg0cl77e1r9u | Low Risk closed | Risk Closed | 44803.6691 | Obs8 | Measures To Limit Fire Spread And Development | 45528 | Low | Court Manager | Store room cupboard door beside by ground floor electrical intake cupboard door doesn't freely close. | Works order 1558907 raised and work completed on 30/08/2022
1709 | Stoneleigh Court | STONELEIGH_S001 | H21 | Scheme | 2022-08-24 10:29 | FRA_1709240820220939.pdf | CooneyE | 1709240820220930 | Retirement Housing | London Kent | North and East London | Central | Central Patch 8 | q5n9ls078pgl77e6hiy | Medium Risk closed | Risk Closed | 44880.625 | Obs8 | Measures To Limit Fire Spread And Development | 44798 | Medium | Court Manager | No smoke detector found in cupboard beside flat 52. Ct Manager having issues with approved contractor completing works | On closer inspection this cupboard does have a detector fitted but could not be seen until we were able to step into the cupboard.
1709 | Stoneleigh Court | STONELEIGH_S001 | H21 | Scheme | 2022-08-24 10:29 | FRA_1709240820220939.pdf | CooneyE | 1709240820220930 | Retirement Housing | London Kent | North and East London | Central | Central Patch 8 | x0zblozw5pol77e5250 | Medium Risk closed | Risk Closed | 44902.5672 | Obs8 | Measures To Limit Fire Spread And Development | 44798 | Medium | Court Manager | Some corridor lobby fire doors wedged open | Openview attended today and completed the required work to fit magnets to the corridor fire doors on level 4 & 5 conservatory area.
1710 | Kelvedon Lodge | KELVEDONLODG_S001 | H21 | Scheme | 2022-08-19 11:04 | FRA_1710190820221100.pdf | CooneyE | 1710190820221100 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | wzirpbs4zil70awqrd | Observation Only | Risk Open | NULL | Obs14 | Access By Emergency Services | NULL | N/A | Other | Fire engine access via rear only through small car park | NULL
1710 | Kelvedon Lodge | KELVEDONLODG_S001 | H21 | Scheme | 2022-08-19 11:04 | FRA_1710190820221100.pdf | CooneyE | 1710190820221100 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | ph2htgexb9pl70awqpe | Medium Risk closed | Risk Closed | 44804.4005 | Obs7 | Fire Protection Measures | 45157 | Medium | Court Manager | Communal door to flats 15-20 doesn't fully freely close | Repaired by Silenster
1710 | Kelvedon Lodge | KELVEDONLODG_S001 | H21 | Scheme | 2022-08-19 11:04 | FRA_1710190820221100.pdf | CooneyE | 1710190820221100 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | 8sh3ngorly2l70awqqd | Medium Risk closed | Risk Closed | 44804.4236 | Obs8 | Measures To Limit Fire Spread And Development | 45157 | Medium | Court Manager | Flat 18 : refix disabled perko to front door | Repaired on job 1556616
1710 | Kelvedon Lodge | KELVEDONLODG_S001 | H21 | Scheme | 2022-08-19 11:04 | FRA_1710190820221100.pdf | CooneyE | 1710190820221100 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | ap7vax1u3wwl70ayclv | Medium Risk closed | Risk Closed | 44804.4227 | Obs8 | Measures To Limit Fire Spread And Development | 45157 | Medium | Court Manager | Reading room : disconnected door closer to be refixed | Repaired on job 1557583
1710 | Kelvedon Lodge | KELVEDONLODG_S001 | H21 | Scheme | 2022-08-19 11:04 | FRA_1710190820221100.pdf | CooneyE | 1710190820221100 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | 52k67vqmx2al70awqsl | Observation Only | Risk Open | NULL | Obs16 | Testing And Maintenance | NULL | N/A | Other | Testing recorded digitally by in house system - Pebbles | NULL
1711 | Hatfield Lodge | HATFIELDCLOS_S001 | H21 | Scheme | 2022-09-01 10:46 | FRA_1711010920221012.pdf | CooneyE | 1711010920221010 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | ev4iytmvlcbl7iuelwn | Observation Only | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Other | For info : Residents can smoke within their own flat | NULL
1711 | Hatfield Lodge | HATFIELDCLOS_S001 | H21 | Scheme | 2022-09-01 10:46 | FRA_1711010920221012.pdf | CooneyE | 1711010920221010 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | btgcr5ssc2ql7iuqith | Observation Only | Risk Open | NULL | Obs15 | Management Of Fire Safety | NULL | N/A | Other | For info: Testing recorded via in house digital software - Pebbles- with hard copy file back up | NULL
1711 | Hatfield Lodge | HATFIELDCLOS_S001 | H21 | Scheme | 2022-09-01 10:46 | FRA_1711010920221012.pdf | CooneyE | 1711010920221010 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | rlawc5rqd0ml7iun3r0 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45536 | Low | Court Manager | Fire notices to be updated to new H21 format | NULL
1711 | Hatfield Lodge | HATFIELDCLOS_S001 | H21 | Scheme | 2022-09-01 10:46 | FRA_1711010920221012.pdf | CooneyE | 1711010920221010 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | n3bhw5e7pqnl7iu4vkv | Observation Only | Risk Open | NULL | Obs1 | The Building | NULL | N/A | Other | For info: unable to view loft space | NULL
1711 | Hatfield Lodge | HATFIELDCLOS_S001 | H21 | Scheme | 2022-09-01 10:46 | FRA_1711010920221012.pdf | CooneyE | 1711010920221010 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | m91itrt38lpl7iugfm7 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45536 | Low | Court Manager | S/f fire exit signs to push bar doors in communal lounge, and fit call point beside | NULL
1712 | Jubilee Lodge | JUBILEELODG_S001 | H21 | Scheme | 2022-08-02 08:59 | FRA_1712020820220819.pdf | CooneyE | 1712020820220810 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | jyar0bicj9l6bv7jlf | Observation Only | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | NULL | N/A | Court Manager | No full time Ct Manager. Court being temp covered with area Ct Managers on rotation basis. | NULL
1712 | Jubilee Lodge | JUBILEELODG_S001 | H21 | Scheme | 2022-08-02 08:59 | FRA_1712020820220819.pdf | CooneyE | 1712020820220810 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | rltsvg9nkyl6bv2tng | Observation Only | Risk Open | NULL | Obs1 | The Building | NULL | N/A | Surveyor | N/a gained to loft space | NULL
1712 | Jubilee Lodge | JUBILEELODG_S001 | H21 | Scheme | 2022-08-02 08:59 | FRA_1712020820220819.pdf | CooneyE | 1712020820220810 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | dsku28tlaz9l6bvvprw | Observation Only | Risk Closed | 44778.7516 | Obs15 | Management Of Fire Safety | NULL | N/A | Other | For info : Testing digitally recorded by in house 'Pebbles' system with some hard copy back up in file | n/a observation only
1712 | Jubilee Lodge | JUBILEELODG_S001 | H21 | Scheme | 2022-08-02 08:59 | FRA_1712020820220819.pdf | CooneyE | 1712020820220810 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | as6lmnj1ar8l6bvp2yw | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45143 | Low | Court Manager | Fire notice signs to indicate fire assembly points and residents informed. | NULL
1712 | Jubilee Lodge | JUBILEELODG_S001 | H21 | Scheme | 2022-08-02 08:59 | FRA_1712020820220819.pdf | CooneyE | 1712020820220810 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | xvde2ngsx0pl6bvyg3t | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45140 | Medium | Court Manager | F20 & F21 have perko door closers disabled. Reinstate to allow automatic door closing | NULL
1712 | Jubilee Lodge | JUBILEELODG_S001 | H21 | Scheme | 2022-08-02 08:59 | FRA_1712020820220819.pdf | CooneyE | 1712020820220810 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | wpvtzwm61yil6bvf0cp | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45506 | Low | Surveyor | Open corridor fire doors (×8) confirmation of requirements to be sought from Fire Brigade | NULL
1713 | Chartwell House (Barkingside) | CHARTWELLHOUS_S001 | H21 | Scheme | 2022-05-12 09:51 | FRA_1713120520220904.pdf | CooneyE | 1713120520220900 | Retirement Housing | London Kent | North and East London | Central | Central Patch 4 | 0bace2dvt11l32rl6ru | Low Risk closed | Risk Closed | 44778.7485 | Obs7 | Fire Protection Measures | 45066 | Low | Other | Unable to confirm integrity of floor/ceilings to service areas. Type 4 investigation required | n/a observation only
1713 | Chartwell House (Barkingside) | CHARTWELLHOUS_S001 | H21 | Scheme | 2022-05-12 09:51 | FRA_1713120520220904.pdf | CooneyE | 1713120520220900 | Retirement Housing | London Kent | North and East London | Central | Central Patch 4 | ibe69y96vidl32rny7v | Low Risk closed | Risk Closed | 44746.5817 | Obs7 | Fire Protection Measures | 45424 | Low | Court Manager | Small area of ceiling cut out to store room beside 1st floor lift to be recovered with 1/2 hr fire resistant board | Repair raised ceiling fixed using fire retardant plaster board
1716 | Churchill Lodge | CHURCHILL_S001 | H21 | Scheme | 2022-05-12 09:03 | FRA_1716120520220806.pdf | CooneyE | 1716120520220800 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | i820n33ip2el32pijky | Low Risk closed | Risk Closed | 44706.4748 | Obs6 | Fire Hazards - Elimination & Control | 45424 | Low | Court Manager | Some combustibles to ground floor store room by lift to be removed | Remove all combustables
1716 | Churchill Lodge | CHURCHILL_S001 | H21 | Scheme | 2022-05-12 09:03 | FRA_1716120520220806.pdf | CooneyE | 1716120520220800 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | iv0b5ah6zhbl32pf0d3 | Observation Only | Risk Closed | 44778.7482 | Obs15 | Management Of Fire Safety | NULL | N/A | Other | Records kept digitally via in house software with hard copy back ups | n/a observation only
1716 | Churchill Lodge | CHURCHILL_S001 | H21 | Scheme | 2022-05-12 09:03 | FRA_1716120520220806.pdf | CooneyE | 1716120520220800 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | u5u5p8mvggpl32pndsi | Observation Only | Risk Closed | 44778.7483 | Obs1 | The Building | NULL | N/A | Other | Unable to view roof void | n/a observation only
1716 | Churchill Lodge | CHURCHILL_S001 | H21 | Scheme | 2022-05-12 09:03 | FRA_1716120520220806.pdf | CooneyE | 1716120520220800 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | 3my4zizet3rl32p05t2 | Low Risk closed | Risk Closed | 44778.7484 | Obs6 | Fire Hazards - Elimination & Control | 45424 | Low | Other | Car crash impact damage to day centre entrance of Court. Area boarded over and Heras fenced off | n/a observation only
1716 | Churchill Lodge | CHURCHILL_S001 | H21 | Scheme | 2022-05-12 09:03 | FRA_1716120520220806.pdf | CooneyE | 1716120520220800 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | zdg2bywi94ll32pdw9o | Low Risk closed | Risk Closed | 44706.4741 | Obs15 | Management Of Fire Safety | 45424 | Low | Court Manager | Fire zone chart to be fixed to entrance wall | Zone chart now attached to the wall
1721 | Peacock Close | PEACOCKCLOS_S001 | H21 | Scheme | 2021-11-24 09:27 | FRA_1721241120210844.pdf | CooneyE | 1721241120210840 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | zt8cfn6s9nkwdb4ktd | Low Risk closed | Risk Closed | 44529.4391 | Obs6 | Fire Hazards - Elimination & Control | 45254 | Low | Court Manager | Extension leads in office overloaded, and fixed twin sockets required | Extension leads in office overloaded, and fixed twin sockets required, this will be raised to the Electrician for fixes.
1721 | Peacock Close | PEACOCKCLOS_S001 | H21 | Scheme | 2021-11-24 09:27 | FRA_1721241120210844.pdf | CooneyE | 1721241120210840 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | v995wwfckzkwdb9jxs | Low Risk closed | Risk Closed | 44529.4285 | Obs8 | Measures To Limit Fire Spread And Development | 45254 | Low | Court Manager | Corridor door leading to rear of Court can be utilsed as fire escape if lock changed and appropriate signage installed | I would have the reinstated by the locksmith to be utilsed as fire escape get the lock changed with the appropriate signage installed
1721 | Peacock Close | PEACOCKCLOS_S001 | H21 | Scheme | 2021-11-24 09:27 | FRA_1721241120210844.pdf | CooneyE | 1721241120210840 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | wvlifo58vghkwdayyop | Medium Risk closed | Risk Closed | 44529.435 | Obs16 | Testing And Maintenance | 44889 | Medium | Court Manager | Communal lounge door doesn't automatically close when pushed back too far | The current door has to be raised for repairs ajustment
1721 | Peacock Close | PEACOCKCLOS_S001 | H21 | Scheme | 2021-11-24 09:27 | FRA_1721241120210844.pdf | CooneyE | 1721241120210840 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | 2b3juslhxmikwdbc7wd | Observation Only | Risk Open | NULL | Obs16 | Testing And Maintenance | NULL | N/A | Other | For info: testing recorded via in house digital system and backed up in file | NULL
1721 | Peacock Close | PEACOCKCLOS_S001 | H21 | Scheme | 2021-11-24 09:27 | FRA_1721241120210844.pdf | CooneyE | 1721241120210840 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | 05f0yx0wyhifkwdb2tde | Low Risk closed | Risk Closed | 44529.4368 | Obs2 | Means Of Giving Warning In Case Of Fire | 45254 | Low | Court Manager | No detectors in electrical intake cupboard or refuse areas | To be addressed with Appello why this areas have been missed out with no detectors in electrical intake cupboard or refuse areas
1721 | Peacock Close | PEACOCKCLOS_S001 | H21 | Scheme | 2021-11-24 09:27 | FRA_1721241120210844.pdf | CooneyE | 1721241120210840 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | 0ncytg0ytvfkwdb0pc7 | Medium Risk closed | Risk Closed | 44529.4336 | Obs16 | Testing And Maintenance | 44889 | Medium | Court Manager | Guest room/library/laundry doors do not fully close | Door to be reinstated for proper fire door closure
1721 | Peacock Close | PEACOCKCLOS_S001 | H21 | Scheme | 2021-11-24 09:27 | FRA_1721241120210844.pdf | CooneyE | 1721241120210840 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | 1d4pcxmbog6kwda6hks | Medium Risk closed | Risk Closed | 44529.4323 | Obs6 | Fire Hazards - Elimination & Control | 44889 | Medium | Court Manager | Serving hatch to communal kitchen, with no automatic shutter in a fire event | Automatic shutter can have to put in place for replacement to current shutter
1721 | Peacock Close | PEACOCKCLOS_S001 | H21 | Scheme | 2021-11-24 09:27 | FRA_1721241120210844.pdf | CooneyE | 1721241120210840 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | 9dqgsvigcgqkwdb7vhh | Low Risk closed | Risk Closed | 44529.4609 | Obs8 | Measures To Limit Fire Spread And Development | 45254 | Low | Court Manager | Service fire door by flat 8 doesn't fully lock | Flat 18 will be raised to lock smith to fix
1721 | Peacock Close | PEACOCKCLOS_S001 | H21 | Scheme | 2021-11-24 09:27 | FRA_1721241120210844.pdf | CooneyE | 1721241120210840 | Retirement Housing | London Kent | North and East London | Central | Central Patch 7 | httbuq0537gkwdauhq6 | Low Risk closed | Risk Closed | 44529.458 | Obs10 | Fire Safety And Notices | 45254 | Low | Court Manager | Assemby point to be completed on Fire Notices | CM to complete Assembly point t on Fire Notices
1733 | Cinnamon Court,Cinnamon Court Day Centre | CINNAMON_S001 | H21 | Scheme | 2022-06-08 08:14 | FRA_1733080620220809.pdf | BhopalP | 1733080620220800 | Extra Care | Extra Care South | EC South 2 | South | South Patch 6 | joqjsznc3tdl45932ur | Observation Only | Risk Closed | 44806.5651 | Obs5 | Evacuation Strategy And Training | NULL | N/A | Court Manager | 2 Care Staff need to complete their Afire Safet awareness course. | No Need actions
1734 | Cedar Court Day Centre,Cedar Court (Lewi | CEDAR_S001 | H21 | Scheme | 2022-07-02 13:08 | FRA_1734010720222217.pdf | BhopalP | 1734010720222210 | Extra Care | Extra Care South | EC South 2 | South | South Patch 6 | ofvdq5bw0trl52yivzb | Observation Only | Risk Closed | 44832.3866 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | There are some left to complete. | No actions required to be taken.
1735 | Lordship Court | LORDSHIP_S001 | H21 | Scheme | 2022-05-27 13:31 | FRA_1735250520221138.pdf | BhopalP | 1735250520221130 | Retirement Housing | London Kent | South London and Surrey | South | South Patch 6 | s32e8dlo8ol3lgh69u | Observation Only | Risk Closed | 44711.4181 | Obs14 | Access By Emergency Services | NULL | N/A | Court Manager | Car park and the basement | Fire brigade spoke to the resident . Resident is aware of the risk of fire .Resident has informed me that she now remains in the room when cooking .
1735 | Lordship Court | LORDSHIP_S001 | H21 | Scheme | 2022-05-27 13:31 | FRA_1735250520221138.pdf | BhopalP | 1735250520221130 | Retirement Housing | London Kent | South London and Surrey | South | South Patch 6 | up3isl1zlgbl3lgek3u | Observation Only | Risk Closed | 44711.4156 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | Resident of 11 is a heavy smoker. FIRE services have provided him with fire retardant bedding. | Fire brigade visited twice regarding the issues of concerns raised .Family member supporting the resident with clutter in the flat fire brigade happy with difference .Social services called the resident due to fire brigade raising concern .Resident has capacity and does not require any further support.Social services called to confirm referral closed .
1736 | Paines Brook Court | PAINESBROOK_S001 | H21 | Scheme | 2022-06-17 12:56 | FRA_1736170620221218.pdf | CooneyE | 1736170620221210 | Extra Care | Extra Care South | EC South 2 | Central | Central Patch 7 | xpq16ihcykl4idkarc | Low Risk closed | Risk Closed | 44778.75 | Obs6 | Fire Hazards - Elimination & Control | 45460 | Low | Other | For info : residents are allowed to smoke within their flats | n/a observation only
1736 | Paines Brook Court | PAINESBROOK_S001 | H21 | Scheme | 2022-06-17 12:56 | FRA_1736170620221218.pdf | CooneyE | 1736170620221210 | Extra Care | Extra Care South | EC South 2 | Central | Central Patch 7 | tth73tzuhyl4idiwcw | Low Risk closed | Risk Closed | 44734.6601 | Obs6 | Fire Hazards - Elimination & Control | 45460 | Low | Court Manager | Store room beside flat 17 requires some clearance of archived files | Email request to Tapestry to clear all archived files by July 2022
1736 | Paines Brook Court | PAINESBROOK_S001 | H21 | Scheme | 2022-06-17 12:56 | FRA_1736170620221218.pdf | CooneyE | 1736170620221210 | Extra Care | Extra Care South | EC South 2 | Central | Central Patch 7 | l1yunjbxcpl4ie263e | Medium Risk closed | Risk Closed | 44734.6529 | Obs15 | Management Of Fire Safety | 45094 | Medium | Court Manager | Only 1 care worker on during nights covering 63 units. | Email notification to care provider about concerns raised
1736 | Paines Brook Court | PAINESBROOK_S001 | H21 | Scheme | 2022-06-17 12:56 | FRA_1736170620221218.pdf | CooneyE | 1736170620221210 | Extra Care | Extra Care South | EC South 2 | Central | Central Patch 7 | j4kuf1i5hcrl4ie53ot | Low Risk closed | Risk Closed | 44739.4823 | Obs16 | Testing And Maintenance | 45460 | Low | Court Manager | O/h door closer to library | Allocated to AHM
1736 | Paines Brook Court | PAINESBROOK_S001 | H21 | Scheme | 2022-06-17 12:56 | FRA_1736170620221218.pdf | CooneyE | 1736170620221210 | Extra Care | Extra Care South | EC South 2 | Central | Central Patch 7 | dwiextrpjiel4ie8in5 | Observation Only | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Surveyor | Unable to confirm full fire integrity of sevice area. Type 4 survey required to establish. | NULL
1736 | Paines Brook Court | PAINESBROOK_S001 | H21 | Scheme | 2022-06-17 12:56 | FRA_1736170620221218.pdf | CooneyE | 1736170620221210 | Extra Care | Extra Care South | EC South 2 | Central | Central Patch 7 | c13tqjbl76tl4idntw0 | Low Risk closed | Risk Closed | 44739.4802 | Obs6 | Fire Hazards - Elimination & Control | 45460 | Low | Court Manager | Roof access fire door to be kept locked and eased ( beside guest room 2). Remove paint and insulation to same room | Task allocated to AHM
1736 | Paines Brook Court | PAINESBROOK_S001 | H21 | Scheme | 2022-06-17 12:56 | FRA_1736170620221218.pdf | CooneyE | 1736170620221210 | Extra Care | Extra Care South | EC South 2 | Central | Central Patch 7 | 1l926o6eob6l4ie0npb | Observation Only | Risk Closed | 44778.7499 | Obs15 | Management Of Fire Safety | NULL | N/A | Other | For info | n/a observation only
1736 | Paines Brook Court | PAINESBROOK_S001 | H21 | Scheme | 2022-06-17 12:56 | FRA_1736170620221218.pdf | CooneyE | 1736170620221210 | Extra Care | Extra Care South | EC South 2 | Central | Central Patch 7 | 3plch2oty2ml4idlzon | Medium Risk closed | Risk Closed | 44739.482 | Obs6 | Fire Hazards - Elimination & Control | 45094 | Medium | Court Manager | Fire door to electrical intake within plant room to be kept locked shut | Allocated to AHM
1736 | Paines Brook Court | PAINESBROOK_S001 | H21 | Scheme | 2022-06-17 12:56 | FRA_1736170620221218.pdf | CooneyE | 1736170620221210 | Extra Care | Extra Care South | EC South 2 | Central | Central Patch 7 | 4dcn6srl38tl4idyv5k | Observation Only | Risk Closed | 44778.7498 | Obs14 | Access By Emergency Services | NULL | N/A | Other | For info : small car park for FB access | n/a observation only
1737 | Greenrod Place | GREENRODPLAC_S001 | H21 | Scheme | 2021-12-09 12:05 | FRA_1737091220211159.pdf | GerrishR | 1737091220211150 | Extra Care | Extra Care South | EC South 3 | South | South Patch 7 | 2qh4a04fqqrkwywv4ll | Low Risk closed | Risk Closed | 44565.6225 | Obs6 | Fire Hazards - Elimination & Control | 45269 | Low | Court Manager | Carried out by handyman twice a week. | Carried out by handy man twice weekly.
1737 | Greenrod Place | GREENRODPLAC_S001 | H21 | Scheme | 2021-12-09 12:05 | FRA_1737091220211159.pdf | GerrishR | 1737091220211150 | Extra Care | Extra Care South | EC South 3 | South | South Patch 7 | vdbkdx0lurkkwywqg86 | High Risk Closed | Risk Closed | 44565.6216 | Obs7 | Fire Protection Measures | 44629 | High | Court Manager | Flat 43 charging mobility scooter in hallway near fire exit door on stairwell. | Sent letter informing resident that the scooter was a fire risk. Resident has removed and placed in buggy room.
1737 | Greenrod Place | GREENRODPLAC_S001 | H21 | Scheme | 2021-12-09 12:05 | FRA_1737091220211159.pdf | GerrishR | 1737091220211150 | Extra Care | Extra Care South | EC South 3 | South | South Patch 7 | vdbkdx0lurkkwywqg86 | High Risk Closed | Risk Closed | 44565.622 | Obs7 | Fire Protection Measures | 44629 | High | Court Manager | Flat 43 charging mobility scooter in hallway near fire exit door on stairwell. | Moved to buggy room
1739 | Dymond House | DYMOND_S001 | H21 | Scheme | 2022-06-15 12:24 | FRA_1739150620221136.pdf | GerrishR | 1739150620221130 | Extra Care | Extra Care South | EC South 2 | South | South Patch 7 | 6m5ghkey8uwl4fgxoxv | Observation Only | Risk Open | NULL | Obs11 | Fire Fighting Equipment | NULL | N/A | M&E Team | Not to be removed, design and installed from construction as per fire regulations. | NULL
1740 | Lime Tree House | LIMETREEHSE_S001 | H21 | Scheme | 2022-01-19 21:21 | FRA_1740190120222027.pdf | BhopalP | 1740190120222020 | Extra Care | Extra Care South | EC South 3 | South | South Patch 6 | ag87oegsffwkylzy943 | Low Risk closed | Risk Closed | 44610.6008 | Obs4 | The Occupant - Information Provided By The Court Manager | 45310 | Low | Court Manager | Flat 13 - Fire retardant bedding has been provided by the Fire Services. Flat 40 resident is bed bound. | Flat 13 is one deceased flat now empty. Flat 40 has a FAR assessment in place in the office.
1740 | Lime Tree House | LIMETREEHSE_S001 | H21 | Scheme | 2022-01-19 21:21 | FRA_1740190120222027.pdf | BhopalP | 1740190120222020 | Extra Care | Extra Care South | EC South 3 | South | South Patch 6 | fusrzyh014vkylzy94l | Observation Only | Risk Closed | 44585.4564 | Obs14 | Access By Emergency Services | NULL | N/A | Court Manager | Assembly point is outside in the car park. | Have printed the updated risk assessment and put in the red fire folder.
1801 | Ian Fraser Court | IANFRAS_S001 | H21 | Scheme | 2022-03-29 10:24 | FRA_1801290320220847.pdf | mitchellj1 | 1801290320220840 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 9 | gckp4aj1wzl1bu6g5v | Observation Only | Risk Closed | 44676.5717 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Christmas decorations (trees with mains powered lights) in ground floor store cupboard, please only allow battery powered decorations to be operated when CM is on site. | Put in different cupboard
1801 | Ian Fraser Court | IANFRAS_S001 | H21 | Scheme | 2022-03-29 10:24 | FRA_1801290320220847.pdf | mitchellj1 | 1801290320220840 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 9 | m2mluy4461l1bu6gbp | Observation Only | Risk Closed | 44676.572 | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | Court fire plan and policy documents to be updated in file. | All updated
1801 | Ian Fraser Court | IANFRAS_S001 | H21 | Scheme | 2022-03-29 10:24 | FRA_1801290320220847.pdf | mitchellj1 | 1801290320220840 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 9 | ln78v70gptl1bu6ga2 | Low Risk closed | Risk Closed | 44720.5703 | Obs10 | Fire Safety And Notices | 45380 | Low | Court Manager | No clear emergency exit signage between flats 2-10, both gates are locked, signage should be introduced to assembly point. | 2 sign fitted now
1801 | Ian Fraser Court | IANFRAS_S001 | H21 | Scheme | 2022-03-29 10:24 | FRA_1801290320220847.pdf | mitchellj1 | 1801290320220840 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 9 | tgr4d4dxybl1bu6g3z | Observation Only | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Surveyor | Understairwell door where bins are stored (near flat 2 and 10) door is not a fire door but detection is in place inside and outside the area. | NULL
1801 | Ian Fraser Court | IANFRAS_S001 | H21 | Scheme | 2022-03-29 10:24 | FRA_1801290320220847.pdf | mitchellj1 | 1801290320220840 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 9 | se7yxb69jwnl1bu6g8i | Low Risk closed | Risk Closed | 44720.5701 | Obs8 | Measures To Limit Fire Spread And Development | 45380 | Low | Court Manager | Flat 19 door : Missing intumescent and smoke seal to hinge side of door, arrange for this to be installed. | All fitted now
1801 | Ian Fraser Court | IANFRAS_S001 | H21 | Scheme | 2022-03-29 10:24 | FRA_1801290320220847.pdf | mitchellj1 | 1801290320220840 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 9 | ppifyczyn3gl1bu6g4m | Low Risk closed | Risk Closed | 44701.4858 | Obs6 | Fire Hazards - Elimination & Control | 45380 | Low | Court Manager | Trip hazard on emergency escape route outside flats 2-10 3nr manhole covers. | All levelled off -now safe
1801 | Ian Fraser Court | IANFRAS_S001 | H21 | Scheme | 2022-03-29 10:24 | FRA_1801290320220847.pdf | mitchellj1 | 1801290320220840 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 9 | cirobxq2m97l1bu6g6t | Medium Risk closed | Risk Closed | 44649.5754 | Obs6 | Fire Hazards - Elimination & Control | 45014 | Medium | Court Manager | Book shelf with a lot of books in corridor, can this be reduced and relocated? | No the redidents use this library daily
1801 | Ian Fraser Court | IANFRAS_S001 | H21 | Scheme | 2022-03-29 10:24 | FRA_1801290320220847.pdf | mitchellj1 | 1801290320220840 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 9 | 67oepuqmiusl1bu6gax | Observation Only | Risk Closed | 44676.5628 | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | Staff have rebooked their fire safety refresher training and will be recording this in the folder once complete. | Fire safety training completed 25.4.2022
1801 | Ian Fraser Court | IANFRAS_S001 | H21 | Scheme | 2022-03-29 10:24 | FRA_1801290320220847.pdf | mitchellj1 | 1801290320220840 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 9 | 6bthvhmdeqil1bu6g20 | Observation Only | Risk Closed | 44904.4456 | Obs1 | The Building | NULL | N/A | Surveyor | Photo of balconies | N.a. note only.
1801 | Ian Fraser Court | IANFRAS_S001 | H21 | Scheme | 2022-03-29 10:24 | FRA_1801290320220847.pdf | mitchellj1 | 1801290320220840 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 9 | 3vy1jx8dipjl1bu6g9f | Observation Only | Risk Closed | 44904.4455 | Obs10 | Fire Safety And Notices | NULL | N/A | Surveyor | Check if fire action notices are in accordance with the h21 policy. | N.A. note only
1803 | Lord Kitchener Court | LORDKITC_S001 | H21 | Scheme | 2022-03-02 07:32 | FRA_1803010320221316.pdf | mitchellj1 | 1803010320221310 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | 4g53nxftlwwl085lxbf | Low Risk closed | Risk Closed | 44624.5789 | Obs11 | Fire Fighting Equipment | 45352 | Low | Court Manager | Arrange for old extinguisher in ground floor meter cupboard near flat 22 to be removed. | Disposed of extinguisher.
1803 | Lord Kitchener Court | LORDKITC_S001 | H21 | Scheme | 2022-03-02 07:32 | FRA_1803010320221316.pdf | mitchellj1 | 1803010320221310 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | ot6z21edbdl098os07 | Observation Only | Risk Closed | 44904.4526 | Obs13 | Other Relevant Fixed Systems | NULL | N/A | Surveyor | Fire fighting lift not in use. | N.a. note only.
1803 | Lord Kitchener Court | LORDKITC_S001 | H21 | Scheme | 2022-03-02 07:32 | FRA_1803010320221316.pdf | mitchellj1 | 1803010320221310 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | o1rze2bxd2l085lxae | Medium Risk closed | Risk Closed | 44622.3701 | Obs8 | Measures To Limit Fire Spread And Development | 44986 | Medium | Court Manager | Flat 11: Intumescent strip needs refixing as it's coming away from the door | Intumescent strip refined to door by contractor on 1st March 2022.
1804 | Corcoran Close | CORCORAN_S001 | H21 | Scheme | 2022-02-10 18:21 | FRA_1804100220221818.pdf | mitchellj1 | 1804100220221810 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 9 | ukf9jtuyx59kzhb0m0l | Observation Only | Risk Closed | 44904.4425 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Panel photo | N.A. - note only.
1804 | Corcoran Close | CORCORAN_S001 | H21 | Scheme | 2022-02-10 18:21 | FRA_1804100220221818.pdf | mitchellj1 | 1804100220221810 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 9 | muve7lpnudokzhb0m8f | Low Risk closed | Risk Closed | 44634.5873 | Obs10 | Fire Safety And Notices | 45332 | Low | Court Manager | Fire assembly point sign should be installed at assembly point. | Signage installed.
1804 | Corcoran Close | CORCORAN_S001 | H21 | Scheme | 2022-02-10 18:21 | FRA_1804100220221818.pdf | mitchellj1 | 1804100220221810 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 9 | fugrvg7zjztkzhb0m2s | Low Risk closed | Risk Closed | 44642.6502 | Obs6 | Fire Hazards - Elimination & Control | 45332 | Low | Court Manager | Fire stopping required above communal corridor doors on ground floor adjacent flat 3. | ABS completed fire stopping
1804 | Corcoran Close | CORCORAN_S001 | H21 | Scheme | 2022-02-10 18:21 | FRA_1804100220221818.pdf | mitchellj1 | 1804100220221810 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 9 | gt0h2iqf0t5kzhb0m7n | Low Risk closed | Risk Closed | 44615.6193 | Obs10 | Fire Safety And Notices | 45332 | Low | Court Manager | Please fill in assembly point location on fire action notices. | Information is filled in.
1804 | Corcoran Close | CORCORAN_S001 | H21 | Scheme | 2022-02-10 18:21 | FRA_1804100220221818.pdf | mitchellj1 | 1804100220221810 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 9 | 4g01ttf01oukzhb0m3u | Low Risk closed | Risk Closed | 44642.6499 | Obs6 | Fire Hazards - Elimination & Control | 45332 | Low | Court Manager | Please remove combustible items being stored in electric meter cupboard under stairs near flat 9. | Items removed
1804 | Corcoran Close | CORCORAN_S001 | H21 | Scheme | 2022-02-10 18:21 | FRA_1804100220221818.pdf | mitchellj1 | 1804100220221810 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 9 | 5ww07l1ac74kzhb0m62 | Low Risk closed | Risk Closed | 44634.5859 | Obs8 | Measures To Limit Fire Spread And Development | 45332 | Low | Court Manager | No closer on flat 3's entrance door. | Door closer was fitted.
1804 | Corcoran Close | CORCORAN_S001 | H21 | Scheme | 2022-02-10 18:21 | FRA_1804100220221818.pdf | mitchellj1 | 1804100220221810 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 9 | cz9rbl6fzzekzhb0m4b | Low Risk closed | Risk Closed | 44634.5881 | Obs6 | Fire Hazards - Elimination & Control | 45332 | Low | Court Manager | Rubbish has been dumped outside building, please arrange for this to be removed if it hasn't alresdy been arranged. | Rubbish removed
1804 | Corcoran Close | CORCORAN_S001 | H21 | Scheme | 2022-02-10 18:21 | FRA_1804100220221818.pdf | mitchellj1 | 1804100220221810 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 9 | ewmxfjo2ytkzhb0m3b | Low Risk closed | Risk Closed | 44642.6508 | Obs6 | Fire Hazards - Elimination & Control | 45332 | Low | Court Manager | Fire stopping required to heating pipes in ground floor store cupboard. | ABS completed fire stopping.
1804 | Corcoran Close | CORCORAN_S001 | H21 | Scheme | 2022-02-10 18:21 | FRA_1804100220221818.pdf | mitchellj1 | 1804100220221810 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 9 | au6rst79wr9kzhb0m6y | Low Risk closed | Risk Closed | 44657.5145 | Obs10 | Fire Safety And Notices | 45332 | Low | Court Manager | No fire exit signage in corridor serving Lounge and guest room, please arrange for this to be installed. | New signs installed.
1804 | Corcoran Close | CORCORAN_S001 | H21 | Scheme | 2022-02-10 18:21 | FRA_1804100220221818.pdf | mitchellj1 | 1804100220221810 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 9 | vuinofli8ilkzhb0m56 | Observation Only | Risk Closed | 44904.4536 | Obs7 | Fire Protection Measures | NULL | N/A | Surveyor | Secondary exit to front elevation leads to gated bin store area. | N.a. note only.
1804 | Corcoran Close | CORCORAN_S001 | H21 | Scheme | 2022-02-10 18:21 | FRA_1804100220221818.pdf | mitchellj1 | 1804100220221810 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 9 | ylocngspv3kzhb0m1c | Low Risk closed | Risk Closed | 44615.6185 | Obs2 | Means Of Giving Warning In Case Of Fire | 45332 | Low | Court Manager | Arrange for old fire panel sign to be removed from cupboard in corridor. | Sign has been removed.
1804 | Corcoran Close | CORCORAN_S001 | H21 | Scheme | 2022-02-10 18:21 | FRA_1804100220221818.pdf | mitchellj1 | 1804100220221810 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 9 | wtvgjgufqrjkzhb0m1y | Low Risk closed | Risk Closed | 44615.6096 | Obs2 | Means Of Giving Warning In Case Of Fire | 45332 | Low | Court Manager | Arrange for items in ground floor electric meter cupboard to be removed so area is sterile. | Removed items so sterile as requested.
1805 | Ben Davies Court | BENDAVI_S001 | H21 | Scheme | 2022-03-11 17:50 | FRA_1805110320221110.pdf | mitchellj1 | 1805110320221110 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 9 | wkp7j78wlhpl0mdp5sl | Low Risk closed | Risk Closed | 44657.4795 | Obs6 | Fire Hazards - Elimination & Control | 45362 | Low | Court Manager | Please arrange for fire blanket in guest kitchen to be serviced. | Check completed by court manager on a monthly basis when completing monthly report
1805 | Ben Davies Court | BENDAVI_S001 | H21 | Scheme | 2022-03-11 17:50 | FRA_1805110320221110.pdf | mitchellj1 | 1805110320221110 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 9 | uvpnldiz5ul0mc26xr | Medium Risk closed | Risk Closed | 44655.6264 | Obs8 | Measures To Limit Fire Spread And Development | 44996 | Medium | Court Manager | Flat 148: closer needs re-fixing to door | Work order raised to renew door closer. Work order ref: 1529854
1805 | Ben Davies Court | BENDAVI_S001 | H21 | Scheme | 2022-03-11 17:50 | FRA_1805110320221110.pdf | mitchellj1 | 1805110320221110 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 9 | cc56inwcqp5l0mbmo84 | Observation Only | Risk Closed | 44655.4261 | Obs10 | Fire Safety And Notices | NULL | N/A | Court Manager | Please arrange for new fire action notices to be installed, available in H21 policy document. | Copy of updated fire action plan in Fire Safety Management folder. Notices located in communal building
1805 | Ben Davies Court | BENDAVI_S001 | H21 | Scheme | 2022-03-11 17:50 | FRA_1805110320221110.pdf | mitchellj1 | 1805110320221110 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 9 | rwwf20thz6l0mcoqm8 | Medium Risk closed | Risk Closed | 44655.6346 | Obs8 | Measures To Limit Fire Spread And Development | 44996 | Medium | Court Manager | Flat 200: door closer requires repairing. | Work order raised to fix door closer, work order ref 1529862
1806 | Chesworth Court | CHESWORTH_S001 | H21 | Scheme | 2022-03-11 06:53 | FRA_1806110320220620.pdf | mitchellj1 | 1806110320220620 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 9 | rlm9ikjsbbpl0m19sa9 | Low Risk closed | Risk Closed | 44634.5134 | Obs5 | Evacuation Strategy And Training | 45362 | Low | Court Manager | Resident of flat 7 has been provided an adapted chair which he is secured into, the chair may impede the residents ability to escape in an emergency, this has been captured in the PCFRA and the information is in the fire box however it is advised that the fire service attend to undertake an FRA of the flat and resident. | Submitted HRS A form on fire service webpage link requesting a home visit
1806 | Chesworth Court | CHESWORTH_S001 | H21 | Scheme | 2022-03-11 06:53 | FRA_1806110320220620.pdf | mitchellj1 | 1806110320220620 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 9 | e32thiw2hctl0m15wmm | Low Risk closed | Risk Closed | 44634.5121 | Obs10 | Fire Safety And Notices | 45362 | Low | Court Manager | Please write assembly point on fire action notices signs. | Wrote on all court signs
1806 | Chesworth Court | CHESWORTH_S001 | H21 | Scheme | 2022-03-11 06:53 | FRA_1806110320220620.pdf | mitchellj1 | 1806110320220620 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 9 | 7jhoft98jynl0m15wp7 | Observation Only | Risk Closed | 44634.402 | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | Test records are being recorded on 1st touch so no written records recorded in file, please can monthly test records be printed out and stored in the file for access. | Printed last 3 months, will now print monthly
1806 | Chesworth Court | CHESWORTH_S001 | H21 | Scheme | 2022-03-11 06:53 | FRA_1806110320220620.pdf | mitchellj1 | 1806110320220620 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 9 | zacm39hl7onl0m15woi | Low Risk closed | Risk Closed | 44658.5753 | Obs14 | Access By Emergency Services | 45362 | Low | Court Manager | Please arrange for a fire assembly point to be installed in the car park. | New signage put up by the handyman
1807 | Brown Court (Wigan) | BROWNWIGA_S001 | H21 | Scheme | 2022-11-02 14:46 | FRA_1807021120221445.pdf | mitchellj1 | 1807021120221440 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | 1owm08swgg4l9zr3th4 | Medium Risk closed | Risk Closed | 44903.6485 | Obs15 | Management Of Fire Safety | 45232 | Medium | Court Manager | Fire stopping required to electric cables existing electric cupboard. | Raised for repair work order now action completed
1807 | Brown Court (Wigan) | BROWNWIGA_S001 | H21 | Scheme | 2022-11-02 14:46 | FRA_1807021120221445.pdf | mitchellj1 | 1807021120221440 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | 13ttau5sceejl9zr3tdk | Low Risk closed | Risk Closed | 44880.6474 | Obs6 | Fire Hazards - Elimination & Control | 45598 | Low | Court Manager | Please ensure mobility scooters in EV store are PAT tested. | Pat tested on all 4 scooters on 13,11,22
1807 | Brown Court (Wigan) | BROWNWIGA_S001 | H21 | Scheme | 2022-11-02 14:46 | FRA_1807021120221445.pdf | mitchellj1 | 1807021120221440 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | 0sq5k40x1tpl9zr3tc4 | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | Court Manager is in the process of completing the new PCFRA form for all residents. | NULL
1807 | Brown Court (Wigan) | BROWNWIGA_S001 | H21 | Scheme | 2022-11-02 14:46 | FRA_1807021120221445.pdf | mitchellj1 | 1807021120221440 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | crwonyi1o2l9zr3tg7 | Low Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45598 | Low | Court Manager | New fire risk management documents to be inserted into fire safety file. | NULL
1807 | Brown Court (Wigan) | BROWNWIGA_S001 | H21 | Scheme | 2022-11-02 14:46 | FRA_1807021120221445.pdf | mitchellj1 | 1807021120221440 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | sgr2s9nkcbl9zr3tev | Medium Risk closed | Risk Closed | 44903.6478 | Obs8 | Measures To Limit Fire Spread And Development | 45232 | Medium | Court Manager | Please review which doors aren't closing in page 11 and arrange for this to be addressed. | raised work order to fix doors all now been fixed action completed
1807 | Brown Court (Wigan) | BROWNWIGA_S001 | H21 | Scheme | 2022-11-02 14:46 | FRA_1807021120221445.pdf | mitchellj1 | 1807021120221440 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | loqojljpg4gl9zr3ti2 | Medium Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45232 | Medium | Court Manager | Storage cupboards between two fire exit doors near flat 70 have non fire door doors on which may pass smoke. Surveyor to seek advice. | NULL
1808 | Corbett Court | CORBETT_S001 | H21 | Scheme | 2022-06-17 11:33 | FRA_1808170620221047.pdf | ClarkG | 1808170620221040 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | wdhh9j4hr8l4iaszai | Low Risk closed | Risk Closed | 44797.4328 | Obs6 | Fire Hazards - Elimination & Control | 45460 | Low | Court Manager | Door Guards required to Managers Office. | New door guard fitted Order number 1549071
1809 | Swinton Court | SWINTON_S001 | H21 | Scheme | 2022-11-10 08:54 | FRA_1809101120220849.pdf | mitchellj1 | 1809101120220840 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | z6yee7tuvk8laatwwtv | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45606 | Low | Court Manager | Please arrange for fire assembly point sign to be installed in car park. | NULL
1809 | Swinton Court | SWINTON_S001 | H21 | Scheme | 2022-11-10 08:54 | FRA_1809101120220849.pdf | mitchellj1 | 1809101120220840 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | rlnhz75j5nlaatwwrf | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45240 | Medium | Court Manager | Please arrange for an intumescent strip to be installed to the communal corridor doors between guest flat and flat 1. | NULL
1809 | Swinton Court | SWINTON_S001 | H21 | Scheme | 2022-11-10 08:54 | FRA_1809101120220849.pdf | mitchellj1 | 1809101120220840 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | 57o2pjzhxglaatwws6 | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45240 | Medium | Court Manager | Flat 4 - door not closing due to carpet, please arrange fornthis to be addressed. | NULL
1809 | Swinton Court | SWINTON_S001 | H21 | Scheme | 2022-11-10 08:54 | FRA_1809101120220849.pdf | mitchellj1 | 1809101120220840 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | 4fmkj4knzfylaatwwps | Medium Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45240 | Medium | Court Manager | On upcoming visit from fire service, please ask the fire officer to review your high risk resident's PCFRA's and discuss emergency evacuation plans necessary. | NULL
1809 | Swinton Court | SWINTON_S001 | H21 | Scheme | 2022-11-10 08:54 | FRA_1809101120220849.pdf | mitchellj1 | 1809101120220840 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | 4z88p6v33u4laatwwqg | Low Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45606 | Low | Court Manager | Please arrange for gate and outside light to be fixed to outside egress route near flat 5. | NULL
1810 | Elkin Court | ELKIN_S001 | H21 | Scheme | 2022-03-17 16:49 | FRA_1810170320221153.pdf | mitchellj1 | 1810170320221150 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 9 | 4pkmc4dakal0uxoj9t | Observation Only | Risk Closed | 44904.4516 | Obs10 | Fire Safety And Notices | NULL | N/A | Surveyor | Check fire action notices are as per h21 policy. | N.a. note only, has been actioned with CM.
1810 | Elkin Court | ELKIN_S001 | H21 | Scheme | 2022-03-17 16:49 | FRA_1810170320221153.pdf | mitchellj1 | 1810170320221150 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 9 | 7ounnh4vuall0uxojd9 | Observation Only | Risk Open | NULL | Obs12 | Automatic Fire Systems i.e. Suppression System | NULL | N/A | Surveyor | Check the automatic fire suppression system is serviced as part of a maintenance contract. | NULL
1810 | Elkin Court | ELKIN_S001 | H21 | Scheme | 2022-03-17 16:49 | FRA_1810170320221153.pdf | mitchellj1 | 1810170320221150 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 9 | 0nunkefwzwydl0uxojen | Observation Only | Risk Closed | 44699.6069 | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | Court Manager had booked fire safety manager refresher training. | Booked for the 26th may for part two part one completed
1810 | Elkin Court | ELKIN_S001 | H21 | Scheme | 2022-03-17 16:49 | FRA_1810170320221153.pdf | mitchellj1 | 1810170320221150 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 9 | 3a0181suz5nl0uxojfb | Observation Only | Risk Closed | 44638.4068 | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | Weekly & monthly tests are being recorded on Pebbles, fire alarm tests are being recorded on Pebbles and in file. | Have put sheets in fire file and noted for this month
1810 | Elkin Court | ELKIN_S001 | H21 | Scheme | 2022-03-17 16:49 | FRA_1810170320221153.pdf | mitchellj1 | 1810170320221150 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 9 | rcb5ihgugenl0uxojbl | Low Risk closed | Risk Closed | 44691.6112 | Obs10 | Fire Safety And Notices | 45368 | Low | Court Manager | Introduce fire action notices above all MCPs | All notices placed above extinguishers and in communal areas and all delivered to residents
1810 | Elkin Court | ELKIN_S001 | H21 | Scheme | 2022-03-17 16:49 | FRA_1810170320221153.pdf | mitchellj1 | 1810170320221150 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 9 | sc0cv9kj7jel0uxoj7b | Low Risk closed | Risk Closed | 44665.5512 | Obs8 | Measures To Limit Fire Spread And Development | 45368 | Low | Court Manager | Flat 40: carpet is obstructing door closing, please arrange for this to be addressed by a contractor. | Monaghan's have completed this work
1810 | Elkin Court | ELKIN_S001 | H21 | Scheme | 2022-03-17 16:49 | FRA_1810170320221153.pdf | mitchellj1 | 1810170320221150 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 9 | nvyhaum1dpsl0uxojgz | Observation Only | Risk Closed | 44904.4477 | Obs16 | Testing And Maintenance | NULL | N/A | Surveyor | Fire extinguishers have been removed from stairs, confirm this was actioned with compliance. | N.A note only
1810 | Elkin Court | ELKIN_S001 | H21 | Scheme | 2022-03-17 16:49 | FRA_1810170320221153.pdf | mitchellj1 | 1810170320221150 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 9 | o18xi7sg1al0uxojaq | Observation Only | Risk Closed | 44904.4512 | Obs10 | Fire Safety And Notices | NULL | N/A | Surveyor | Fire action notice contradicts a stay put policy. | CM was advised and notices changed.
1810 | Elkin Court | ELKIN_S001 | H21 | Scheme | 2022-03-17 16:49 | FRA_1810170320221153.pdf | mitchellj1 | 1810170320221150 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 9 | p3zgyx6g8ujl0v83k1j | Observation Only | Risk Closed | 44638.4083 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | There are 3nr oxygen users in the Court, this information is accessible in the fire box. | This information is on the resident fire list in the fire box
1810 | Elkin Court | ELKIN_S001 | H21 | Scheme | 2022-03-17 16:49 | FRA_1810170320221153.pdf | mitchellj1 | 1810170320221150 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 9 | gx7f670zw8sl0uxoj84 | Observation Only | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Surveyor | Check if the free swing closer devices are serviced. | NULL
1810 | Elkin Court | ELKIN_S001 | H21 | Scheme | 2022-03-17 16:49 | FRA_1810170320221153.pdf | mitchellj1 | 1810170320221150 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 9 | imqpzqwz5rql0uxumkl | Low Risk closed | Risk Closed | 44638.4079 | Obs6 | Fire Hazards - Elimination & Control | 45368 | Low | Court Manager | Please arrange for combustible Items stored near electrical equipment in cleaners cupboard near flat 33 to be stored away from electrical equipment. | I have moved away from the electrics and have arranged for items to be removed
1810 | Elkin Court | ELKIN_S001 | H21 | Scheme | 2022-03-17 16:49 | FRA_1810170320221153.pdf | mitchellj1 | 1810170320221150 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 9 | ytl5dx6odrkl0uxojg8 | Observation Only | Risk Closed | 44904.4479 | Obs16 | Testing And Maintenance | NULL | N/A | Surveyor | Smoke vent tested 06/2021 | N.a. photo only.
1812 | Crandon Court | CRANDON_S001 | H21 | Scheme | 2022-07-06 17:17 | FRA_1812060720221054.pdf | mitchellj1 | 1812060720221050 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | m4s9fkujrzgl59fay64 | Medium Risk closed | Risk Closed | 44755.5581 | Obs8 | Measures To Limit Fire Spread And Development | 45113 | Medium | Court Manager | Flat 29: no closer in place, please arrange for one to be installed. | Work completed by GCH 12/7/22
1812 | Crandon Court | CRANDON_S001 | H21 | Scheme | 2022-07-06 17:17 | FRA_1812060720221054.pdf | mitchellj1 | 1812060720221050 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | ravbzt2uhol59fay54 | Low Risk closed | Risk Closed | 44755.557 | Obs8 | Measures To Limit Fire Spread And Development | 45479 | Low | Court Manager | Flat 12: The intumescent/brush strip is missing from the hinge side face of door, please arrange for one to be installed. | Work completed by GCH 12/7/22
1812 | Crandon Court | CRANDON_S001 | H21 | Scheme | 2022-07-06 17:17 | FRA_1812060720221054.pdf | mitchellj1 | 1812060720221050 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | r146tpwmv5gl59fay9q | Observation Only | Risk Closed | 44904.444 | Obs14 | Access By Emergency Services | NULL | N/A | Surveyor | There is limited access for FRS due to the layout and accessible areas around the court. | N.a. note only
1812 | Crandon Court | CRANDON_S001 | H21 | Scheme | 2022-07-06 17:17 | FRA_1812060720221054.pdf | mitchellj1 | 1812060720221050 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | 7vu4932mp0fl59fay76 | Medium Risk closed | Risk Closed | 44755.5578 | Obs8 | Measures To Limit Fire Spread And Development | 45113 | Medium | Court Manager | Flat 28:Brush/intumescent seal and missing from RHS of door. Please arrange for one to be installed. | Work completed by GCH 12/7/22
1812 | Crandon Court | CRANDON_S001 | H21 | Scheme | 2022-07-06 17:17 | FRA_1812060720221054.pdf | mitchellj1 | 1812060720221050 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | 6ymbeqeqotkl59fay25 | Observation Only | Risk Closed | 44904.4438 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Zone layout photo. | N.a. note only
1812 | Crandon Court | CRANDON_S001 | H21 | Scheme | 2022-07-06 17:17 | FRA_1812060720221054.pdf | mitchellj1 | 1812060720221050 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | cldbbp4x3qfl59fay12 | Low Risk closed | Risk Closed | 44755.5574 | Obs1 | The Building | 45479 | Low | Court Manager | Making good/fire stopping required around service cables to ceiling in corridor outside guest flat | Work completed by GCH 12/7/22
1813 | Harry Whitehead Court | HARRYWHIT_R001 | H21 | Unknown | 2020-05-26 11:55 | FRA_181326052020.pdf | JohnsonD | 181326052020 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 9 | 42qp2edoid5kanslti1 | Medium Risk closed | Risk Closed | 44006.5175 | Obs5 | Evacuation Strategy And Training | 44342 | Medium | Court Manager | Red box key to be relocated from the key safe to a break glass key safe adjacent to the red fire box. | Fitted break glass for key on 24.06.2020
1813 | Harry Whitehead Court | HARRYWHIT_S001 | H21 | Scheme | 2022-05-24 17:39 | FRA_1813240520221109.pdf | mitchellj1 | 1813240520221100 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 9 | 5zql4z73qnjl3kdnoci | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45070 | Medium | Surveyor | Some gaps to flat entrance doors would benefit from additional smoke seals, doors to be identified and seals to be installed. | NULL
1813 | Harry Whitehead Court | HARRYWHIT_S001 | H21 | Scheme | 2022-05-24 17:39 | FRA_1813240520221109.pdf | mitchellj1 | 1813240520221100 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 9 | 0v07tewrtlvdl3kdkp24 | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45088 | Low | Court Manager | Fire assembly point signage to be fitted, location TBA with Surveyor. | NULL
1813 | Harry Whitehead Court | HARRYWHIT_R001 | H21 | Unknown | 2020-05-26 11:55 | FRA_181326052020.pdf | JohnsonD | 181326052020 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 9 | jf07wmbrvnkansglro | Medium Risk closed | Risk Closed | 44022.5362 | Obs5 | Evacuation Strategy And Training | 44342 | Medium | Court Manager | CM to attend fire training course. | Did course on 05062020
1814 | Carlton Crescent | CARLTONCRES_S001 | H21 | Scheme | 2022-09-29 14:23 | FRA_1814290920221422.pdf | JohnsonD | 1814290920221420 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 7 | l0vub8eedfl8n36cf4 | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Other | 2x vulnerable residents have been identified in PCFRA. Noted in information for frs. | NULL
1814 | Carlton Crescent | CARLTONCRES_S001 | H21 | Scheme | 2022-09-29 14:23 | FRA_1814290920221422.pdf | JohnsonD | 1814290920221420 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 7 | esawhwyozq8l8n36cg3 | Low Risk closed | Risk Closed | 44848.5436 | Obs6 | Fire Hazards - Elimination & Control | 45564 | Low | Court Manager | Letter to residents who place clothing on storage heaters. Warning not to do this and find alternative means for drying clothes. | Sent letters
1815 | Avril Court | AVRIL_S001 | H21 | Scheme | 2022-10-31 17:26 | FRA_1815311020221312.pdf | mitchellj1 | 1815311020221310 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | sjlxv0s5lml9x1w9kb | Medium Risk closed | Risk Closed | 44886.3385 | Obs8 | Measures To Limit Fire Spread And Development | 45230 | Medium | Court Manager | Please arrange for closers to be adjusted to ensure the following flat entrance doors close completely: 38, 39 & 18 | Raised works order for CBE to come out and adjust the door closers
1815 | Avril Court | AVRIL_S001 | H21 | Scheme | 2022-10-31 17:26 | FRA_1815311020221312.pdf | mitchellj1 | 1815311020221310 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | w587swarm7el9wvqscn | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45263 | Low | Court Manager | Warden call cables in lift motor room require fire stopping. | NULL
1817 | Langton Court | LANGTON_S001 | H21 | Scheme | 2022-01-25 13:23 | FRA_1817250120221156.pdf | ClarkG | 1817250120221150 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | ooxprxgjispkyu2bjm1 | Low Risk closed | Risk Closed | 44664.6553 | Obs10 | Fire Safety And Notices | 44952 | Low | Surveyor | Fire Safety signage and notices require updating. These signs will be replaced when the lighting is upgraded on planned works. | The signage has been updated
1817 | Langton Court | LANGTON_S001 | H21 | Scheme | 2022-01-25 13:23 | FRA_1817250120221156.pdf | ClarkG | 1817250120221150 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | lr5y3dtb7mmkyu2bjkd | Low Risk closed | Risk Closed | 44664.6548 | Obs9 | Escape Lighting | 44952 | Low | Surveyor | Communal lighting has a number of emergency lights failing. The lighting is due for replacement on planned works. | Lighting has been updated
1818 | Legh Court | LEGH_S001 | H21 | Scheme | 2022-05-27 14:48 | FRA_1818270520221420.pdf | ClarkG | 1818270520221420 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | jtnpjwyohool3oh1ypa | Low Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45439 | Low | Court Manager | Cleaners FRED fire warning training needs refreshing. | NULL
1818 | Legh Court | LEGH_S001 | H21 | Scheme | 2022-05-27 14:48 | FRA_1818270520221420.pdf | ClarkG | 1818270520221420 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | p97wkklyl97l3oh1yn5 | Low Risk to be actioned | Risk Open | NULL | Obs1 | The Building | 45439 | Low | Court Manager | Service cover needs reinstalling in Cleaners cupboard. | NULL
1818 | Legh Court | LEGH_S001 | H21 | Scheme | 2022-05-27 14:48 | FRA_1818270520221420.pdf | ClarkG | 1818270520221420 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | s8fn8p0zascl3oh1yoh | Observation Only | Risk Closed | 44711.6064 | Obs5 | Evacuation Strategy And Training | NULL | N/A | Court Manager | New cleaner having training on the fire warden training. | COMPLETED FIRE TRAINING 30.05.22
1818 | Legh Court | LEGH_S001 | H21 | Scheme | 2022-05-27 14:48 | FRA_1818270520221420.pdf | ClarkG | 1818270520221420 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | 8ri71sox4n6l3oh1yno | Low Risk to be actioned | Risk Open | NULL | Obs1 | The Building | 45439 | Low | Court Manager | Fire stopping required above communal corridor door adjacent to Flat 5 | NULL
1818 | Legh Court | LEGH_S001 | H21 | Scheme | 2022-05-27 14:48 | FRA_1818270520221420.pdf | ClarkG | 1818270520221420 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | 32n8lvz3tl3ohee8m | Low Risk to be actioned | Risk Open | NULL | Obs1 | The Building | 45439 | Low | Court Manager | Fire stopping required above communal door to central lift lobby on first floor. | NULL
1818 | Legh Court | LEGH_S001 | H21 | Scheme | 2022-05-27 14:48 | FRA_1818270520221420.pdf | ClarkG | 1818270520221420 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | 6p1aoad2mlel3oh2anu | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45439 | Low | Surveyor | Fire Extinguisher bracket loose and needs re-fixing adjacent to Flat 19. | NULL
1818 | Legh Court | LEGH_S001 | H21 | Scheme | 2022-05-27 14:48 | FRA_1818270520221420.pdf | ClarkG | 1818270520221420 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | yphys02nelpl3oh1ymk | Low Risk to be actioned | Risk Open | NULL | Obs1 | The Building | 45439 | Low | Court Manager | Fire stopping required above communal corridor door adjacent to Flat 1. | NULL
1819 | Saddle Court | SADDLE_S001 | H21 | Scheme | 2022-06-07 14:09 | FRA_1819070620221212.pdf | ClarkG | 1819070620221210 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | wfcajnnclhgl445nhb2 | Low Risk closed | Risk Closed | 44760.42 | Obs7 | Fire Protection Measures | 45450 | Low | Court Manager | Fire stopping required above communal corridor doors adjacent to Flat 28 | raised WO to contractors to complete required works
1819 | Saddle Court | SADDLE_S001 | H21 | Scheme | 2022-06-07 14:09 | FRA_1819070620221212.pdf | ClarkG | 1819070620221210 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | 2y8mvjpkbpbl445abz3 | Low Risk closed | Risk Closed | 44760.474 | Obs7 | Fire Protection Measures | 45450 | Low | Court Manager | Communal corridor fire door adjacent to Flat 24 warped at bottom. Recommend the door is replaced with new fire door. | Raised WO to contractors to complete required works
1819 | Saddle Court | SADDLE_S001 | H21 | Scheme | 2022-06-07 14:09 | FRA_1819070620221212.pdf | ClarkG | 1819070620221210 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | rbfej6kywrgl445jlfv | Low Risk closed | Risk Closed | 44760.4184 | Obs7 | Fire Protection Measures | 45450 | Low | Court Manager | Fire stopping required above top floor central stairwell windows and doors. | raised WO to contractors to complete required works
1819 | Saddle Court | SADDLE_S001 | H21 | Scheme | 2022-06-07 14:09 | FRA_1819070620221212.pdf | ClarkG | 1819070620221210 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | nxd18x7ts0el442coea | Low Risk closed | Risk Closed | 44790.4702 | Obs2 | Means Of Giving Warning In Case Of Fire | 45086 | Low | Surveyor | Fire Zone plan needs updating with current zoning | Complete by Quartzelec
1819 | Saddle Court | SADDLE_S001 | H21 | Scheme | 2022-06-07 14:09 | FRA_1819070620221212.pdf | ClarkG | 1819070620221210 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | hg9tvyzubnl44531sa | Low Risk closed | Risk Closed | 44761.6491 | Obs7 | Fire Protection Measures | 45450 | Low | Court Manager | Fire stopping required above communal corridor doors adjacent to Flat 13. | raised WO with contractors to complete required works
1819 | Saddle Court | SADDLE_S001 | H21 | Scheme | 2022-06-07 14:09 | FRA_1819070620221212.pdf | ClarkG | 1819070620221210 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | i6wczrgbudl445pmc1 | Low Risk closed | Risk Closed | 44760.4197 | Obs7 | Fire Protection Measures | 45450 | Low | Court Manager | Fire stopping required in cleaners store on second floor. | raised WO with contractor to complete required works
1838 | Aston Court | ASTON_S001 | H21 | Scheme | 2022-11-02 20:10 | FRA_1838021120221522.pdf | mitchellj1 | 1838021120221520 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | krnnac7rw1l9zupq91 | Low Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45598 | Low | Court Manager | The laundry fire exit door, although unlocked at the time of assessment, has a key barrel, please consider changing this to a thumb turn operated door. | NULL
1838 | Aston Court | ASTON_S001 | H21 | Scheme | 2022-11-02 20:10 | FRA_1838021120221522.pdf | mitchellj1 | 1838021120221520 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | uoemn20whlfla00tixn | Medium Risk to be actioned | Risk Open | NULL | Obs1 | The Building | 45077 | Medium | Surveyor | Void detection to roof space above guest flat and to stairwell roof space near flat 37 has had head removed, fire alarm contractor to be contacted to advise and return if required. | NULL
1838 | Aston Court | ASTON_S001 | H21 | Scheme | 2022-11-02 20:10 | FRA_1838021120221522.pdf | mitchellj1 | 1838021120221520 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | 52dhjhpx7jkl9zutr0w | Observation Only | Risk Closed | 44904.443 | Obs5 | Evacuation Strategy And Training | NULL | N/A | Surveyor | Following the recent fire at flat 31, residents will be reminded of the evacuation strategy in the event of a fire. | N.A. - note only.
1838 | Aston Court | ASTON_S001 | H21 | Scheme | 2022-11-02 20:10 | FRA_1838021120221522.pdf | mitchellj1 | 1838021120221520 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | 9555zq7l0mdl9zucf4p | Observation Only | Risk Closed | 44904.4432 | Obs1 | The Building | NULL | N/A | Surveyor | Fire stopping to door head in communal corridor | N.a. note only
1838 | Aston Court | ASTON_S001 | H21 | Scheme | 2022-11-02 20:10 | FRA_1838021120221522.pdf | mitchellj1 | 1838021120221520 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | cx90v0tsblel9zulbon | Observation Only | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | PAT testing to portable appliances in communal areas completed in October 2022. | NULL
1838 | Aston Court | ASTON_S001 | H21 | Scheme | 2022-11-02 20:10 | FRA_1838021120221522.pdf | mitchellj1 | 1838021120221520 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | wmzb5oxbwgll9zvr9fy | Observation Only | Risk Closed | 44904.4437 | Obs10 | Fire Safety And Notices | NULL | N/A | Surveyor | Fire action notice. | N.a. - note only
1838 | Aston Court | ASTON_S001 | H21 | Scheme | 2022-11-02 20:10 | FRA_1838021120221522.pdf | mitchellj1 | 1838021120221520 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | vz98qizv7l9zuzrfj | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | Up to date resident information (including high, medium and low risk ratings) is in the fire box, the Court Manager is in the process of completing the new person centred FRA's on each resident. | NULL
1838 | Aston Court | ASTON_S001 | H21 | Scheme | 2022-11-02 20:10 | FRA_1838021120221522.pdf | mitchellj1 | 1838021120221520 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | urpx73fgycl9zvcq62 | Observation Only | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Currently 3nr flats empty at the moment: Flat 1: Old Court Managers house Flat 16: void Flat 31: now empty and recently suffered a fire, electrics have been isolated. At the time of assessment there were no plugged in appliances to flats 1 and 16. | NULL
1839 | Hurst Court | HURST_S001 | H21 | Scheme | 2022-03-03 07:28 | FRA_1839020320221030.pdf | mitchellj1 | 1839020320221030 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | zqerh9kmunhl09rp7zr | Low Risk closed | Risk Closed | 44642.6039 | Obs7 | Fire Protection Measures | 45353 | Low | Court Manager | Items stored in communal area opposite flat 18, these should removed so the area is sterile. | Asked resident to remove items from the corridor. This has been done and the corridor is now clear. Checked today 22.03.22.
1839 | Hurst Court | HURST_S001 | H21 | Scheme | 2022-03-03 07:28 | FRA_1839020320221030.pdf | mitchellj1 | 1839020320221030 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | dabelh27xv5l09iq6ko | Low Risk closed | Risk Closed | 44657.5111 | Obs6 | Fire Hazards - Elimination & Control | 45353 | Low | Court Manager | Items stored outside flat 30 on corridor, communal area should be sterile, can resident be advised to store items within the flat please. | Requested residents clear the area, checked yesterday and it is now clear.
1839 | Hurst Court | HURST_B001 | H21 | Unknown | 2020-03-31 14:59 | FRA_183931032020.pdf | JohnsonD | 183931032020 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | brbskfch2uok8fyhd8o | Medium Risk closed | Risk Closed | 43965.4245 | Obs8 | Measures To Limit Fire Spread And Development | 44286 | Medium | Court Manager | Ease and adjust fire door in block 31 to 34 | Raised works order for the door to be adjusted, completed
1839 | Hurst Court | HURST_S001 | H21 | Scheme | 2022-03-03 07:28 | FRA_1839020320221030.pdf | mitchellj1 | 1839020320221030 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | erk5isjh44hl09j4cqo | Low Risk closed | Risk Closed | 44686.6039 | Obs6 | Fire Hazards - Elimination & Control | 45353 | Low | Court Manager | Items on landing outside flat 33, spoke to resident and advised the items can't be stored in the communal area, he will speak to nurses to locate space to store them. | Landing is now clear
1839 | Hurst Court | HURST_B001 | H21 | Unknown | 2020-03-31 14:59 | FRA_183931032020.pdf | JohnsonD | 183931032020 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | betd7me0hark8fyfm2c | Low Risk closed | Risk Closed | 43965.4239 | Obs10 | Fire Safety And Notices | 44651 | Low | Court Manager | Running man sign required in lounge | Running man sign put on wall in communal lounge
1839 | Hurst Court | HURST_S001 | H21 | Scheme | 2022-03-03 07:28 | FRA_1839020320221030.pdf | mitchellj1 | 1839020320221030 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | a2h8oaioo4il09rklwp | Low Risk closed | Risk Closed | 44651.6091 | Obs8 | Measures To Limit Fire Spread And Development | 45353 | Low | Court Manager | Intumescent strip from top LHS of door not in place, this should be installed. | New piece of intumescent strip fitted today 31.03.22 to the front door of Flat 14 by All Building Services
1839 | Hurst Court | HURST_S001 | H21 | Scheme | 2022-03-03 07:28 | FRA_1839020320221030.pdf | mitchellj1 | 1839020320221030 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | 446m9y14sjsl09j0uoy | Low Risk closed | Risk Closed | 44651.6074 | Obs6 | Fire Hazards - Elimination & Control | 45353 | Low | Court Manager | Thumb turn to entrance door to block 25-30 broken, please arrange for a repair. | All Building Services have repaired today 31.03.22
1839 | Hurst Court | HURST_S001 | H21 | Scheme | 2022-03-03 07:28 | FRA_1839020320221030.pdf | mitchellj1 | 1839020320221030 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | qi68lul988hl09ryq24 | Observation Only | Risk Open | NULL | Obs7 | Fire Protection Measures | NULL | N/A | Surveyor | Bins stored outside escape route and under timber clad canopy. | NULL
1839 | Hurst Court | HURST_S001 | H21 | Scheme | 2022-03-03 07:28 | FRA_1839020320221030.pdf | mitchellj1 | 1839020320221030 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | qjvgio0h8al09rl88b | Low Risk closed | Risk Closed | 44651.608 | Obs8 | Measures To Limit Fire Spread And Development | 45353 | Low | Court Manager | Flat 28 and flat 29's doors don't close all the way from open, the closer should be adjusted. | All Building Services have adjusted today 31.03.22.
1839 | Hurst Court | HURST_S001 | H21 | Scheme | 2022-03-03 07:28 | FRA_1839020320221030.pdf | mitchellj1 | 1839020320221030 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | mxw2zptx2mql09fofr6 | Observation Only | Risk Closed | 44904.4522 | Obs3 | Details Of Fire Loss | NULL | N/A | Surveyor | Recent ignition caused by the wall mounted water boiler in the communal lounge was attended by the fire service, the fire didn't cause damage to the building and the unit has been taken out of use. | N.a. note only.
1839 | Hurst Court | HURST_B001 | H21 | Unknown | 2020-03-31 14:59 | FRA_183931032020.pdf | JohnsonD | 183931032020 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | n4sahfg1lkk8fyrcuj | Low Risk closed | Risk Closed | 43922.57 | Obs6 | Fire Hazards - Elimination & Control | 44651 | Low | Court Manager | Please arrange for the removal of stored items outside flat 29. | Tenant has been asked to remove items and has done so
1839 | Hurst Court | HURST_S001 | H21 | Scheme | 2022-03-03 07:28 | FRA_1839020320221030.pdf | mitchellj1 | 1839020320221030 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | fjeahx1oe2ul09g03ma | Observation Only | Risk Closed | 44904.4524 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Photo of panel | N.a. note only.
1840 | Sydney Jones Court | SYDNEYJONE_S001 | H21 | Scheme | 2022-05-21 08:23 | FRA_1840210520220821.pdf | mitchellj1 | 1840210520220820 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | q5puduq2qfl3fjl54k | Low Risk closed | Risk Closed | 44720.456 | Obs8 | Measures To Limit Fire Spread And Development | 45433 | Low | Court Manager | Flat 32 - please arrange for letter box to be repaired. | New letter box fitted
1840 | Sydney Jones Court | SYDNEYJONE_S001 | H21 | Scheme | 2022-05-21 08:23 | FRA_1840210520220821.pdf | mitchellj1 | 1840210520220820 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | 574m0750mp3l3fjl53e | Observation Only | Risk Closed | 44711.447 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Discussed with the resident of flat 42 her removing items out of the under stairs store as it was quite full. | Resident cleared items in storeroom to acceptable standard.
1840 | Sydney Jones Court | SYDNEYJONE_S001 | H21 | Scheme | 2022-05-21 08:23 | FRA_1840210520220821.pdf | mitchellj1 | 1840210520220820 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | 5dp316ltql8l3fjl5op | Observation Only | Risk Closed | 44764.495 | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | Cleaner to receive fire safety refresher training | Jackie completed fire safety awareness refresher course
1840 | Sydney Jones Court | SYDNEYJONE_S001 | H21 | Scheme | 2022-05-21 08:23 | FRA_1840210520220821.pdf | mitchellj1 | 1840210520220820 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | 6f91ljumo5jl3fjl55m | Low Risk closed | Risk Closed | 44720.4675 | Obs8 | Measures To Limit Fire Spread And Development | 45433 | Low | Court Manager | Flat 1 - door not closing fully, please arrange for closer to be adjusted. | Door closer adjusted
1840 | Sydney Jones Court | SYDNEYJONE_S001 | H21 | Scheme | 2022-05-21 08:23 | FRA_1840210520220821.pdf | mitchellj1 | 1840210520220820 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | 8ea4xtz9slvl3fjl5nu | Observation Only | Risk Closed | 44711.4491 | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | All tests are recorded on 1st touch and not in the fire safety folder, evidence of tests were shown on survey. | Evidence of all test carried out recorded on 1st touch
1840 | Sydney Jones Court | SYDNEYJONE_S001 | H21 | Scheme | 2022-05-21 08:23 | FRA_1840210520220821.pdf | mitchellj1 | 1840210520220820 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | btzs5qc7p1pl3fjl56y | Low Risk closed | Risk Closed | 44711.5054 | Obs10 | Fire Safety And Notices | 45433 | Low | Court Manager | Please can all fire action notice signs be filled in to confirm the assembly point location. | Completed
1840 | Sydney Jones Court | SYDNEYJONE_S001 | H21 | Scheme | 2022-05-21 08:23 | FRA_1840210520220821.pdf | mitchellj1 | 1840210520220820 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | ylblh1wsz9l3fjl52e | Medium Risk closed | Risk Closed | 44720.4619 | Obs6 | Fire Hazards - Elimination & Control | 45067 | Medium | Court Manager | Please confirm boilers have been serviced as service record on boilers indicates last service was 2020. | Boiler serviced October 2021 - see Y drive for certificates
1841 | Joseph Jennings Court | JOSEPHJENN_S001 | H21 | Scheme | 2022-03-17 06:31 | FRA_1841160320221424.pdf | mitchellj1 | 1841160320221420 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 9 | rluazss9sidl0tq83sl | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45367 | Low | Surveyor | Check fire action signage is as per policy. | NULL
1841 | Joseph Jennings Court | JOSEPHJENN_S001 | H21 | Scheme | 2022-03-17 06:31 | FRA_1841160320221424.pdf | mitchellj1 | 1841160320221420 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 9 | r6vv2zh538l0toe5jh | Low Risk closed | Risk Closed | 44657.4104 | Obs6 | Fire Hazards - Elimination & Control | 45367 | Low | Court Manager | PAT test label not visible on mobility scooter in store, please confirm this has been done. | This scooter is no longer in use and though it was plugged in there is no power going to the socket
1841 | Joseph Jennings Court | JOSEPHJENN_S001 | H21 | Scheme | 2022-03-17 06:31 | FRA_1841160320221424.pdf | mitchellj1 | 1841160320221420 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 9 | l6rf2wtedxl0tofcc2 | Medium Risk closed | Risk Closed | 44662.7058 | Obs6 | Fire Hazards - Elimination & Control | 45001 | Medium | Court Manager | Please arrange for smoke seal to be adjusted to bottom of corridor door near flat 11 as it's obstructing it closing. | Fitted 8th April 2022
1841 | Joseph Jennings Court | JOSEPHJENN_S001 | H21 | Scheme | 2022-03-17 06:31 | FRA_1841160320221424.pdf | mitchellj1 | 1841160320221420 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 9 | jq0d961sr7l0tp8flh | Low Risk closed | Risk Closed | 44662.7061 | Obs8 | Measures To Limit Fire Spread And Development | 45367 | Low | Court Manager | Flat 35: smoke seal missing from hinge side of door. | Adjusted 8th April 2022
1842 | Edward Onyon Court | EDWARDONYO_S001 | H21 | Scheme | 2022-06-10 07:57 | FRA_1842100620220756.pdf | mitchellj1 | 1842100620220750 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | r83zoiihq9l483hkt7 | Observation Only | Risk Closed | 44757.4413 | Obs9 | Escape Lighting | NULL | N/A | Court Manager | Emergency light fittings which failed Openview's test are (and were on day of visit) being replaced by Openview, with jobs raised with them. | New lighting system including emergency lights being fitted week commencing 25 th July 2022
1842 | Edward Onyon Court | EDWARDONYO_S001 | H21 | Scheme | 2022-06-10 07:57 | FRA_1842100620220756.pdf | mitchellj1 | 1842100620220750 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | q2aucpknhol483hkq8 | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45453 | Low | Court Manager | Fire barrier in riser between flats 7 and 5 is damaged, please arrange for this to be repaired/replaced by an accredited contractor. | NULL
1842 | Edward Onyon Court | EDWARDONYO_S001 | H21 | Scheme | 2022-06-10 07:57 | FRA_1842100620220756.pdf | mitchellj1 | 1842100620220750 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | 574ewc9kimwl483hkrl | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45453 | Low | Court Manager | Couldn't see PAT test labels on mobility scooters in store (charge leads missing), please ensure these have been PAT tested. | NULL
1842 | Edward Onyon Court | EDWARDONYO_S001 | H21 | Scheme | 2022-06-10 07:57 | FRA_1842100620220756.pdf | mitchellj1 | 1842100620220750 | Retirement Housing | Yorks Lancs | Greater Manchester | North | North Patch 9 | 1g73y9zmt0yl483hkuf | Observation Only | Risk Open | NULL | Obs14 | Access By Emergency Services | NULL | N/A | Other | Access to the rear of the building for FRS is restricted somewhat. | NULL
1902 | Wallis Court | WALLIS_S001 | H21 | Scheme | 2022-08-24 17:49 | FRA_1902240820221727.pdf | pickfordj | 1902240820221720 | Retirement Housing | Mid South | Berks and Hampshire North | South | South Patch 4 | ueh8ix9pr3ml77u9oyx | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45162 | Medium | Other | Bin store is a potential fire hazard as it is on an escape route with no fire wall break | NULL
1903 | Turvey King Court | TURVEYKING_S001 | H21 | Scheme | 2022-02-22 11:15 | FRA_1903220220220950.pdf | ComleyB | 1903220220220950 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | ltyuy4p3ilkzy05n7x | Low Risk closed | Risk Closed | 44656.4329 | Obs8 | Measures To Limit Fire Spread And Development | 45344 | Low | Court Manager | Flat 4 front door - penetration to be fire stopped and door to be eased and adjusted as not fully closing | Door fully closing and repaired.
1903 | Turvey King Court | TURVEYKING_S001 | H21 | Scheme | 2022-02-22 11:15 | FRA_1903220220220950.pdf | ComleyB | 1903220220220950 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | g76imf89jlkzy12hvg | Medium Risk closed | Risk Closed | 44630.5231 | Obs6 | Fire Hazards - Elimination & Control | 44979 | Medium | Court Manager | Remove blanking plate and patch repair wall to prevent heat and water damage from cooker. | Removed blanked plate and replaced with a whole tile covering the gap as there are life cables inside.
1903 | Turvey King Court | TURVEYKING_S001 | H21 | Scheme | 2022-02-22 11:15 | FRA_1903220220220950.pdf | ComleyB | 1903220220220950 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | em5mp3mkb7bkzy0a1vi | Low Risk closed | Risk Closed | 44630.5234 | Obs8 | Measures To Limit Fire Spread And Development | 45344 | Low | Court Manager | Flat 1 door to be eased and adjusted as not fully closing | Adjusted - now closing.
1903 | Turvey King Court | TURVEYKING_S001 | H21 | Scheme | 2022-02-22 11:15 | FRA_1903220220220950.pdf | ComleyB | 1903220220220950 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | xsbhdynymtkkzxzpv48 | Observation Only | Risk Open | NULL | Obs15 | Management Of Fire Safety | NULL | N/A | Other | False alarms recorded on ERICA | NULL
1903 | Turvey King Court | TURVEYKING_S001 | H21 | Scheme | 2022-02-22 11:15 | FRA_1903220220220950.pdf | ComleyB | 1903220220220950 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | whoclrvby0qkzy0ddo9 | Low Risk closed | Risk Closed | 44630.5239 | Obs8 | Measures To Limit Fire Spread And Development | 45344 | Low | Court Manager | Flat 5 - automatic closure has been disconnected, door not closing. Automatic closure to be reunited and damage to be repaired to hinge side of door | Refitted and adjusted. Filled hole in door.
1904 | Mountbatten Court | MOUNTBATTEN_S001 | H21 | Scheme | 2022-01-27 12:41 | FRA_1904270120221215.pdf | fowlerb1 | 1904270120221210 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | wi85zu9mcukywydlvk | Low Risk closed | Risk Closed | 44662.4024 | Obs14 | Access By Emergency Services | 45318 | Low | Court Manager | Fire assembly point signage missing | Now have the sign in place.
1904 | Mountbatten Court | MOUNTBATTEN_S001 | H21 | Scheme | 2022-01-27 12:41 | FRA_1904270120221215.pdf | fowlerb1 | 1904270120221210 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | ysz8xrmogvqkywxwuke | Observation Only | Risk Closed | 44649.369 | Obs1 | The Building | NULL | N/A | Surveyor | Fire stopping evidence - for information only | This is information only
1904 | Mountbatten Court | MOUNTBATTEN_S001 | H21 | Scheme | 2022-01-27 12:41 | FRA_1904270120221215.pdf | fowlerb1 | 1904270120221210 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 2p2rwtfckg4kywxwumt | High Risk Closed | Risk Closed | 44634.4483 | Obs6 | Fire Hazards - Elimination & Control | 44678 | High | Court Manager | Laundry electrics | electrician has removed old wires and boxed in
1904 | Mountbatten Court | MOUNTBATTEN_S001 | H21 | Scheme | 2022-01-27 12:41 | FRA_1904270120221215.pdf | fowlerb1 | 1904270120221210 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 47ave5q274xkywxwum8 | High Risk Closed | Risk Closed | 44634.4477 | Obs6 | Fire Hazards - Elimination & Control | 44678 | High | Court Manager | Laundry electrics | Electrician has now tidied wires and boxed in.
1904 | Mountbatten Court | MOUNTBATTEN_S001 | H21 | Scheme | 2022-01-27 12:41 | FRA_1904270120221215.pdf | fowlerb1 | 1904270120221210 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | ln3wyogmybnkywyl23w | Observation Only | Risk Closed | 44649.3686 | Obs15 | Management Of Fire Safety | NULL | N/A | Surveyor | P50 - for information only | This is information only
1904 | Mountbatten Court | MOUNTBATTEN_S001 | H21 | Scheme | 2022-01-27 12:41 | FRA_1904270120221215.pdf | fowlerb1 | 1904270120221210 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | jf2y1xl2zqkywxwunt | Medium Risk closed | Risk Closed | 44671.6058 | Obs6 | Fire Hazards - Elimination & Control | 44953 | Medium | Court Manager | Garage buggy store | Smoke detector fitted and linked to fire panel
1904 | Mountbatten Court | MOUNTBATTEN_S001 | H21 | Scheme | 2022-01-27 12:41 | FRA_1904270120221215.pdf | fowlerb1 | 1904270120221210 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | tjlxicpomykywxwula | Observation Only | Risk Closed | 44649.3688 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel for information only | This is information only
1904 | Mountbatten Court | MOUNTBATTEN_S001 | H21 | Scheme | 2022-01-27 12:41 | FRA_1904270120221215.pdf | fowlerb1 | 1904270120221210 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | roes676ys3ekywxwuna | High Risk Closed | Risk Closed | 44634.447 | Obs6 | Fire Hazards - Elimination & Control | 44678 | High | Court Manager | Flat 3 communal electrics | Electrician has now completed work of taking old cables out.
1905 | Reginald Mitchell Court | REGINALDMITC_S001 | H21 | Scheme | 2022-02-24 12:29 | FRA_1905240220221139.pdf | ComleyB | 1905240220221130 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | rwomzckvtudl00xmfhp | Low Risk closed | Risk Closed | 44725.4452 | Obs1 | The Building | 45346 | Low | Court Manager | Penetration to be fire stopped | Work ORDER RAISED, completed on 10/06/22
1905 | Reginald Mitchell Court | REGINALDMITC_S001 | H21 | Scheme | 2022-02-24 12:29 | FRA_1905240220221139.pdf | ComleyB | 1905240220221130 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 3kolh40h2n4l00y60k6 | Low Risk closed | Risk Closed | 44636.5045 | Obs8 | Measures To Limit Fire Spread And Development | 45346 | Low | Court Manager | Flat 6 - Free swing closure or automatic closure to be fitted | Work ORDER RAISED, part ordered, JOB COMPLETED 14th Mar
1905 | Reginald Mitchell Court | REGINALDMITC_S001 | H21 | Scheme | 2022-02-24 12:29 | FRA_1905240220221139.pdf | ComleyB | 1905240220221130 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 8q229m5jdi8l00wxf6r | Observation Only | Risk Open | NULL | Obs15 | Management Of Fire Safety | NULL | N/A | Other | All compliance checks stored on PEBBLES and ERICA | NULL
1906 | Malmesbury Court | MALMESBURY_S001 | H21 | Scheme | 2022-10-26 14:16 | FRA_1906261020221213.pdf | ComleyB | 1906261020221210 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | a5yrsdlxoyjl9plxte2 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45591 | Low | Court Manager | Flat 6 front door not self closing. Door may need ease and adjusting or planing. | NULL
1906 | Malmesbury Court | MALMESBURY_S001 | H21 | Scheme | 2022-10-26 14:16 | FRA_1906261020221213.pdf | ComleyB | 1906261020221210 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 3hx6b02avssl9pnjrib | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45591 | Low | Court Manager | Sticky pads to be removed from door stop on compartment fire door. | NULL
1906 | Malmesbury Court | MALMESBURY_S001 | H21 | Scheme | 2022-10-26 14:16 | FRA_1906261020221213.pdf | ComleyB | 1906261020221210 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 4cbt71dndjjl9plh639 | Low Risk closed | Risk Closed | 44887.7064 | Obs15 | Management Of Fire Safety | 45591 | Low | Court Manager | Fire Safety Manager training to be updated and recorded in fire safety management folder. | Attended 21/11/2022
1906 | Malmesbury Court | MALMESBURY_S001 | H21 | Scheme | 2022-10-26 14:16 | FRA_1906261020221213.pdf | ComleyB | 1906261020221210 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | ov33i311pfl9pm4ib1 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45591 | Low | Court Manager | Flat 7 flat door not fully closing and need ease and adjusting. | NULL
1906 | Malmesbury Court | MALMESBURY_S001 | H21 | Scheme | 2022-10-26 14:16 | FRA_1906261020221213.pdf | ComleyB | 1906261020221210 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | jfh163uinnol9pll6h4 | Observation Only | Risk Open | NULL | Obs16 | Testing And Maintenance | NULL | N/A | Other | Compliance checks stored on PEBBLES. | NULL
1906 | Malmesbury Court | MALMESBURY_S001 | H21 | Scheme | 2022-10-26 14:16 | FRA_1906261020221213.pdf | ComleyB | 1906261020221210 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | wdfhwq612ql9pn7i9n | Low Risk closed | Risk Closed | 44883.7052 | Obs8 | Measures To Limit Fire Spread And Development | 45591 | Low | Court Manager | Flat 2 front door wedged open. Door must not be wedged open and foam to be removed from door stop as preventing door from closing. | spoke to resident and done
1906 | Malmesbury Court | MALMESBURY_S001 | H21 | Scheme | 2022-10-26 14:16 | FRA_1906261020221213.pdf | ComleyB | 1906261020221210 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | vakez1u8qlal9pmblwe | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45591 | Low | Court Manager | Flat 11 front door not self closing. Underlay to be removed from hallway carpet to reduce friction. | NULL
1907 | Hylton Court | HYLTON_S001 | H21 | Scheme | 2022-09-12 13:04 | FRA_1907120920221001.pdf | pickfordj | 1907120920221000 | Retirement Housing | Mid South | Berks and Hampshire North | South | South Patch 4 | 7p57gxjoovjl7ypudp1 | Low Risk closed | Risk Closed | 44839.4849 | Obs8 | Measures To Limit Fire Spread And Development | 45547 | Low | Court Manager | As noted p,ease get fire doors adjusted | laundry door and flat 7 have now been adjusted by Handyperson service and closing properly.
1907 | Hylton Court | HYLTON_S001 | H21 | Scheme | 2022-09-12 13:04 | FRA_1907120920221001.pdf | pickfordj | 1907120920221000 | Retirement Housing | Mid South | Berks and Hampshire North | South | South Patch 4 | 04ypgbxupodrl7yjqr6e | Observation Only | Risk Closed | 44816.653 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Smoking, residents appear to not be sticking to the policy and smoking in the designated area and are just smoking where they want or out the front | Remind Residents at the next Resident Meeting of the Court service agreement and designated area for smoking.
1908 | Charles Ley Court | CHARLESLEY_S001 | H21 | Scheme | 2022-09-20 14:36 | FRA_1908200920221425.pdf | fowlerb1 | 1908200920221420 | Retirement Housing | South West | Dorset | South | South Patch 2 | c5wbqic289l8a8bktu | Observation Only | Risk Closed | 44832.4505 | Obs10 | Fire Safety And Notices | NULL | N/A | Surveyor | Fire action notices for information only | Information only
1908 | Charles Ley Court | CHARLESLEY_S001 | H21 | Scheme | 2022-09-20 14:36 | FRA_1908200920221425.pdf | fowlerb1 | 1908200920221420 | Retirement Housing | South West | Dorset | South | South Patch 2 | gazds43ho18l8a8bkss | Observation Only | Risk Closed | 44832.4507 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel for information only | Information only
1908 | Charles Ley Court | CHARLESLEY_S001 | H21 | Scheme | 2022-09-20 14:36 | FRA_1908200920221425.pdf | fowlerb1 | 1908200920221420 | Retirement Housing | South West | Dorset | South | South Patch 2 | r4mxolrmrsl8a8f830 | Observation Only | Risk Closed | 44832.4509 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Surveyor | Buggy store for information only - buggies need to be included with pat testing | Information only
1909 | Charles Dalton Court | CHARLESDALT_S001 | H21 | Scheme | 2022-02-22 11:12 | FRA_1909220220221001.pdf | fowlerb1 | 1909220220221000 | Retirement Housing | Mid South | Berks and Hampshire North | South | South Patch 5 | ouqjrdv04emkzxzdqsa | Observation Only | Risk Closed | 44649.3693 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel & zone plan | This is information only
1909 | Charles Dalton Court | CHARLESDALT_S001 | H21 | Scheme | 2022-02-22 11:12 | FRA_1909220220221001.pdf | fowlerb1 | 1909220220221000 | Retirement Housing | Mid South | Berks and Hampshire North | South | South Patch 5 | iamfi7sftnkzxzxedh | Observation Only | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Bin store | NULL
1909 | Charles Dalton Court | CHARLESDALT_S001 | H21 | Scheme | 2022-02-22 11:12 | FRA_1909220220221001.pdf | fowlerb1 | 1909220220221000 | Retirement Housing | Mid South | Berks and Hampshire North | South | South Patch 5 | l1957nr1ekkzy024ii | Medium Risk closed | Risk Closed | 44791.6565 | Obs6 | Fire Hazards - Elimination & Control | 44979 | Medium | Court Manager | Gas bbq | all complete
1909 | Charles Dalton Court | CHARLESDALT_S001 | H21 | Scheme | 2022-02-22 11:12 | FRA_1909220220221001.pdf | fowlerb1 | 1909220220221000 | Retirement Housing | Mid South | Berks and Hampshire North | South | South Patch 5 | mfy8rk6a0fkzy046tb | Observation Only | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Kitchen p50 fire extinguisher | NULL
1909 | Charles Dalton Court | CHARLESDALT_S001 | H21 | Scheme | 2022-02-22 11:12 | FRA_1909220220221001.pdf | fowlerb1 | 1909220220221000 | Retirement Housing | Mid South | Berks and Hampshire North | South | South Patch 5 | c1pibwmby9kzy0ke8p | Observation Only | Risk Closed | 44649.3691 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Surveyor | Flat 1 only internal door | This is information only
1909 | Charles Dalton Court | CHARLESDALT_S001 | H21 | Scheme | 2022-02-22 11:12 | FRA_1909220220221001.pdf | fowlerb1 | 1909220220221000 | Retirement Housing | Mid South | Berks and Hampshire North | South | South Patch 5 | 829awupkbo5kzy0056n | Observation Only | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Communal kitchen | NULL
1909 | Charles Dalton Court | CHARLESDALT_S001 | H21 | Scheme | 2022-02-22 11:12 | FRA_1909220220221001.pdf | fowlerb1 | 1909220220221000 | Retirement Housing | Mid South | Berks and Hampshire North | South | South Patch 5 | 3kswfzgsc5ekzy0mvwp | Observation Only | Risk Open | NULL | Obs10 | Fire Safety And Notices | NULL | N/A | Court Manager | Fire action notice | NULL
1909 | Charles Dalton Court | CHARLESDALT_S001 | H21 | Scheme | 2022-02-22 11:12 | FRA_1909220220221001.pdf | fowlerb1 | 1909220220221000 | Retirement Housing | Mid South | Berks and Hampshire North | South | South Patch 5 | wa4n0q5kiqakzy09iov | Observation Only | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | External meter cupboards | NULL
1909 | Charles Dalton Court | CHARLESDALT_S001 | H21 | Scheme | 2022-02-22 11:12 | FRA_1909220220221001.pdf | fowlerb1 | 1909220220221000 | Retirement Housing | Mid South | Berks and Hampshire North | South | South Patch 5 | zjp47d1j3pkkzy0t9g9 | Observation Only | Risk Closed | 44649.3696 | Obs14 | Access By Emergency Services | NULL | N/A | Surveyor | Car park | This is information only
1910 | Latham Court | LATHAM_S001 | H21 | Scheme | 2022-10-12 15:59 | FRA_1910121020221350.pdf | ComleyB | 1910121020221350 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 1y068raneuol95qktug | Low Risk closed | Risk Closed | 44854.3785 | Obs8 | Measures To Limit Fire Spread And Development | 45577 | Low | Court Manager | Flat 43 front door not fully closing. Keep may need adjusting. | Will inform tenants that handle has to be raised when closing door inside as advised by installer
1910 | Latham Court | LATHAM_S001 | H21 | Scheme | 2022-10-12 15:59 | FRA_1910121020221350.pdf | ComleyB | 1910121020221350 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 0tfoydye3cpl95ob20w | Observation Only | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Other | Most flat front doors open to external walkway with two directions of travel for escape. Flats that are located on single route of travel or are internal have a minimum of 30 minutes protection (FD30). | NULL
1910 | Latham Court | LATHAM_S001 | H21 | Scheme | 2022-10-12 15:59 | FRA_1910121020221350.pdf | ComleyB | 1910121020221350 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 1u4drrnfcnhl95q7lio | Low Risk closed | Risk Closed | 44851.6184 | Obs6 | Fire Hazards - Elimination & Control | 45577 | Low | Court Manager | Mobility scooter chargers to be PAT tested. | All owners of scooters were sent letter requesting they pat test their charging equipment
1910 | Latham Court | LATHAM_S001 | H21 | Scheme | 2022-10-12 15:59 | FRA_1910121020221350.pdf | ComleyB | 1910121020221350 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 1ctigovcof6l95onlxi | Low Risk closed | Risk Closed | 44847.4339 | Obs15 | Management Of Fire Safety | 45577 | Low | Court Manager | Fire management training records to be updated and placed in fire safety management folder. | Records updated and filed
1910 | Latham Court | LATHAM_S001 | H21 | Scheme | 2022-10-12 15:59 | FRA_1910121020221350.pdf | ComleyB | 1910121020221350 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 7xg3zqnpmtml95qb3bp | Low Risk closed | Risk Closed | 44851.6176 | Obs6 | Fire Hazards - Elimination & Control | 45577 | Low | Court Manager | Mobility scooter currently impeding escape route. Scooter to be moved to allow sufficient passing. | Resident flat 39 was asked to move scooter to allow better access
1910 | Latham Court | LATHAM_S001 | H21 | Scheme | 2022-10-12 15:59 | FRA_1910121020221350.pdf | ComleyB | 1910121020221350 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 4lnqr8k7016l95orlki | Observation Only | Risk Open | NULL | Obs15 | Management Of Fire Safety | NULL | N/A | Other | Compliance checks stored on PEBBLES. | NULL
1910 | Latham Court | LATHAM_S001 | H21 | Scheme | 2022-10-12 15:59 | FRA_1910121020221350.pdf | ComleyB | 1910121020221350 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 5kdiqrvb1ql95oltxa | Observation Only | Risk Open | NULL | Obs14 | Access By Emergency Services | NULL | N/A | Other | Fire assembly point located to small clearing by endeavour close (access road). | NULL
1910 | Latham Court | LATHAM_S001 | H21 | Scheme | 2022-10-12 15:59 | FRA_1910121020221350.pdf | ComleyB | 1910121020221350 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 9r9fzggmnpml95o3bdq | Observation Only | Risk Closed | 44847.4262 | Obs7 | Fire Protection Measures | NULL | N/A | Court Manager | Mobility scooters stored on external walkways. There is sufficient room to pass safely. Court manager to ensure Scooters do not impede escape routes or block block access. | Ongoing to be monitored
1910 | Latham Court | LATHAM_S001 | H21 | Scheme | 2022-10-12 15:59 | FRA_1910121020221350.pdf | ComleyB | 1910121020221350 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | k7wyp6zwm4jl95ov8yk | Low Risk closed | Risk Closed | 44847.4239 | Obs15 | Management Of Fire Safety | 45212 | Low | Court Manager | Fire Safety Responsibilities matrix to be completed and placed in fire safety management. | matrix completed as filed as requested
1910 | Latham Court | LATHAM_S001 | H21 | Scheme | 2022-10-12 15:59 | FRA_1910121020221350.pdf | ComleyB | 1910121020221350 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | pvbkl5jpcyil95oq2ro | Low Risk closed | Risk Closed | 44847.423 | Obs15 | Management Of Fire Safety | 45577 | Low | Court Manager | Fire Safety training due for renewal in January 2023. | manager aware of renewal dates for training January 2023
1911 | Brunel Court | BRUNEL_S001 | H21 | Scheme | 2022-10-31 12:31 | FRA_1911311020221152.pdf | ComleyB | 1911311020221150 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | pdcepseplcil9wq15oq | Observation Only | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | NULL | N/A | Court Manager | Court Manager to complete Fire Safety Training, due for renewal in January 2023. | NULL
1911 | Brunel Court | BRUNEL_S001 | H21 | Scheme | 2022-10-31 12:31 | FRA_1911311020221152.pdf | ComleyB | 1911311020221150 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | phfn875bljgl9wq3924 | Low Risk closed | Risk Closed | 44866.5105 | Obs8 | Measures To Limit Fire Spread And Development | 45596 | Low | Court Manager | Flat 14 front flat door lock to be adjusted, preventing door from self closing. | works order raised 1572505 Kings maintenance attended 1-11-2022
1911 | Brunel Court | BRUNEL_S001 | H21 | Scheme | 2022-10-31 12:31 | FRA_1911311020221152.pdf | ComleyB | 1911311020221150 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | ubsciqh4al9wq15pk | Low Risk closed | Risk Closed | 44865.5724 | Obs5 | Evacuation Strategy And Training | 45596 | Low | Court Manager | Indicate on plans in resident fire box where gas and electrical shut off points are. | completed gas and electric cuts off in court fire plan in the red fire box
1911 | Brunel Court | BRUNEL_S001 | H21 | Scheme | 2022-10-31 12:31 | FRA_1911311020221152.pdf | ComleyB | 1911311020221150 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | jzn0201orill9wq15s0 | Observation Only | Risk Closed | 44865.5687 | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | Only latest FRA required to be stored in folder. Previous FRA's to be archived. | Old copies have been achieved and just the new copy is in the fire folder
1911 | Brunel Court | BRUNEL_S001 | H21 | Scheme | 2022-10-31 12:31 | FRA_1911311020221152.pdf | ComleyB | 1911311020221150 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | fywuficwamgl9wqnzaq | Low Risk closed | Risk Closed | 44866.5115 | Obs8 | Measures To Limit Fire Spread And Development | 45596 | Low | Court Manager | Flat 24 front door not fully sitting in frame and may require ease and adjusting. | works order raised 1572508 kings maintenance attended 1-11-2022
1911 | Brunel Court | BRUNEL_S001 | H21 | Scheme | 2022-10-31 12:31 | FRA_1911311020221152.pdf | ComleyB | 1911311020221150 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | baw3mg969wl9wqswiz | Low Risk closed | Risk Closed | 44866.5099 | Obs8 | Measures To Limit Fire Spread And Development | 45596 | Low | Court Manager | Flat 28 front door not fully closing, keep may require ease and adjusting. | works order raised 1572508 - Kings maintenance attended 1-11-2022
1911 | Brunel Court | BRUNEL_S001 | H21 | Scheme | 2022-10-31 12:31 | FRA_1911311020221152.pdf | ComleyB | 1911311020221150 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | dwxtixy5o5sl9wq15qo | Low Risk closed | Risk Closed | 44867.3763 | Obs8 | Measures To Limit Fire Spread And Development | 45596 | Low | Court Manager | Electrical controls to door opener hanging loose. | works order raised to lift tech - lift tech attended 1-11-22 now all boxed in
1911 | Brunel Court | BRUNEL_S001 | H21 | Scheme | 2022-10-31 12:31 | FRA_1911311020221152.pdf | ComleyB | 1911311020221150 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | yhx630tch7l9wq6oij | Low Risk closed | Risk Closed | 44868.4288 | Obs8 | Measures To Limit Fire Spread And Development | 45596 | Low | Court Manager | Fire stopping been removed by tv ariel company. Cables to be adequately fire stopped by accredited operative. | Tv aerial Specialist Ltd has completed the fire stopping works in the area of the installation of the new sky dish. completed 03/11/2022
1912 | James Butcher Court | JBJAMESBUTCHER_S001 | H21 | Scheme | 2022-07-27 12:24 | FRA_1912270720221027.pdf | ComleyB | 1912270720221020 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | f9edbryvakl63hpcia | Low Risk closed | Risk Closed | 44879.3652 | Obs8 | Measures To Limit Fire Spread And Development | 45500 | Low | Court Manager | Flat 2 Door not automatically closing. Catching on carpet. Door ans Drop plate to be adjusted. | WO COMPLETED
1912 | James Butcher Court | JBJAMESBUTCHER_S001 | H21 | Scheme | 2022-07-27 12:24 | FRA_1912270720221027.pdf | ComleyB | 1912270720221020 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | d0ntua5ncwwl63h4wk2 | Low Risk closed | Risk Closed | 44774.5075 | Obs5 | Evacuation Strategy And Training | 45500 | Low | Court Manager | Resident fire risk information sheet to be updated. | AMENDED
1912 | James Butcher Court | JBJAMESBUTCHER_S001 | H21 | Scheme | 2022-07-27 12:24 | FRA_1912270720221027.pdf | ComleyB | 1912270720221020 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | ajfbueryh0hl63hr88u | Low Risk closed | Risk Closed | 44860.4308 | Obs8 | Measures To Limit Fire Spread And Development | 45500 | Low | Court Manager | Drop plates on entrance doors to be cleaned and ensure all are working. | RR WORKS CARRIED OUT
1912 | James Butcher Court | JBJAMESBUTCHER_S001 | H21 | Scheme | 2022-07-27 12:24 | FRA_1912270720221027.pdf | ComleyB | 1912270720221020 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 9206rasrh1l63fno7g | Low Risk closed | Risk Closed | 44774.5073 | Obs15 | Management Of Fire Safety | 45500 | Low | Court Manager | Resident fire box information sheet in fire management folder to be updated | AMENDED
1912 | James Butcher Court | JBJAMESBUTCHER_S001 | H21 | Scheme | 2022-07-27 12:24 | FRA_1912270720221027.pdf | ComleyB | 1912270720221020 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 923fk32devl63hzpqf | Low Risk closed | Risk Closed | 44860.4305 | Obs8 | Measures To Limit Fire Spread And Development | 45500 | Low | Court Manager | Flat 16 door not fully closing. Door and Keep to be adjusted. | RR works
1912 | James Butcher Court | JBJAMESBUTCHER_S001 | H21 | Scheme | 2022-07-27 12:24 | FRA_1912270720221027.pdf | ComleyB | 1912270720221020 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 92cuoks45zl63hbv81 | Low Risk closed | Risk Closed | 44774.5078 | Obs8 | Measures To Limit Fire Spread And Development | 45500 | Low | Court Manager | Flat 4 door mat holding door open. Door mat to be removed. | SURVEYOR ASKED RESIDENT TO REMOVE HER MAT
1912 | James Butcher Court | JBJAMESBUTCHER_S001 | H21 | Scheme | 2022-07-27 12:24 | FRA_1912270720221027.pdf | ComleyB | 1912270720221020 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 820qb2h0wfpl63f14af | Observation Only | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Other | Fire alarm system is in the process of the of being re-zoned to provide early detection to nearby flats. Should the fire alarm be activated, the alarm will sound within the property of activation and adjoining properties deemed at risk. | NULL
1912 | James Butcher Court | JBJAMESBUTCHER_S001 | H21 | Scheme | 2022-07-27 12:24 | FRA_1912270720221027.pdf | ComleyB | 1912270720221020 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 74qkfbfmvril63gwbdu | Low Risk closed | Risk Closed | 44774.5085 | Obs6 | Fire Hazards - Elimination & Control | 45500 | Low | Court Manager | Mobility scooter chargers to be PAT tested | OWNERS ASKED TO PAT TEST AND COPY TO CM WHEN TESTED
1912 | James Butcher Court | JBJAMESBUTCHER_S001 | H21 | Scheme | 2022-07-27 12:24 | FRA_1912270720221027.pdf | ComleyB | 1912270720221020 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 3da8goyi13ul63gql1m | Low Risk to be actioned | Risk Open | NULL | Obs1 | The Building | 45500 | Low | Surveyor | Penthouse balcony is shared between between two properties. | NULL
1912 | James Butcher Court | JBJAMESBUTCHER_S001 | H21 | Scheme | 2022-07-27 12:24 | FRA_1912270720221027.pdf | ComleyB | 1912270720221020 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | iakkbq527al63h35at | Low Risk closed | Risk Closed | 44774.5234 | Obs5 | Evacuation Strategy And Training | 45500 | Low | Court Manager | Gas isolation valve to be identified tidied on court floor plans. | EXTERIOR OF BUILDING BY FRONT DOOR 2 GAS POINTS ON COURT PLANS
1912 | James Butcher Court | JBJAMESBUTCHER_S001 | H21 | Scheme | 2022-07-27 12:24 | FRA_1912270720221027.pdf | ComleyB | 1912270720221020 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | kdccmj436ycl63g4pwn | Low Risk closed | Risk Closed | 44781.336 | Obs6 | Fire Hazards - Elimination & Control | 45500 | Low | Court Manager | Door stops to be removed from from door entrances to prevent fire doors being held open. Communal lounge to be fitted with sound operated door gaurd | Removed and residents informed
1912 | James Butcher Court | JBJAMESBUTCHER_S001 | H21 | Scheme | 2022-07-27 12:24 | FRA_1912270720221027.pdf | ComleyB | 1912270720221020 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | m6rndv8h8wrl63g2sk9 | Low Risk closed | Risk Closed | 44774.5082 | Obs6 | Fire Hazards - Elimination & Control | 45500 | Low | Court Manager | Portable heater to be replaced in communal lounge | REMOVED
1916 | Alexandra Court | ALEXANDRA_B001 | H21 | Unknown | 2019-11-19 12:27 | FRA_191619112019.pdf | ComleyB | 191619112019 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | ira3u7y2d4k35rhjor | Medium Risk Overdue | Risk Open | NULL | Obs16 | Testing And Maintenance | 44154 | Medium | M&E Team | Lighenting protection to be serviced. | NULL
1916 | Alexandra Court | ALEXANDRA_B001 | H21 | Unknown | 2019-11-19 12:27 | FRA_191619112019.pdf | ComleyB | 191619112019 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | ira3u7y2d4k35rhjor | Medium Risk Overdue | Risk Open | NULL | Obs16 | Testing And Maintenance | 44154 | Medium | M&E Team | Lighenting protection to be serviced. | NULL
1916 | Alexandra Court | ALEXANDRA_S001 | H21 | Scheme | 2022-08-15 11:59 | FRA_1916150820221000.pdf | mayesd | 1916150820221000 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | i19ilisrxthl6ului7g | Medium Risk closed | Risk Closed | 44797.6363 | Obs7 | Fire Protection Measures | 45153 | Medium | Court Manager | Fire stopping a defective where the sprinkler pipe enters the managers office and around the cable tray above the false ceiling in the corridors | Passed to Bryn as this is an Asset Management funded project
1916 | Alexandra Court | ALEXANDRA_S001 | H21 | Scheme | 2022-08-15 11:59 | FRA_1916150820221000.pdf | mayesd | 1916150820221000 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | rp52li0v7gl6ukdpjk | Low Risk closed | Risk Closed | 44797.4947 | Obs8 | Measures To Limit Fire Spread And Development | 45519 | Low | Court Manager | One screw missing from the hinge or Flat 41 front door | Order Number 1558274
1916 | Alexandra Court | ALEXANDRA_B001 | H21 | Unknown | 2019-11-19 12:27 | FRA_191619112019.pdf | ComleyB | 191619112019 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | qo95xal386mk35tfg5v | Medium Risk closed | Risk Closed | 43864.7005 | Obs8 | Measures To Limit Fire Spread And Development | 44154 | Medium | Court Manager | Where removed, drop plates to be reinstalled. | Costed for the advised 7 and there were eight.completed by Ace today
1916 | Alexandra Court | ALEXANDRA_B001 | H21 | Unknown | 2019-11-19 12:27 | FRA_191619112019.pdf | ComleyB | 191619112019 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | qo95xal386mk35tfg5v | Medium Risk closed | Risk Closed | 43788.5985 | Obs8 | Measures To Limit Fire Spread And Development | 44154 | Medium | Court Manager | Where removed, drop plates to be reinstalled. | Contacted Ace for coatings with images 7 in total
1916 | Alexandra Court | ALEXANDRA_S001 | H21 | Scheme | 2022-08-15 11:59 | FRA_1916150820221000.pdf | mayesd | 1916150820221000 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | nhwdddxmdml6uk1bqr | Low Risk closed | Risk Closed | 44890.5476 | Obs14 | Access By Emergency Services | 45519 | Low | Court Manager | Assembly point should be repositioned away from the sprinkler control room. Location to be agreed on court managers return | Its is not possible to relocate the assembly point as this is the furthest point from the building & the only area with no direct vehicular access to obstruct - in any case this is only the point to meet & then transfer to James Butcher Court upper lounge
1916 | Alexandra Court | ALEXANDRA_S001 | H21 | Scheme | 2022-08-15 11:59 | FRA_1916150820221000.pdf | mayesd | 1916150820221000 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 3t98debl0shl6uj8cej | Medium Risk closed | Risk Closed | 44806.7168 | Obs15 | Management Of Fire Safety | 45153 | Medium | Court Manager | The Policy and Procedure document requires updating to the new version. | Error
1916 | Alexandra Court | ALEXANDRA_B001 | H21 | Unknown | 2019-11-19 12:27 | FRA_191619112019.pdf | ComleyB | 191619112019 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 3xfm3ncr9ekk35rdqq2 | Low Risk closed | Risk Closed | 43788.5851 | Obs15 | Management Of Fire Safety | 44519 | Low | Court Manager | Attemot meeting with residents and Fire brigade. | Last email request was July 2019 and today 19th November 2019 we have requested another FSVisit. It is now quite difficult with reduced staffing /funding as these officers are responding to live call outs.
1916 | Alexandra Court | ALEXANDRA_B001 | H21 | Unknown | 2019-11-19 12:27 | FRA_191619112019.pdf | ComleyB | 191619112019 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 3xfm3ncr9ekk35rdqq2 | Low Risk closed | Risk Closed | 43804.4097 | Obs15 | Management Of Fire Safety | 44519 | Low | Court Manager | Attemot meeting with residents and Fire brigade. | Fire Safety meeting planned 12th December 2019
1916 | Alexandra Court | ALEXANDRA_B001 | H21 | Unknown | 2019-11-19 12:27 | FRA_191619112019.pdf | ComleyB | 191619112019 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 3xfm3ncr9ekk35rdqq2 | Low Risk closed | Risk Closed | 43788.5851 | Obs15 | Management Of Fire Safety | 44519 | Low | Court Manager | Attemot meeting with residents and Fire brigade. | Last email request was July 2019 and today 19th November 2019 we have requested another FSVisit. It is now quite difficult with reduced staffing /funding as these officers are responding to live call outs.
1916 | Alexandra Court | ALEXANDRA_B001 | H21 | Unknown | 2019-11-19 12:27 | FRA_191619112019.pdf | ComleyB | 191619112019 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 3xfm3ncr9ekk35rdqq2 | Low Risk closed | Risk Closed | 43804.4097 | Obs15 | Management Of Fire Safety | 44519 | Low | Court Manager | Attemot meeting with residents and Fire brigade. | Fire Safety meeting planned 12th December 2019
1916 | Alexandra Court | ALEXANDRA_S001 | H21 | Scheme | 2022-08-15 11:59 | FRA_1916150820221000.pdf | mayesd | 1916150820221000 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 8b6rlqopz7sl6ukg7jc | Medium Risk closed | Risk Closed | 44890.5455 | Obs13 | Other Relevant Fixed Systems | 45153 | Medium | Court Manager | Openview or others to establish the purpose of the coiled red cable above the lifts and either reconnect or remove | CM emailed David Mayes in April 2022 as the works that had not been briefed had remained incomplete and Ed Hayward is now looking into this & has yet to confirm that Otis are over due to complete the works to adjust the lifts during a fir activation
1916 | Alexandra Court | ALEXANDRA_S001 | H21 | Scheme | 2022-08-15 11:59 | FRA_1916150820221000.pdf | mayesd | 1916150820221000 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | acwcgf9y33bl6um2lb6 | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45153 | Medium | Court Manager | Excessive lint is evident on the external dryer vent pipes. These will need to be cleaned | NULL
1916 | Alexandra Court | ALEXANDRA_B001 | H21 | Unknown | 2019-11-19 12:27 | FRA_191619112019.pdf | ComleyB | 191619112019 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | a2j39yy9tt8k35r5qae | Low Risk closed | Risk Closed | 43791.5579 | Obs7 | Fire Protection Measures | 44519 | Low | Court Manager | Bikes to be removed from escape stairwell. | Plan is to move them into the mobility store on racks early 2020.this is a historical arrangement that has been through the complaint process
1916 | Alexandra Court | ALEXANDRA_B001 | H21 | Unknown | 2019-11-19 12:27 | FRA_191619112019.pdf | ComleyB | 191619112019 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | a2j39yy9tt8k35r5qae | Low Risk closed | Risk Closed | 43804.4025 | Obs7 | Fire Protection Measures | 44519 | Low | Court Manager | Bikes to be removed from escape stairwell. | Deferred resolution until mobility store is built
1916 | Alexandra Court | ALEXANDRA_B001 | H21 | Unknown | 2019-11-19 12:27 | FRA_191619112019.pdf | ComleyB | 191619112019 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 9xk2jprhrfvk35rutth | Medium Risk Overdue | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44154 | Medium | M&E Team | Laundry Room ducts to be serviced. | NULL
1916 | Alexandra Court | ALEXANDRA_B001 | H21 | Unknown | 2019-11-19 12:27 | FRA_191619112019.pdf | ComleyB | 191619112019 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | wbm7tlsp1xok35r8i55 | Observation Only | Risk Open | NULL | Obs13 | Other Relevant Fixed Systems | NULL | N/A | Other | Dry riser to be charged and converted to wet riser for sprinkler system. | NULL
1916 | Alexandra Court | ALEXANDRA_B001 | H21 | Unknown | 2019-11-19 12:27 | FRA_191619112019.pdf | ComleyB | 191619112019 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | w13fm18c7yk35qv4ya | Low Risk closed | Risk Closed | 43809.5927 | Obs6 | Fire Hazards - Elimination & Control | 44519 | Low | Court Manager | Residents using communal mobility store charging points to have chargers PAT tested. | Advised in court news
1916 | Alexandra Court | ALEXANDRA_B001 | H21 | Unknown | 2019-11-19 12:27 | FRA_191619112019.pdf | ComleyB | 191619112019 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | w13fm18c7yk35qv4ya | Low Risk closed | Risk Closed | 43788.603 | Obs6 | Fire Hazards - Elimination & Control | 44519 | Low | Court Manager | Residents using communal mobility store charging points to have chargers PAT tested. | This will be auctioned with new store facility .there are fixed power surge protectors. Next corporate Pat test is due in june 2020
1916 | Alexandra Court | ALEXANDRA_S001 | H21 | Scheme | 2022-08-15 11:59 | FRA_1916150820221000.pdf | mayesd | 1916150820221000 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | yu53wvpmhzsl6ulybfs | Medium Risk closed | Risk Closed | 44797.4856 | Obs10 | Fire Safety And Notices | 45153 | Medium | Court Manager | The building fire main has been converted to a wet riser but the sign states dry riser. This needs to be removed | Removed 24/08/22
1916 | Alexandra Court | ALEXANDRA_S001 | H21 | Scheme | 2022-08-15 11:59 | FRA_1916150820221000.pdf | mayesd | 1916150820221000 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | yx4rqx31iqol6ump8g7 | Medium Risk closed | Risk Closed | 44795.6744 | Obs4 | The Occupant - Information Provided By The Court Manager | 45153 | Medium | Court Manager | PCFRA summary needs to be within the red fire box by the main entrance. The policy also needs to be changed to reflect the new version | Was in the box - updated last 05/07/22
1917 | Osprey Court | OSPREY_S001 | H21 | Scheme | 2022-09-21 13:49 | FRA_1917210920221340.pdf | ComleyB | 1917210920221340 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | 9td0i9axp0el8bm4p4o | Low Risk closed | Risk Closed | 44867.4753 | Obs8 | Measures To Limit Fire Spread And Development | 45556 | Low | Court Manager | Flat 5 front door to be eased and adjusted, not fully closing. | Contractor eased and adjusted door, now closes flush with fire alarm.
1917 | Osprey Court | OSPREY_S001 | H21 | Scheme | 2022-09-21 13:49 | FRA_1917210920221340.pdf | ComleyB | 1917210920221340 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | pa1a8rl5xul8bm4p6p | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45556 | Low | Surveyor | Fire exit signs to be installed and direct to nearest fire exit. | NULL
1917 | Osprey Court | OSPREY_S001 | H21 | Scheme | 2022-09-21 13:49 | FRA_1917210920221340.pdf | ComleyB | 1917210920221340 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | t9xssynv7ol8bm4p2w | Low Risk closed | Risk Closed | 44867.4965 | Obs5 | Evacuation Strategy And Training | 45556 | Low | Court Manager | Gas isolation and electrical mains fuse to be located on floor plans in fire box | Correctly labelled up as requested.
1917 | Osprey Court | OSPREY_S001 | H21 | Scheme | 2022-09-21 13:49 | FRA_1917210920221340.pdf | ComleyB | 1917210920221340 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | hpz2kvubq1ql8bm4p5m | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45556 | Low | Surveyor | Cable pentrations to be adequately fire stopped. | NULL
1918 | Crane Court | CRANE_S001 | H21 | Scheme | 2022-09-21 13:08 | FRA_1918210920221202.pdf | ComleyB | 1918210920221200 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | nqjyoayxoul8bktspt | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45556 | Low | Surveyor | Fire exit signs to direct to nearest fire exit. | NULL
1918 | Crane Court | CRANE_S001 | H21 | Scheme | 2022-09-21 13:08 | FRA_1918210920221202.pdf | ComleyB | 1918210920221200 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | yz8uaq0lolgl8bki6uu | Low Risk closed | Risk Closed | 44867.5098 | Obs5 | Evacuation Strategy And Training | 45556 | Low | Court Manager | Gas isolation and electrical mains fuse to be located on floor plans in fire box | Correctly labelled up as requested.
1918 | Crane Court | CRANE_S001 | H21 | Scheme | 2022-09-21 13:08 | FRA_1918210920221202.pdf | ComleyB | 1918210920221200 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | zr5xpkfczgel8bkqz9t | Low Risk closed | Risk Closed | 44867.5107 | Obs8 | Measures To Limit Fire Spread And Development | 45556 | Low | Court Manager | Flat front door 2 not fully closing. Door catching on the threshold. | Eased and adjusted by contractor, now closing with fire alarm.
1919 | Brent Court | BRENT_S001 | H21 | Scheme | 2022-09-21 12:02 | FRA_1919210920220949.pdf | ComleyB | 1919210920220940 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | z7ji252p1kgl8bhosx7 | Low Risk to be actioned | Risk Open | NULL | Obs1 | The Building | 45556 | Low | Surveyor | Cable pentration to be fire stopped. | NULL
1919 | Brent Court | BRENT_S001 | H21 | Scheme | 2022-09-21 12:02 | FRA_1919210920220949.pdf | ComleyB | 1919210920220940 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | ofs4c6vsyvrl8bh2ffg | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45556 | Low | Court Manager | Pat testing due to mobility scooter chargers in October. | NULL
1919 | Brent Court | BRENT_S001 | H21 | Scheme | 2022-09-21 12:02 | FRA_1919210920220949.pdf | ComleyB | 1919210920220940 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | h3jky1sk8pl8bi5zlw | Low Risk to be actioned | Risk Open | NULL | Obs1 | The Building | 45556 | Low | Surveyor | Cable penetration to be fire stopped. | NULL
1919 | Brent Court | BRENT_S001 | H21 | Scheme | 2022-09-21 12:02 | FRA_1919210920220949.pdf | ComleyB | 1919210920220940 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | dirysccka06l8bhi4m3 | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45556 | Low | Court Manager | Electrical bike stored in water cupboard. Bike to removed and stored in mobility scooter store or flat | NULL
1920 | Pearce Smith Court | PEARCESMIT_S001 | H21 | Scheme | 2022-04-25 11:51 | FRA_1920250420221015.pdf | fowlerb1 | 1920250420221010 | Retirement Housing | South West | Dorset | South | South Patch 2 | 7dpgxf8g2zol2eiuvvx | Observation Only | Risk Closed | 44719.5864 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel | For information only
1920 | Pearce Smith Court | PEARCESMIT_S001 | H21 | Scheme | 2022-04-25 11:51 | FRA_1920250420221015.pdf | fowlerb1 | 1920250420221010 | Retirement Housing | South West | Dorset | South | South Patch 2 | 7umkonhkpn6l2eizu36 | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | Flats with RA's are 4, 12, 14, 20 & 29. | NULL
1920 | Pearce Smith Court | PEARCESMIT_S001 | H21 | Scheme | 2022-04-25 11:51 | FRA_1920250420221015.pdf | fowlerb1 | 1920250420221010 | Retirement Housing | South West | Dorset | South | South Patch 2 | gtqk9mdnaeol2eja74n | Observation Only | Risk Closed | 44719.5872 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Surveyor | Electric meter flat 6 | For information only
1920 | Pearce Smith Court | PEARCESMIT_S001 | H21 | Scheme | 2022-04-25 11:51 | FRA_1920250420221015.pdf | fowlerb1 | 1920250420221010 | Retirement Housing | South West | Dorset | South | South Patch 2 | ly41culb9cl2eklx4q | Observation Only | Risk Closed | 44719.5869 | Obs10 | Fire Safety And Notices | NULL | N/A | Surveyor | Fire action notice - for information only | For information only
1920 | Pearce Smith Court | PEARCESMIT_S001 | H21 | Scheme | 2022-04-25 11:51 | FRA_1920250420221015.pdf | fowlerb1 | 1920250420221010 | Retirement Housing | South West | Dorset | South | South Patch 2 | menlu1i2gzl2ejdea3 | Observation Only | Risk Closed | 44719.5866 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Surveyor | Electric meter flat 16 | For information only
1922 | Hart Court | HART_S001 | H21 | Scheme | 2022-10-25 16:13 | FRA_1922251020221442.pdf | ComleyB | 1922251020221440 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | mgsf0z2jdkgl9obwltr | Low Risk closed | Risk Closed | 44861.5127 | Obs8 | Measures To Limit Fire Spread And Development | 45590 | Low | Court Manager | Cable pentrations to be fire stopped outside flat 15 | Repair raised as flat us in void status
1922 | Hart Court | HART_S001 | H21 | Scheme | 2022-10-25 16:13 | FRA_1922251020221442.pdf | ComleyB | 1922251020221440 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | k15ryxsccucl9obnmdp | Low Risk closed | Risk Closed | 44861.6872 | Obs5 | Evacuation Strategy And Training | 45590 | Low | Court Manager | Out of date court action plan to be removed from resident fire box. | removed court action plan from resident fire box
1922 | Hart Court | HART_S001 | H21 | Scheme | 2022-10-25 16:13 | FRA_1922251020221442.pdf | ComleyB | 1922251020221440 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | u8zpscr73hrl9ob0iy4 | Low Risk closed | Risk Closed | 44861.6875 | Obs15 | Management Of Fire Safety | 45590 | Low | Court Manager | Fire Safety Responsibilities matrix to be completed. | completed
1922 | Hart Court | HART_S001 | H21 | Scheme | 2022-10-25 16:13 | FRA_1922251020221442.pdf | ComleyB | 1922251020221440 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 4mvcoh8y1kil9obyyah | Low Risk closed | Risk Closed | 44861.4674 | Obs8 | Measures To Limit Fire Spread And Development | 45590 | Low | Court Manager | Flat 16 front door requires ease and adjusting as not automatically closing. May require drop plate if door is shaved down. | Repair raised 27 October
1922 | Hart Court | HART_S001 | H21 | Scheme | 2022-10-25 16:13 | FRA_1922251020221442.pdf | ComleyB | 1922251020221440 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 60guriox2idl9ob2zga | Low Risk closed | Risk Closed | 44861.6861 | Obs15 | Management Of Fire Safety | 45590 | Low | Court Manager | Fire Risk Management information to be printed and placed in fire safety management folder. | printed and placed in fire folder
1922 | Hart Court | HART_S001 | H21 | Scheme | 2022-10-25 16:13 | FRA_1922251020221442.pdf | ComleyB | 1922251020221440 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | f9djuaqldlil9obkple | Low Risk closed | Risk Closed | 44861.685 | Obs4 | The Occupant - Information Provided By The Court Manager | 45590 | Low | Court Manager | Resident fire box information sheet to be updated. | updated today, due to completing the PCFRA for all residents
1922 | Hart Court | HART_S001 | H21 | Scheme | 2022-10-25 16:13 | FRA_1922251020221442.pdf | ComleyB | 1922251020221440 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 9oam338omll9oayjdq | Low Risk closed | Risk Closed | 44861.6854 | Obs15 | Management Of Fire Safety | 45590 | Low | Court Manager | Fire Safety training records to be updated | updated
1922 | Hart Court | HART_S001 | H21 | Scheme | 2022-10-25 16:13 | FRA_1922251020221442.pdf | ComleyB | 1922251020221440 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 91c7aao5v5tl9obgqry | Low Risk closed | Risk Closed | 44861.4659 | Obs8 | Measures To Limit Fire Spread And Development | 45590 | Low | Court Manager | Decoration to be removed from fire door and communal corridor to be kept sterile. | Halloween Decoration removed by myself today
1922 | Hart Court | HART_S001 | H21 | Scheme | 2022-10-25 16:13 | FRA_1922251020221442.pdf | ComleyB | 1922251020221440 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | y8185fzsykkl9oc85zz | Low Risk closed | Risk Closed | 44861.6839 | Obs8 | Measures To Limit Fire Spread And Development | 45590 | Low | Court Manager | Flat 19 front door catching in door bell cable. Cable to be removed and pentration fire stopped. | REPAIR RAISED WILL BE COMPLETED ON MONDAY
1923 | Ironside Court | IRONSIDE_S001 | H21 | Scheme | 2022-05-13 13:02 | FRA_1923130520221027.pdf | ComleyB | 1923130520221020 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | bj0hjk5ubthl34ctyom | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45425 | Low | Court Manager | Flat 25 door not fully closing. Door to be eased and adjusted | NULL
1923 | Ironside Court | IRONSIDE_S001 | H21 | Scheme | 2022-05-13 13:02 | FRA_1923130520221027.pdf | ComleyB | 1923130520221020 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | f65q11qgzfjl34d0s05 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45425 | Low | Court Manager | Flat 29 door to have draught exclusion brushes raised or removed to allow automatic closing | NULL
1923 | Ironside Court | IRONSIDE_S001 | H21 | Scheme | 2022-05-13 13:02 | FRA_1923130520221027.pdf | ComleyB | 1923130520221020 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | dc3yllrlsacl34ci9ni | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45425 | Low | Court Manager | Flat 12 front door not adequately closing. Door to be eased and adjusted. | NULL
1923 | Ironside Court | IRONSIDE_S001 | H21 | Scheme | 2022-05-13 13:02 | FRA_1923130520221027.pdf | ComleyB | 1923130520221020 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 3y8q3sp84erl349s7u2 | Low Risk to be actioned | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | 45425 | Low | Court Manager | Person-centred fire risk assessments to be reviewed and updated. | NULL
1923 | Ironside Court | IRONSIDE_S001 | H21 | Scheme | 2022-05-13 13:02 | FRA_1923130520221027.pdf | ComleyB | 1923130520221020 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 3u6dx7k19g7l34b9971 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45425 | Low | Court Manager | Door to office requires strips and seals | NULL
1923 | Ironside Court | IRONSIDE_S001 | H21 | Scheme | 2022-05-13 13:02 | FRA_1923130520221027.pdf | ComleyB | 1923130520221020 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 1zlxpf5mcq4l34d97ro | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45425 | Low | Court Manager | Flat 37 not fully closing, carpet underlay to be removed from hallway | NULL
1923 | Ironside Court | IRONSIDE_S001 | H21 | Scheme | 2022-05-13 13:02 | FRA_1923130520221027.pdf | ComleyB | 1923130520221020 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 0gcbuv4yj2ttl34bsot9 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45425 | Low | Court Manager | Compartment doors outside office to be replaced. | NULL
1923 | Ironside Court | IRONSIDE_S001 | H21 | Scheme | 2022-05-13 13:02 | FRA_1923130520221027.pdf | ComleyB | 1923130520221020 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 05tx6m6ywnkkl34dt7gz | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45425 | Low | Court Manager | Flat 41 door has been trimmed and large threshold inserted. Door now non-compliant and requires replacing, threshold to be removed. | NULL
1923 | Ironside Court | IRONSIDE_S001 | H21 | Scheme | 2022-05-13 13:02 | FRA_1923130520221027.pdf | ComleyB | 1923130520221020 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | tlqugsz3isl34djwca | Low Risk to be actioned | Risk Open | NULL | Obs13 | Other Relevant Fixed Systems | 45425 | Low | Court Manager | Additional restrictor to be installed to AOVs to prevent window dropping out or new opener to be installed to secure window to frame | NULL
1923 | Ironside Court | IRONSIDE_S001 | H21 | Scheme | 2022-05-13 13:02 | FRA_1923130520221027.pdf | ComleyB | 1923130520221020 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | sgnt5cyqq4ql34amcyl | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45059 | Medium | Court Manager | Bare cables to be terminated and put back into switch box | NULL
1923 | Ironside Court | IRONSIDE_S001 | H21 | Scheme | 2022-05-13 13:02 | FRA_1923130520221027.pdf | ComleyB | 1923130520221020 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | o9erfh5tncpl34ajsaq | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45425 | Low | Court Manager | Reduce use of extension leads and use mains plug sockets in office | NULL
1923 | Ironside Court | IRONSIDE_S001 | H21 | Scheme | 2022-05-13 13:02 | FRA_1923130520221027.pdf | ComleyB | 1923130520221020 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | nnv9r21jstil34e16cs | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45425 | Low | Surveyor | Additional fire exit signs and fire action notices required. | NULL
1923 | Ironside Court | IRONSIDE_S001 | H21 | Scheme | 2022-05-13 13:02 | FRA_1923130520221027.pdf | ComleyB | 1923130520221020 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | gcy2wuppf0jl34dao6r | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45425 | Low | Court Manager | Flay 38 door has been trimmed too much. Drop plate be installed to bottom of door | NULL
1923 | Ironside Court | IRONSIDE_S001 | H21 | Scheme | 2022-05-13 13:02 | FRA_1923130520221027.pdf | ComleyB | 1923130520221020 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | fy2zqd3coajl34bxlk2 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45425 | Low | Court Manager | Compartment door to rear lobby to be eased and adjusted | NULL
1923 | Ironside Court | IRONSIDE_S001 | H21 | Scheme | 2022-05-13 13:02 | FRA_1923130520221027.pdf | ComleyB | 1923130520221020 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | i0ojs07ystbl34ahlmz | Observation Only | Risk Open | NULL | Obs16 | Testing And Maintenance | NULL | N/A | Other | Compliance checks stored on PEBBLES and ERICA. | NULL
1924 | Pegasus Court | PEGASUS_S001 | H21 | Scheme | 2022-06-14 12:39 | FRA_1924140620221037.pdf | GerrishR | 1924140620221030 | Retirement Housing | Mid South | Berks and Hampshire North | South | South Patch 4 | hg094ohvxnql4e2lh5r | Medium Risk closed | Risk Closed | 44726.6371 | Obs6 | Fire Hazards - Elimination & Control | 45091 | Medium | Court Manager | Remove excess material from boiler room | removed the items and put them into a store cupboard
1924 | Pegasus Court | PEGASUS_S001 | H21 | Scheme | 2022-06-14 12:39 | FRA_1924140620221037.pdf | GerrishR | 1924140620221030 | Retirement Housing | Mid South | Berks and Hampshire North | South | South Patch 4 | k692wok6tbhl4e2h7xl | Medium Risk closed | Risk Closed | 44728.4311 | Obs6 | Fire Hazards - Elimination & Control | 45091 | Medium | Court Manager | Fill hole near around light using correct fire rated material in electric cupboard | Con6tractor filled hole with fire rated material
1924 | Pegasus Court | PEGASUS_S001 | H21 | Scheme | 2022-06-14 12:39 | FRA_1924140620221037.pdf | GerrishR | 1924140620221030 | Retirement Housing | Mid South | Berks and Hampshire North | South | South Patch 4 | wzsl9otxnqhl4e2f93e | Medium Risk closed | Risk Closed | 44727.5082 | Obs6 | Fire Hazards - Elimination & Control | 45091 | Medium | Court Manager | Remove chairs from electrical cupboard | tables and chairs removed and stored in store cupboard
1925 | Patrick Howard-Dobson Court | PATRICKHOWA_S001 | H21 | Scheme | 2022-02-04 17:35 | FRA_1925040220221436.pdf | ComleyB | 1925040220221430 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 4320p2dy81nkz8jobmm | Observation Only | Risk Open | NULL | Obs16 | Testing And Maintenance | NULL | N/A | Other | Compliance checks stored on PEBBLES and ERICA | NULL
1925 | Patrick Howard-Dobson Court | PATRICKHOWA_S001 | H21 | Scheme | 2022-02-04 17:35 | FRA_1925040220221436.pdf | ComleyB | 1925040220221430 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | cbl09npkytckz8jlmbx | Observation Only | Risk Open | NULL | Obs15 | Management Of Fire Safety | NULL | N/A | Other | False alarms recorded on ERICA. | NULL
1928 | Caroline Square | CAROLINESQUA_S001 | H21 | Scheme | 2022-03-02 13:58 | FRA_1928020320221221.pdf | ComleyB | 1928020320221220 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | du9i1enj7qml09kthgl | Low Risk closed | Risk Closed | 44630.4263 | Obs15 | Management Of Fire Safety | 45353 | Low | Court Manager | Fire Safety training records for care staff to be updated in fire safety management folder | CARE STAFF TRAINING RECORD ADDED TO FIRE SAFETY MANAGEMENT FOLDER
1928 | Caroline Square | CAROLINESQUA_S001 | H21 | Scheme | 2022-03-02 13:58 | FRA_1928020320221221.pdf | ComleyB | 1928020320221220 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | 7ys7ogggz73l09l25p2 | Observation Only | Risk Open | NULL | Obs16 | Testing And Maintenance | NULL | N/A | Other | Compliance checks stored on PEBBLES | NULL
1928 | Caroline Square | CAROLINESQUA_S001 | H21 | Scheme | 2022-03-02 13:58 | FRA_1928020320221221.pdf | ComleyB | 1928020320221220 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | h33hm7n5yr9l09k2kkf | Low Risk closed | Risk Closed | 44636.5282 | Obs11 | Fire Fighting Equipment | 45353 | Low | Court Manager | Unit to be moved to one side to allow access to fire extinguisher. | UNIT HAS BEEN MOVED TO ONE SIDE TO ALLOW ACCESS TO EXTINGUISHER
1928 | Caroline Square | CAROLINESQUA_S001 | H21 | Scheme | 2022-03-02 13:58 | FRA_1928020320221221.pdf | ComleyB | 1928020320221220 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | nc1uhnroivl09m2ttr | Low Risk closed | Risk Closed | 44636.5286 | Obs8 | Measures To Limit Fire Spread And Development | 45353 | Low | Court Manager | Flat 10 door to have intrumescent strips and seals fitted | HAVE RAISED A WORKS ORDER TO COMPLETE ACTION
1928 | Caroline Square | CAROLINESQUA_S001 | H21 | Scheme | 2022-03-02 13:58 | FRA_1928020320221221.pdf | ComleyB | 1928020320221220 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | u48rie71cf7l09lhs9k | Medium Risk closed | Risk Closed | 44630.423 | Obs6 | Fire Hazards - Elimination & Control | 44987 | Medium | Court Manager | Breaches of smoking. Smoking point to be away from the building. Cigarette ends found in flower beds and wood chips. | DISCUSSED WITH CARE MANAGER AND CARE TEAM TO REMIND THEM OF THE COURT POLICY
1928 | Caroline Square | CAROLINESQUA_S001 | H21 | Scheme | 2022-03-02 13:58 | FRA_1928020320221221.pdf | ComleyB | 1928020320221220 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | tw9jcv97m2l09jxay1 | Low Risk closed | Risk Closed | 44644.6308 | Obs6 | Fire Hazards - Elimination & Control | 45353 | Low | Court Manager | Remove extension plugs and install 3 or 4 additional sockets. | 4 extra plug sockets were fitted in the managers office
1928 | Caroline Square | CAROLINESQUA_S001 | H21 | Scheme | 2022-03-02 13:58 | FRA_1928020320221221.pdf | ComleyB | 1928020320221220 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | xwa2mf6bpdl09l0muf | Low Risk closed | Risk Closed | 44637.6377 | Obs15 | Management Of Fire Safety | 45353 | Low | Court Manager | False alarms and activations to be recorded on ERICA | ENTERED FALSE ALARM ACTIVATED BY FLAT 7 ONTO ERICA, NO FURTHER ACTION REQUIRED
1928 | Caroline Square | CAROLINESQUA_S001 | H21 | Scheme | 2022-03-02 13:58 | FRA_1928020320221221.pdf | ComleyB | 1928020320221220 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | w9ty6frlhbil09kquiy | Low Risk closed | Risk Closed | 44630.4224 | Obs15 | Management Of Fire Safety | 45353 | Low | Court Manager | Fire Safety training record sheet to updated in fire safety management folder | STAFF TRAINING RECORD SHEET ADDED INTO FIRE FOLDER
1928 | Caroline Square | CAROLINESQUA_S001 | H21 | Scheme | 2022-03-02 13:58 | FRA_1928020320221221.pdf | ComleyB | 1928020320221220 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | zn92gtczqkl09lkbik | Low Risk closed | Risk Closed | 44630.4218 | Obs6 | Fire Hazards - Elimination & Control | 45353 | Low | Court Manager | Lighter found in flower bed | LIGHTER REMOVED FROM FLOWER BED, DISCUSSED AT RESIDENTS MEETING AND WITH CARE TEAM TO REMIND THEM TO DISPOSE OF LIGHTERS SAFETY
1928 | Caroline Square | CAROLINESQUA_S001 | H21 | Scheme | 2022-03-02 13:58 | FRA_1928020320221221.pdf | ComleyB | 1928020320221220 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | zvyvwwb1xo9l09lc08r | Low Risk closed | Risk Closed | 44636.5295 | Obs6 | Fire Hazards - Elimination & Control | 45353 | Low | Court Manager | Door mats to be removed due to trip hazard and flammable gel removed from corridors | ACTION DISCUSSED AT RESIDENTS MEETING AND NOW DOOR MATS REMOVED AND HAND GEL REMOVED FROM SHELVES OUTSIDE THE FLATS
1929 | Maritime House | MARITIMEHOUS_S001 | H21 | Scheme | 2022-07-22 10:16 | FRA_1929210720221901.pdf | ComleyB | 1929210720221900 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | ytv79fe07pml5vcb7sb | Low Risk closed | Risk Closed | 44768.4558 | Obs15 | Management Of Fire Safety | 45494 | Low | Court Manager | Employee Fire Safety training records sheet to be updated. | All fire training is recorded on a separate sheet at the front of the fire folder, fully up to date.
1929 | Maritime House | MARITIMEHOUS_S001 | H21 | Scheme | 2022-07-22 10:16 | FRA_1929210720221901.pdf | ComleyB | 1929210720221900 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | xsnpq9hnqgl5vcb7mz | Low Risk closed | Risk Closed | 44785.6217 | Obs9 | Escape Lighting | 45494 | Low | Court Manager | EML by flat 16 to be cleaned | Handyman completed on 10/08
1929 | Maritime House | MARITIMEHOUS_S001 | H21 | Scheme | 2022-07-22 10:16 | FRA_1929210720221901.pdf | ComleyB | 1929210720221900 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | smlb9ebtr2gl5vcb7ii | Low Risk closed | Risk Closed | 44771.4244 | Obs8 | Measures To Limit Fire Spread And Development | 45494 | Low | Court Manager | Flat 11, large amounts or foliage, cluster and door mat to be removed from communal door. | A letter was sent to Mrs Kinder requesting that she now take all of this down as discussed with the surveyor and she promptly did.
1929 | Maritime House | MARITIMEHOUS_S001 | H21 | Scheme | 2022-07-22 10:16 | FRA_1929210720221901.pdf | ComleyB | 1929210720221900 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | ox6typbofell5vcb7j7 | Low Risk closed | Risk Closed | 44785.6217 | Obs8 | Measures To Limit Fire Spread And Development | 45494 | Low | Court Manager | Flat 17 smoke seals to be replaced | Handyman completed on 10/08
1929 | Maritime House | MARITIMEHOUS_S001 | H21 | Scheme | 2022-07-22 10:16 | FRA_1929210720221901.pdf | ComleyB | 1929210720221900 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | p1glxr8gpyl5vcb7gj | Low Risk closed | Risk Closed | 44785.6224 | Obs8 | Measures To Limit Fire Spread And Development | 45494 | Low | Court Manager | Flat 3 front door smoke seal is broken and requires replacing | Handyman completed on 10/08
1929 | Maritime House | MARITIMEHOUS_S001 | H21 | Scheme | 2022-07-22 10:16 | FRA_1929210720221901.pdf | ComleyB | 1929210720221900 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | ipbq2ghxrml5vcb7jx | Low Risk closed | Risk Closed | 44771.4258 | Obs8 | Measures To Limit Fire Spread And Development | 45494 | Low | Court Manager | Door mats to be removed from communal corridors | Letters sent to the 11 flats that had these outside, asking for them to be removed. All mats have now been removed.
1929 | Maritime House | MARITIMEHOUS_S001 | H21 | Scheme | 2022-07-22 10:16 | FRA_1929210720221901.pdf | ComleyB | 1929210720221900 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | n3e5p2lxxpl5vcb7h5 | Low Risk closed | Risk Closed | 44785.6213 | Obs8 | Measures To Limit Fire Spread And Development | 45494 | Low | Court Manager | Flat 9 smoke seal to be replaced | Handyman completed on 10th Aug
1929 | Maritime House | MARITIMEHOUS_S001 | H21 | Scheme | 2022-07-22 10:16 | FRA_1929210720221901.pdf | ComleyB | 1929210720221900 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | n0ygsyl0ohll5vcb7oe | Observation Only | Risk Open | NULL | Obs14 | Access By Emergency Services | NULL | N/A | Other | Fire assembly point located in main car park. | NULL
1929 | Maritime House | MARITIMEHOUS_S001 | H21 | Scheme | 2022-07-22 10:16 | FRA_1929210720221901.pdf | ComleyB | 1929210720221900 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | lawzch06xll5vcb7ht | Low Risk closed | Risk Closed | 44785.6215 | Obs8 | Measures To Limit Fire Spread And Development | 45494 | Low | Court Manager | Flat 10 smoke seals to be replaced | Handyman completed on 10/08
1929 | Maritime House | MARITIMEHOUS_S001 | H21 | Scheme | 2022-07-22 10:16 | FRA_1929210720221901.pdf | ComleyB | 1929210720221900 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | 95qsmwig0uwl5vcb7fm | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45494 | Low | Court Manager | Flat 1, 5, hinges to be cleaned and cleared of debris | NULL
1929 | Maritime House | MARITIMEHOUS_S001 | H21 | Scheme | 2022-07-22 10:16 | FRA_1929210720221901.pdf | ComleyB | 1929210720221900 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | aum7vyu5lll5vcb7kn | Low Risk closed | Risk Closed | 44785.6225 | Obs8 | Measures To Limit Fire Spread And Development | 45494 | Low | Court Manager | Flat 19 smoke seals to be replaced | Handyman completed on 10/08
1929 | Maritime House | MARITIMEHOUS_S001 | H21 | Scheme | 2022-07-22 10:16 | FRA_1929210720221901.pdf | ComleyB | 1929210720221900 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | 4mn8h21tdftl5vcb7lb | Low Risk closed | Risk Closed | 44768.4538 | Obs8 | Measures To Limit Fire Spread And Development | 45494 | Low | Court Manager | Flat 21 Mobilty Scooter stored tight behind door preventing access | Spoke with the resident and reminded him that the scooter must never be left behind the door. We moved this to a safe place, he understood. I also asked the care team to make me aware if they notice this happens again.
1929 | Maritime House | MARITIMEHOUS_S001 | H21 | Scheme | 2022-07-22 10:16 | FRA_1929210720221901.pdf | ComleyB | 1929210720221900 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | 60j43ncd1k9l5vcb7po | Low Risk closed | Risk Closed | 44810.421 | Obs15 | Management Of Fire Safety | 45494 | Low | Court Manager | CarelineUK - scheme information sheet to be updated. Located in court fire plan. | Updated form with my details
1929 | Maritime House | MARITIMEHOUS_S001 | H21 | Scheme | 2022-07-22 10:16 | FRA_1929210720221901.pdf | ComleyB | 1929210720221900 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | 2ew1p30owql5vcb7re | Low Risk closed | Risk Closed | 44810.4212 | Obs15 | Management Of Fire Safety | 45494 | Low | Court Manager | Automatic Fire Detection and alarm system contractor information sheet to be updated. | Updated form
1929 | Maritime House | MARITIMEHOUS_S001 | H21 | Scheme | 2022-07-22 10:16 | FRA_1929210720221901.pdf | ComleyB | 1929210720221900 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | 1vvsaddf81kl5vcb7qi | Low Risk closed | Risk Closed | 44810.4216 | Obs15 | Management Of Fire Safety | 45494 | Low | Court Manager | Fire Safety Responsibilities matrix to be completed and placed in fire safety management folder. | Updated form
1929 | Maritime House | MARITIMEHOUS_S001 | H21 | Scheme | 2022-07-22 10:16 | FRA_1929210720221901.pdf | ComleyB | 1929210720221900 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | 3am88iovp8kl5vcb7cu | Low Risk closed | Risk Closed | 44771.425 | Obs6 | Fire Hazards - Elimination & Control | 45494 | Low | Court Manager | Nurse aprons and gloves to be removed from communal corridors. | Cleaners always remove these on shift, plus email sent to care manager, asking them not to leave.
1929 | Maritime House | MARITIMEHOUS_S001 | H21 | Scheme | 2022-07-22 10:16 | FRA_1929210720221901.pdf | ComleyB | 1929210720221900 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | 3a15nnu3a89l5vcb7ek | Medium Risk Overdue | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44768 | Medium | Surveyor | CLC have undertaken a full bolster survey of the compartmentation. The report has identified a number issues with fire stopping installation and suitability. The concern has been raised as a Latent defect. A number of issues have been rectified but still outstanding issues present. | NULL
1932 | Summergate Lodge | SUMMERGATELODGE_S001 | H21 | Scheme | 2022-09-27 14:29 | FRA_1932270920221237.pdf | ComleyB | 1932270920221230 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 7gz4rabcf4l8k7cwo7 | Low Risk closed | Risk Closed | 44834.3623 | Obs5 | Evacuation Strategy And Training | 45562 | Low | Court Manager | Floor plans of each floor to be placed in red fire box, floor plans must indicate gas & electric shut off points, fire exits and dry risers. | extra floor plans have been copied adding dry riser and fire exit locations
1932 | Summergate Lodge | SUMMERGATELODGE_S001 | H21 | Scheme | 2022-09-27 14:29 | FRA_1932270920221237.pdf | ComleyB | 1932270920221230 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 7jh04ctiqxbl8k771oy | Low Risk closed | Risk Closed | 44832.4461 | Obs5 | Evacuation Strategy And Training | 45562 | Low | Court Manager | Resident information sheet requires updating. | Resident information sheet updated 27.09.2022, replaced in red box
1932 | Summergate Lodge | SUMMERGATELODGE_S001 | H21 | Scheme | 2022-09-27 14:29 | FRA_1932270920221237.pdf | ComleyB | 1932270920221230 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 8hh8ufq6xh8l8k7tq4m | Low Risk closed | Risk Closed | 44832.4478 | Obs6 | Fire Hazards - Elimination & Control | 45562 | Low | Court Manager | Electrical air fresheners to be removed from communal corridors. | Air freshers removed
1932 | Summergate Lodge | SUMMERGATELODGE_S001 | H21 | Scheme | 2022-09-27 14:29 | FRA_1932270920221237.pdf | ComleyB | 1932270920221230 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | drtmdimlpikl8k5x27i | Low Risk closed | Risk Closed | 44868.6314 | Obs15 | Management Of Fire Safety | 45562 | Low | Court Manager | False alarm activations to be recorded on ERICA. | one missing report up loaded
1932 | Summergate Lodge | SUMMERGATELODGE_S001 | H21 | Scheme | 2022-09-27 14:29 | FRA_1932270920221237.pdf | ComleyB | 1932270920221230 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | dnx1y5zxcpil8k5ohqo | Low Risk closed | Risk Closed | 44832.4441 | Obs15 | Management Of Fire Safety | 45562 | Low | Court Manager | Fire Safety training records to be updated. Record sheet and certificate to be placed in fire safety management folder. | Completed certificate has now printed off from Fred
1932 | Summergate Lodge | SUMMERGATELODGE_S001 | H21 | Scheme | 2022-09-27 14:29 | FRA_1932270920221237.pdf | ComleyB | 1932270920221230 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | d03xq3i8nsdl8k7nimn | Low Risk closed | Risk Closed | 44833.7069 | Obs7 | Fire Protection Measures | 45562 | Low | Court Manager | Fire exit door not holding open and closing back on itself. Catch to be adjusted. | Handy man came out today and made a small adjustment, all working ok
1932 | Summergate Lodge | SUMMERGATELODGE_S001 | H21 | Scheme | 2022-09-27 14:29 | FRA_1932270920221237.pdf | ComleyB | 1932270920221230 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | d4gmhtwc2el8k7io7b | Low Risk closed | Risk Closed | 44863.5922 | Obs6 | Fire Hazards - Elimination & Control | 45562 | Low | Court Manager | Mobility scooters and chargers to be PAT tested. | 1x false fire alarm add to Erica back dated to 02/03/2022 reference 58637
1932 | Summergate Lodge | SUMMERGATELODGE_S001 | H21 | Scheme | 2022-09-27 14:29 | FRA_1932270920221237.pdf | ComleyB | 1932270920221230 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | n052xz447ul8k8bfx9 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45562 | Low | Surveyor | Outstanding concern surrounding Fire stopping of building. Independent specialist to investigate. | NULL
1932 | Summergate Lodge | SUMMERGATELODGE_S001 | H21 | Scheme | 2022-09-27 14:29 | FRA_1932270920221237.pdf | ComleyB | 1932270920221230 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | o07wzefct08l8k6218x | Low Risk closed | Risk Closed | 44833.7001 | Obs15 | Management Of Fire Safety | 45562 | Low | Court Manager | Training to be provided to court manager for maintaing fire safety management folder and to ensure all information is stored correctly. | Visit made to Reginald Mitchell court to look at fire management safety folders. all completed
1932 | Summergate Lodge | SUMMERGATELODGE_S001 | H21 | Scheme | 2022-09-27 14:29 | FRA_1932270920221237.pdf | ComleyB | 1932270920221230 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | rkhnmmrd1al8k81chx | Low Risk closed | Risk Closed | 44833.7011 | Obs8 | Measures To Limit Fire Spread And Development | 45562 | Low | Court Manager | First floor cross corridor door not fully closing. Door requires ease and adjusting. | Handy man on site today and has made adjustments to the doors, all working well.
1932 | Summergate Lodge | SUMMERGATELODGE_S001 | H21 | Scheme | 2022-09-27 14:29 | FRA_1932270920221237.pdf | ComleyB | 1932270920221230 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | v43yf1xmvi8l8k5bhfi | Low Risk closed | Risk Closed | 44863.5864 | Obs6 | Fire Hazards - Elimination & Control | 45562 | Low | Court Manager | All electrical appliances/equipment to be PAT tested. | Asset managing have said Summergate is not due until next year.
2001 | Viscount Cobham Court | VISCOUNTCOBH_S001 | H21 | Scheme | 2022-10-19 23:38 | FRA_2001181020221519.pdf | HallS | 2001181020221510 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 1 | s2u6e4fegbsl9g71noo | Low Risk closed | Risk Closed | 44859.3717 | Obs6 | Fire Hazards - Elimination & Control | 45584 | Low | Court Manager | Electrical waste equipment left in bin store. The court manager is to advise residents on the importance of safe disposal of electrical waste items. Bulky waste collection can be arranged by the local council or disposal at an appropriate recycling centre. | Items removed, paragraph in November 22 newsletter
2001 | Viscount Cobham Court | VISCOUNTCOBH_S001 | H21 | Scheme | 2022-10-19 23:38 | FRA_2001181020221519.pdf | HallS | 2001181020221510 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 1 | 5i7zsudlfxl9g6pm8e | Low Risk closed | Risk Closed | 44859.3565 | Obs6 | Fire Hazards - Elimination & Control | 45584 | Low | Court Manager | Flammable air freshener have been sited within the communal blocks. Immediate removal has been advised along with a reminder to the building occupants of the importance of fire safety within the next court newsletter. | I have spoken to the residents, removed the offending air fresheners and highlighted this in the newsletter for November 22
2001 | Viscount Cobham Court | VISCOUNTCOBH_S001 | H21 | Scheme | 2022-10-19 23:38 | FRA_2001181020221519.pdf | HallS | 2001181020221510 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 1 | 31pvghat4sil9g7hey0 | Observation Only | Risk Closed | 44858.595 | Obs1 | The Building | NULL | N/A | Court Manager | Viscount Cobham Court operates an open roof void design above all first floor dwellings to the category 2 scheme. Roof void detection has been installed and linked to each of the 1st floor dwellings below as a precautionary measure to provide early warning. Should there be an activation of a detector within the roof void, the 1st floor flats directly below will receive an alert tone to evacuate. This is an advisory note only. | Advisory only
2001 | Viscount Cobham Court | VISCOUNTCOBH_S001 | H21 | Scheme | 2022-10-19 23:38 | FRA_2001181020221519.pdf | HallS | 2001181020221510 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 1 | 0rqcqh43vhnl9g7909w | Low Risk closed | Risk Closed | 44859.3688 | Obs10 | Fire Safety And Notices | 45584 | Low | Court Manager | Fire safety signage required to passenger lift to notify building occupants not to use the lift in the event of a fire. | Sourced sign and posted by lift call button
2002 | Roland Rutter Court | ROLANDRUTT_S001 | H21 | Scheme | 2022-10-26 16:43 | FRA_2002261020221249.pdf | HallS | 2002261020221240 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 1 | sr0rbnww0eml9pksz90 | Observation Only | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | M&E Team | I would recommend the installation of B.S. 5839 Part 6 devices linked to the warden call system when the scheme receives a fire alarm upgrade. This comment is advisory only. | NULL
2006 | Wood Court | WOOD_S001 | H21 | Scheme | 2022-04-29 15:20 | FRA_2006290420221217.pdf | HallS | 2006290420221210 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 4 | wa1o7ub0j6el2kdwuz9 | Observation Only | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | M&E Team | There are no Pt 6 mains powered devices linked to warden call system installed on court. I recommend installation during the next scheduled fire alarm upgrade. This is an advisory note only. | NULL
2008 | Kyrle Pope Court | KYRLEPOPE_S001 | H21 | Scheme | 2022-01-26 08:39 | FRA_2008250120220730.pdf | HallS | 2008250120220730 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 1 | gzbcnetv4uokytzjzo7 | Observation Only | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | M&E Team | There is no part 6 detection installed within the residents properties. I would therefore recommend that part 6 devices linked to warden call system are installed when the fire alarm system is upgraded. This is an advisory note only. | NULL
2009 | Dennis Potter Court | DENNISPOTT_S001 | H21 | Scheme | 2022-10-20 23:26 | FRA_2009201020222257.pdf | HallS | 2009201020222250 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 4 | 04uj0r1zomlil9hlsu50 | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45224 | Low | Court Manager | There are several trailing leads located under the court managers desk. I recommend the installation of additional sockets within the office to accommodate the office equipment and eliminate the trailing leads. The court manager is to raise a works order for the addition of sockets to the office in the form of dado trunking. | NULL
2009 | Dennis Potter Court | DENNISPOTT_S001 | H21 | Scheme | 2022-10-20 23:26 | FRA_2009201020222257.pdf | HallS | 2009201020222250 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 4 | 3ph34syz3d8l9hm3a3p | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45585 | Low | Surveyor | Additional fire stopping required to service cupboard housing consumer unit within communal circulation area serving flats 19 and 19a. A works order has been raised in lieu of these works. | NULL
2009 | Dennis Potter Court | DENNISPOTT_S001 | H21 | Scheme | 2022-10-20 23:26 | FRA_2009201020222257.pdf | HallS | 2009201020222250 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 4 | fasu5q88f7ll9hlu370 | Medium Risk to be actioned | Risk Open | NULL | Obs1 | The Building | 45219 | Medium | Surveyor | Section of UPVC walling enclosing the office and communal escape route requires replacement with materials that provide 30 minutes of fire protection. Fire stopping contractors have priced this work for approval. | NULL
2015 | Crookbarrow View | CROOKBARROW_S001 | H21 | Scheme | 2022-10-28 15:27 | FRA_2015271020221415.pdf | HallS | 2015271020221410 | Extra Care | Extra Care Central | EC Central 1 | Central | Central Patch 4 | di99kttfo7rl9sl12pj | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45593 | Low | M&E Team | Lightning protection system has not been inspected since the scheme was opened. Recommendation for the M&E team to add this court to the cyclical service contract as there is no evidence of this court within the centrally held service folder. | NULL
2015 | Crookbarrow View | CROOKBARROW_S001 | H21 | Scheme | 2022-10-28 15:27 | FRA_2015271020221415.pdf | HallS | 2015271020221410 | Extra Care | Extra Care Central | EC Central 1 | Central | Central Patch 4 | 8otceavgbgl9r39kn1 | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45238 | Low | Other | The existing The existing fire safety signage is a mixture of B.S. and EN signage. To avoid confusion, all signs within a system of escape route signing should be of similar style, design, size and format. Refer to BS 5499-4:2013 Safety signs Code of practice for escape route signage. This has been raised via the defects system and passed back to the development contractor for actioning. See B.S. Sign. | NULL
2015 | Crookbarrow View | CROOKBARROW_S001 | H21 | Scheme | 2022-10-28 15:27 | FRA_2015271020221415.pdf | HallS | 2015271020221410 | Extra Care | Extra Care Central | EC Central 1 | Central | Central Patch 4 | 0lg7o7webgal9r39kkl | Medium Risk closed | Risk Closed | 44908.6284 | Obs7 | Fire Protection Measures | 44873 | Medium | Court Manager | Fire door Separating commercial kitchen from communal escape route is constantly wedged open by commercial kitchen staff. External commercial kitchen staff have been reminded of the importance of fire safety and the requirement for fire separation between high risk rooms / locations and adjacent escape routes. Staff are to provide evidence of fire safety training in line with their duties and responsibilities. | Door is no longer wedged open, a flyscreen has been delivered and will be fitted on 15.12.2022, the kitchen staff will then open the window for air ventilation into the kitchen.
2015 | Crookbarrow View | CROOKBARROW_S001 | H21 | Scheme | 2022-10-28 15:27 | FRA_2015271020221415.pdf | HallS | 2015271020221410 | Extra Care | Extra Care Central | EC Central 1 | Central | Central Patch 4 | 1r4p3hd2qu5l9r39kjk | Low Risk closed | Risk Closed | 44908.6289 | Obs6 | Fire Hazards - Elimination & Control | 45592 | Low | Court Manager | No evidence of PAT testing to scooters stored & charged within the communal scooter store. Assistant Housing manager has been advised to ensure that these are tested during the next scheduled service visit. | Scooters will be PAT tested when the scheme is PAT tested in May 2023, this has been agreed with Fiona Clarke and Jamie Lewis.
2015 | Crookbarrow View | CROOKBARROW_S001 | H21 | Scheme | 2022-10-28 15:27 | FRA_2015271020221415.pdf | HallS | 2015271020221410 | Extra Care | Extra Care Central | EC Central 1 | Central | Central Patch 4 | 71zlz3bz6j4l9r3bl7s | Medium Risk to be actioned | Risk Open | NULL | Obs16 | Testing And Maintenance | 45226 | Medium | M&E Team | Commercial Kitchen required deep clean to ducts etc. This court was not added to the service list. M&E team to have the scheme added immediately. | NULL
2015 | Crookbarrow View | CROOKBARROW_S001 | H21 | Scheme | 2022-10-28 15:27 | FRA_2015271020221415.pdf | HallS | 2015271020221410 | Extra Care | Extra Care Central | EC Central 1 | Central | Central Patch 4 | ucxfh6rk2fl9r39kip | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45226 | Medium | M&E Team | Commercial Kitchen required deep clean to ducts etc. This court was not added to the service list. M&E team to have the scheme added immediately. | NULL
2015 | Crookbarrow View | CROOKBARROW_S001 | H21 | Scheme | 2022-10-28 15:27 | FRA_2015271020221415.pdf | HallS | 2015271020221410 | Extra Care | Extra Care Central | EC Central 1 | Central | Central Patch 4 | r9s9i8dcc5rl9r39km3 | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45238 | Low | Other | The existing fire safety signage is a mixture of B.S. and EN signage. To avoid confusion, all signs within a system of escape route signing should be of similar style, design, size and format. Refer to BS 5499-4:2013 Safety signs Code of practice for escape route signage. This had been raised via the defects system and passed back to the development contractor for actioning. See EN sign. | NULL
2101 | Blackett Ord Court | BLACKETTORD_S001 | H21 | Scheme | 2022-07-13 16:20 | FRA_2101130720220859.pdf | colej | 2101130720220850 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 3 | ly16flvu8zl5jpzll5 | Observation Only | Risk Closed | 44778.751 | Obs7 | Fire Protection Measures | NULL | N/A | Other | Information only. For the duration of the construction works the existing fire panel has been rezoned to cover all of the affected wing so as to sound in all areas in the event of a fire. This will be reconfigured upon completion and in line with the Housing 21 policy. | n/a observation only
2101 | Blackett Ord Court | BLACKETTORD_S001 | H21 | Scheme | 2022-07-13 16:20 | FRA_2101130720220859.pdf | colej | 2101130720220850 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 3 | 35bsts57v6tl5jiy7i2 | Observation Only | Risk Closed | 44756.5079 | Obs14 | Access By Emergency Services | NULL | N/A | Court Manager | Information only. The assembly point is located in the front garden outside of the communal lounge fire exit. | Information only
2101 | Blackett Ord Court | BLACKETTORD_S001 | H21 | Scheme | 2022-07-13 16:20 | FRA_2101130720220859.pdf | colej | 2101130720220850 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 3 | 9q8e0aqmvw9l5jka2uo | Observation Only | Risk Closed | 44778.7509 | Obs7 | Fire Protection Measures | NULL | N/A | Other | Information only. The fire exit door for the flats affected by the staircase removal leading to the new build are temporarily out of use during construction. The remaining alternative exit has been discussed with the leading fire authority Cambrigeshire fire and rescue and has been deemed acceptable until completion of the new build. Completion is planned for the end of August 22 and is on track. There is a stay put policy in place for all properties with a delayed evacuation if required. In the event of an emergency the exit into the new build is possible but does lead into a building site. This would only be used in an absolute emergency situation at the point of a coordinated evacuation. The addition of an additional lobby as detail below has been also implemented. | n/a observation only
2101 | Blackett Ord Court | BLACKETTORD_S001 | H21 | Scheme | 2022-07-13 16:20 | FRA_2101130720220859.pdf | colej | 2101130720220850 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 3 | x7lqmkhk7cl5jpmzas | Observation Only | Risk Closed | 44778.7508 | Obs7 | Fire Protection Measures | NULL | N/A | Other | Comment only: Throughout the duration of the works an additional fire door and lobby area have been created between the laundry and stairs to provide additional compartmentation and place of relative safety. This will be removed upon completion of the new development and the area made good during the court makeover works. | n/a observation only
2102 | Chalmers Court | CHALMERS_S001 | H21 | Scheme | 2021-12-24 10:08 | FRA_2102241220210959.pdf | doerrd | 2102241220210950 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 1 | 8789d0dmqakxk82rgh | Observation Only | Risk Closed | 44567.3778 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Surveyor | All flat doors exit onto external escape routes | None required
2103 | Fuller Court | FULLER_S001 | H21 | Scheme | 2022-11-03 13:43 | FRA_2103031120220938.pdf | colej | 2103031120220930 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 3 | qi7vuh571wela101p91 | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45233 | Medium | M&E Team | It was noted at the time of inspection the AOVs require servicing as the gas struts and manual winders are sticking in some locations. | NULL
2110 | McGovern Court | MCGOVERN_S001 | H21 | Scheme | 2022-10-26 13:01 | FRA_2110261020221254.pdf | doerrd | 2110261020221250 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 1 | gbcao468zs7l9pkx6ny | Observation Only | Risk Closed | 44860.5451 | Obs1 | The Building | NULL | N/A | Surveyor | Compartmentation in the roof space of the lounge doesn't continue in the roof space. Due to the detection level and that there are no flats off of this area it is accepted that the risk has been mitigated. | None required
2110 | McGovern Court | MCGOVERN_S001 | H21 | Scheme | 2022-10-26 13:01 | FRA_2110261020221254.pdf | doerrd | 2110261020221250 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 1 | 5af2k7n0otil9pkx6rk | Low Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45591 | Low | Court Manager | The external stair well by flat 27 hasn't got fire action notices at the call points. Please order two, add the assembly point location and secure to the wall. | NULL
2110 | McGovern Court | MCGOVERN_S001 | H21 | Scheme | 2022-10-26 13:01 | FRA_2110261020221254.pdf | doerrd | 2110261020221250 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 1 | xr0428opu5fl9pkx6qm | Low Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45591 | Low | Court Manager | Fire action notices around the court have the assembly point location missing or isn't readable. Please re-write in permanent marker again. | NULL
2110 | McGovern Court | MCGOVERN_S001 | H21 | Scheme | 2022-10-26 13:01 | FRA_2110261020221254.pdf | doerrd | 2110261020221250 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 1 | vbgt8mzz3lml9pkx6p5 | Observation Only | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | There is no hot works permit system in place. | NULL
2117 | Temple Court | TEMPLE_S001 | H21 | Scheme | 2022-10-12 16:57 | FRA_2117121020221124.pdf | doerrd | 2117121020221120 | Retirement Housing | East Anglia | Essex and Hertfordshire | Central | Central Patch 1 | 88fc36krfzhl95t62bb | Observation Only | Risk Closed | 44847.6139 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Meter cupboard doors in the communal areas are metal however their ability to offer 30 mins protection is not guaranteed. | After confirming with Dean Doerr no further action is required.
2122 | Lea Springs | LEASPRINGS_S001 | H21 | Scheme | 2022-07-07 16:46 | FRA_2122070720221557.pdf | doerrd | 2122070720221550 | Extra Care | Extra Care South | EC South 2 | Central | Central Patch 1 | a3do9t13a7ql5b5whq4 | Medium Risk closed | Risk Closed | 44781.6777 | Obs14 | Access By Emergency Services | 45114 | Medium | Court Manager | Emergency access to keys and access to be needs to be resolved. There were no keys in the key safe that Careline can release remotely. This should house a master key and fob, the fire panel key and the fire box key. | This has been resolved. The aforementioned are in the key safe which is operated by Apello
2122 | Lea Springs | LEASPRINGS_S001 | H21 | Scheme | 2022-07-07 16:46 | FRA_2122070720221557.pdf | doerrd | 2122070720221550 | Extra Care | Extra Care South | EC South 2 | Central | Central Patch 1 | cwbz7qj11nnl5b5q8s6 | Low Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45114 | Low | Court Manager | Fire management folder needs to include maintenance details for the alarm, lights, FFE, AOV's etc. The certificates and details are online but the fire brigade need general information. | NULL
2122 | Lea Springs | LEASPRINGS_S001 | H21 | Scheme | 2022-07-07 16:46 | FRA_2122070720221557.pdf | doerrd | 2122070720221550 | Extra Care | Extra Care South | EC South 2 | Central | Central Patch 1 | cganfpvt2htl5b5ktms | Low Risk closed | Risk Closed | 44862.5372 | Obs8 | Measures To Limit Fire Spread And Development | 45480 | Low | Court Manager | AOV cover isn't secure / lock is broken. This could result in damage. | Jo Shelley has appointment booked with OpenView to change AOVs
2122 | Lea Springs | LEASPRINGS_S001 | H21 | Scheme | 2022-07-07 16:46 | FRA_2122070720221557.pdf | doerrd | 2122070720221550 | Extra Care | Extra Care South | EC South 2 | Central | Central Patch 1 | esf9ylyvy0vl5b5kar7 | Low Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45480 | Low | Court Manager | Fire box in front lobby should have a folder with important information for the fire brigade. There is the resident information but very little about the building and access arrangements. | NULL
2122 | Lea Springs | LEASPRINGS_S001 | H21 | Scheme | 2022-07-07 16:46 | FRA_2122070720221557.pdf | doerrd | 2122070720221550 | Extra Care | Extra Care South | EC South 2 | Central | Central Patch 1 | 7bsofml2q92l5b66eoc | Medium Risk closed | Risk Closed | 44781.682 | Obs8 | Measures To Limit Fire Spread And Development | 45114 | Medium | Court Manager | Hair Salon door doesn't close when released as the door fouls the floor. Door needs removing and adjusting to close fully. | MGS have been booked to remove and adjust the door so it can fully close
2122 | Lea Springs | LEASPRINGS_S001 | H21 | Scheme | 2022-07-07 16:46 | FRA_2122070720221557.pdf | doerrd | 2122070720221550 | Extra Care | Extra Care South | EC South 2 | Central | Central Patch 1 | 16wgw1r9n51l5b685g4 | Low Risk closed | Risk Closed | 44781.6826 | Obs8 | Measures To Limit Fire Spread And Development | 45480 | Low | Court Manager | Court managers office door closer and locks require adjustment as they do not close fully causing a fire spread risk. | MGS have been booked to attend to this job while fixing salon door
2122 | Lea Springs | LEASPRINGS_S001 | H21 | Scheme | 2022-07-07 16:46 | FRA_2122070720221557.pdf | doerrd | 2122070720221550 | Extra Care | Extra Care South | EC South 2 | Central | Central Patch 1 | 174yxqsxjhml5b6tp5k | Medium Risk closed | Risk Closed | 44859.8087 | Obs7 | Fire Protection Measures | 45114 | Medium | Surveyor | The emergency exits for the lounge need to be looked at to clarify distances and how doors are used. If the lounge doors to the rear garden are to be fire exits they need single action release, a fire call point and signage. Alternatively the fire exit sign to the rear lobby needs reinstating and the fob access to this escape route resolving maintaining security possibly with an emergency door release installation. | The door that is fob controlled was checked on a fire alarm test and it releases when the alarm sounds. This means that the fire exit can remain as it is and the runninģ man light can be reinstated. The patio doors serve as an additional exit not a specific fire exit.
2122 | Lea Springs | LEASPRINGS_S001 | H21 | Scheme | 2022-07-07 16:46 | FRA_2122070720221557.pdf | doerrd | 2122070720221550 | Extra Care | Extra Care South | EC South 2 | Central | Central Patch 1 | r1p87egoibl5b64o59 | Low Risk closed | Risk Closed | 44862.5355 | Obs8 | Measures To Limit Fire Spread And Development | 45480 | Low | Court Manager | 2nd floor cleaners cupboard door is missi g a section of intumescent strip and smoke seal. | Watford branch of CLC is being chased for several weeks. Last contact 21st and 28th October. They are the only company I am aware of who do this work for us.
2201 | Jellicoe Court | JELLICOE_S001 | H21 | Scheme | 2022-10-25 15:14 | FRA_2201251020221435.pdf | BrigdenN | 2201251020221430 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | e00forx2js7l9oaaj7z | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45590 | Low | Court Manager | Fire Action sign needed to break glass in laundry area. | NULL
2201 | Jellicoe Court | JELLICOE_S001 | H21 | Scheme | 2022-10-25 15:14 | FRA_2201251020221435.pdf | BrigdenN | 2201251020221430 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | xs3u814wf5ml9o9g8wy | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Other | Flat No's 1,4,7,8,9,10 & 27 classed as high risk. | NULL
2202 | Brough Court | BROUGH_S001 | H21 | Scheme | 2022-11-09 15:33 | FRA_2202091120221141.pdf | BrigdenN | 2202091120221140 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | agby7bs12brla9ruzgm | Medium Risk closed | Risk Closed | 44879.565 | Obs8 | Measures To Limit Fire Spread And Development | 45239 | Medium | Court Manager | Numerous flat doors have a large gap at the bottom of the door. Please arrange for these to be repaired urgently. | Raised WO with OpenView but have been told they do not fix this so cancelled and raised new WO with Dennis and Marwood WO 1575885.
2202 | Brough Court | BROUGH_S001 | H21 | Scheme | 2022-11-09 15:33 | FRA_2202091120221141.pdf | BrigdenN | 2202091120221140 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | apt1ddbikila9s229l | High Risk Closed | Risk Closed | 44879.5654 | Obs7 | Fire Protection Measures | 44601 | High | Court Manager | Fire door between corridor and scooter store has large gap at bottom to allow the escape of smoke and fire. | WO raised with Dennis and Marwood WO1575885.
2202 | Brough Court | BROUGH_S001 | H21 | Scheme | 2022-11-09 15:33 | FRA_2202091120221141.pdf | BrigdenN | 2202091120221140 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | hf6ftpz9ghlla9r9joj | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Other | Flat No's 2, 5, 23,25 are all high risk tenants | NULL
2203 | Meakin Court | MEAKIN_S001 | H21 | Scheme | 2022-09-01 12:17 | FRA_2203010920221109.pdf | BrigdenN | 2203010920221100 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | lg3wyln9qbl7iy0qfc | Low Risk closed | Risk Closed | 44859.3452 | Obs4 | The Occupant - Information Provided By The Court Manager | 45536 | Low | Court Manager | Individual person centred fire risk assessments need to be updated onto new form. | All PCFRA up to date
2203 | Meakin Court | MEAKIN_S001 | H21 | Scheme | 2022-09-01 12:17 | FRA_2203010920221109.pdf | BrigdenN | 2203010920221100 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | 35yoih34ygcl7ixy6rh | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Other | Flat no's 4,5,9 & 31 are classed as high risk tenants. | NULL
2204 | Singleton Court | SINGLETON_S001 | H21 | Scheme | 2022-10-05 16:05 | FRA_2204051020221513.pdf | BrigdenN | 2204051020221510 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | 3crp13zl1rrl8vpmiv5 | Medium Risk to be actioned | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | 45204 | Medium | M&E Team | Fire alarm showing faults on a regular basis | NULL
2204 | Singleton Court | SINGLETON_S001 | H21 | Scheme | 2022-10-05 16:05 | FRA_2204051020221513.pdf | BrigdenN | 2204051020221510 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | 3qqn2jec83vl8vqouym | Medium Risk closed | Risk Closed | 44844.5558 | Obs7 | Fire Protection Measures | 45204 | Medium | Court Manager | Communal fire door to lounge need intumescent strips refixing. | Raised works order now completed
2204 | Singleton Court | SINGLETON_S001 | H21 | Scheme | 2022-10-05 16:05 | FRA_2204051020221513.pdf | BrigdenN | 2204051020221510 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | 3qqn2jec83vl8vqouym | Medium Risk closed | Risk Closed | 44844.5582 | Obs7 | Fire Protection Measures | 45204 | Medium | Court Manager | Communal fire door to lounge need intumescent strips refixing. | W/O raised and completed
2204 | Singleton Court | SINGLETON_S001 | H21 | Scheme | 2022-10-05 16:05 | FRA_2204051020221513.pdf | BrigdenN | 2204051020221510 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | 196or36eqe1l8vpmiw2 | High Risk Closed | Risk Closed | 44861.6776 | Obs4 | The Occupant - Information Provided By The Court Manager | 44931 | High | Court Manager | Information on tenants in red fire box need updating | Produced updated information and placed in fire box 27.10.22
2204 | Singleton Court | SINGLETON_S001 | H21 | Scheme | 2022-10-05 16:05 | FRA_2204051020221513.pdf | BrigdenN | 2204051020221510 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | 196or36eqe1l8vpmiw2 | High Risk Closed | Risk Closed | 44861.6859 | Obs4 | The Occupant - Information Provided By The Court Manager | 44931 | High | Court Manager | Information on tenants in red fire box need updating | Updated 27.10.22
2204 | Singleton Court | SINGLETON_S001 | H21 | Scheme | 2022-10-05 16:05 | FRA_2204051020221513.pdf | BrigdenN | 2204051020221510 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | be1s9oi4h5cl8vq5egv | Medium Risk closed | Risk Closed | 44844.5442 | Obs6 | Fire Hazards - Elimination & Control | 44842 | Medium | Court Manager | All combustible items need to be cleared from cupboard under stairs that houses the electric meters. | Discussed one to one with residents and in the contents of the newsletter
2204 | Singleton Court | SINGLETON_S001 | H21 | Scheme | 2022-10-05 16:05 | FRA_2204051020221513.pdf | BrigdenN | 2204051020221510 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | be1s9oi4h5cl8vq5egv | Medium Risk closed | Risk Closed | 44844.5574 | Obs6 | Fire Hazards - Elimination & Control | 44842 | Medium | Court Manager | All combustible items need to be cleared from cupboard under stairs that houses the electric meters. | Actioned via news letter and items that re Rubbish requested to be disposed of and others stored in garage if no room in flats
2204 | Singleton Court | SINGLETON_S001 | H21 | Scheme | 2022-10-05 16:05 | FRA_2204051020221513.pdf | BrigdenN | 2204051020221510 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | skht47g9wtl8vpwu0q | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Other | Flat No's 1, 5, 8, 14, 17, 22, 24, 27, 30 are all high risk tenants. | NULL
2204 | Singleton Court | SINGLETON_S001 | H21 | Scheme | 2022-10-05 16:05 | FRA_2204051020221513.pdf | BrigdenN | 2204051020221510 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | tpwj642ujil8vqg0og | Medium Risk closed | Risk Closed | 44844.5562 | Obs6 | Fire Hazards - Elimination & Control | 45204 | Medium | Court Manager | All combustible items need to be cleared from communal electric meter cupboard. | Actioned via newsletter
2204 | Singleton Court | SINGLETON_S001 | H21 | Scheme | 2022-10-05 16:05 | FRA_2204051020221513.pdf | BrigdenN | 2204051020221510 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | tpwj642ujil8vqg0og | Medium Risk closed | Risk Closed | 44844.5551 | Obs6 | Fire Hazards - Elimination & Control | 45204 | Medium | Court Manager | All combustible items need to be cleared from communal electric meter cupboard. | Auctioned via newsletter
2204 | Singleton Court | SINGLETON_S001 | H21 | Scheme | 2022-10-05 16:05 | FRA_2204051020221513.pdf | BrigdenN | 2204051020221510 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | p8aglpxbd4hl8vqukv8 | Low Risk closed | Risk Closed | 44874.7 | Obs10 | Fire Safety And Notices | 45207 | Low | Court Manager | Fire Action Notice needed above break glass next to communal lounge. | TIS will replace as discussed
2204 | Singleton Court | SINGLETON_S001 | H21 | Scheme | 2022-10-05 16:05 | FRA_2204051020221513.pdf | BrigdenN | 2204051020221510 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | p8aglpxbd4hl8vqukv8 | Low Risk closed | Risk Closed | 44844.5473 | Obs10 | Fire Safety And Notices | 45207 | Low | Court Manager | Fire Action Notice needed above break glass next to communal lounge. | Emailed retirement living
2204 | Singleton Court | SINGLETON_S001 | H21 | Scheme | 2022-10-05 16:05 | FRA_2204051020221513.pdf | BrigdenN | 2204051020221510 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | nmasex1b7nel8vqncea | Medium Risk closed | Risk Closed | 44844.5565 | Obs7 | Fire Protection Measures | 44842 | Medium | Court Manager | Fire door to communal lounge is being wedged open. | Discussed with residents and removed door stopper
2204 | Singleton Court | SINGLETON_S001 | H21 | Scheme | 2022-10-05 16:05 | FRA_2204051020221513.pdf | BrigdenN | 2204051020221510 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | nmasex1b7nel8vqncea | Medium Risk closed | Risk Closed | 44844.5541 | Obs7 | Fire Protection Measures | 44842 | Medium | Court Manager | Fire door to communal lounge is being wedged open. | Discussed with residents
2204 | Singleton Court | SINGLETON_S001 | H21 | Scheme | 2022-10-05 16:05 | FRA_2204051020221513.pdf | BrigdenN | 2204051020221510 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | oif9oug40zbl8vpmix0 | High Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 44931 | High | M&E Team | Fire alarm seem to have persistent fault. | NULL
2204 | Singleton Court | SINGLETON_S001 | H21 | Scheme | 2022-10-05 16:05 | FRA_2204051020221513.pdf | BrigdenN | 2204051020221510 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | oif9oug40zbl8vpmix0 | High Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 44931 | High | M&E Team | Fire alarm seem to have persistent fault. | NULL
2204 | Singleton Court | SINGLETON_S001 | H21 | Scheme | 2022-10-05 16:05 | FRA_2204051020221513.pdf | BrigdenN | 2204051020221510 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | xmrzxxu24nl8vpmixj | Observation Only | Risk Open | NULL | Obs15 | Management Of Fire Safety | NULL | N/A | Other | Court manager has advised all checks are up to date. But this cannot be checked as all online. | NULL
2204 | Singleton Court | SINGLETON_S001 | H21 | Scheme | 2022-10-05 16:05 | FRA_2204051020221513.pdf | BrigdenN | 2204051020221510 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | xmrzxxu24nl8vpmixj | Observation Only | Risk Open | NULL | Obs15 | Management Of Fire Safety | NULL | N/A | Other | Court manager has advised all checks are up to date. But this cannot be checked as all online. | NULL
2204 | Singleton Court | SINGLETON_S001 | H21 | Scheme | 2022-10-05 16:05 | FRA_2204051020221513.pdf | BrigdenN | 2204051020221510 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | w7zkils9dfdl8vqe76u | Medium Risk closed | Risk Closed | 44844.5579 | Obs6 | Fire Hazards - Elimination & Control | 44842 | Medium | Court Manager | All items need to be cleared from fire escape route | Scooter has been collected by a charity with negotiation from flat 22
2204 | Singleton Court | SINGLETON_S001 | H21 | Scheme | 2022-10-05 16:05 | FRA_2204051020221513.pdf | BrigdenN | 2204051020221510 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | w7zkils9dfdl8vqe76u | Medium Risk closed | Risk Closed | 44845.6813 | Obs6 | Fire Hazards - Elimination & Control | 44842 | Medium | Court Manager | All items need to be cleared from fire escape route | Scooters now been removed
2204 | Singleton Court | SINGLETON_S001 | H21 | Scheme | 2022-10-05 16:05 | FRA_2204051020221513.pdf | BrigdenN | 2204051020221510 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | wntfub5l6il8vq923n | Medium Risk closed | Risk Closed | 44844.5545 | Obs6 | Fire Hazards - Elimination & Control | 44842 | Medium | Court Manager | All cupboards/Chairs combustible materials need to be cleared from stairwell areas. | Auctioned via newsletter
2204 | Singleton Court | SINGLETON_S001 | H21 | Scheme | 2022-10-05 16:05 | FRA_2204051020221513.pdf | BrigdenN | 2204051020221510 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | wntfub5l6il8vq923n | Medium Risk closed | Risk Closed | 44844.5548 | Obs6 | Fire Hazards - Elimination & Control | 44842 | Medium | Court Manager | All cupboards/Chairs combustible materials need to be cleared from stairwell areas. | Auctioned via newsletter
2205 | Middleton Court | MIDDLETON_S001 | H21 | Scheme | 2022-05-31 15:24 | FRA_2205310520221053.pdf | BrigdenN | 2205310520221050 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | y0d82py7hshl3u8x0up | Medium Risk closed | Risk Closed | 44763.4742 | Obs9 | Escape Lighting | 45077 | Medium | Court Manager | Emergency Lighting is marked as non compliant by service contractor. | Awaiting installation of new lighting
2205 | Middleton Court | MIDDLETON_S001 | H21 | Scheme | 2022-05-31 15:24 | FRA_2205310520221053.pdf | BrigdenN | 2205310520221050 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | inf7cgficarl3u8mjpm | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Other | Flat No s 3, 7, 15 & 29 have been identified as high risk tenants. | NULL
2205 | Middleton Court | MIDDLETON_S001 | H21 | Scheme | 2022-05-31 15:24 | FRA_2205310520221053.pdf | BrigdenN | 2205310520221050 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | 5nzgdiieis6l3u9131y | Medium Risk closed | Risk Closed | 44763.4485 | Obs5 | Evacuation Strategy And Training | 45077 | Medium | Court Manager | Red Fire box needs updating with details of high risk tenants. | PCFRA done for 3 residents, 3, 7 and 15
2206 | Applegarth Court | APPLEGARTH_S001 | H21 | Scheme | 2022-07-28 15:38 | FRA_2206280720221530.pdf | BrigdenN | 2206280720221530 | Extra Care | Extra Care North | EC North 3 | North | North Patch 6 | 72cnmazru2xl654ucuz | Medium Risk closed | Risk Closed | 44770.7719 | Obs7 | Fire Protection Measures | 44772 | Medium | Court Manager | Fire doors to kitchen need to be kept closed. | Nikola and myself went to the kitchen and explained to the staff that this door must be kept shut at all times, the staff said they would confirm this with the restaurant proprietor
2206 | Applegarth Court | APPLEGARTH_S001 | H21 | Scheme | 2022-07-28 15:38 | FRA_2206280720221530.pdf | BrigdenN | 2206280720221530 | Extra Care | Extra Care North | EC North 3 | North | North Patch 6 | 0q62fiz6d2djl654ucu8 | Low Risk closed | Risk Closed | 44770.7695 | Obs7 | Fire Protection Measures | 45501 | Low | Court Manager | All walking frames need to be removed from the fire escape route. | We spoke to the resident confirmed and explained that this could not stay outside her flat, and the lady removed this
2206 | Applegarth Court | APPLEGARTH_S001 | H21 | Scheme | 2022-07-28 15:38 | FRA_2206280720221530.pdf | BrigdenN | 2206280720221530 | Extra Care | Extra Care North | EC North 3 | North | North Patch 6 | icamw0kasal654ucpd | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Other | Flat No s 1, 10, 11,15,17,24, 29, 32 & 38 are identified as high risk | NULL
2206 | Applegarth Court | APPLEGARTH_S001 | H21 | Scheme | 2022-07-28 15:38 | FRA_2206280720221530.pdf | BrigdenN | 2206280720221530 | Extra Care | Extra Care North | EC North 3 | North | North Patch 6 | hol163kjvq4l654ucro | Medium Risk closed | Risk Closed | 44771.5236 | Obs6 | Fire Hazards - Elimination & Control | 44772 | Medium | Court Manager | Combustible items need to be moved from Boiler Room | Cleared and swept
2206 | Applegarth Court | APPLEGARTH_S001 | H21 | Scheme | 2022-07-28 15:38 | FRA_2206280720221530.pdf | BrigdenN | 2206280720221530 | Extra Care | Extra Care North | EC North 3 | North | North Patch 6 | hdx7026jcpal654ucth | Medium Risk closed | Risk Closed | 44775.5252 | Obs7 | Fire Protection Measures | 45135 | Medium | Court Manager | Door to laundry requires door closer to be repaired as it's not shutting properly. | Eased and adjusted by Handyperson
2206 | Applegarth Court | APPLEGARTH_S001 | H21 | Scheme | 2022-07-28 15:38 | FRA_2206280720221530.pdf | BrigdenN | 2206280720221530 | Extra Care | Extra Care North | EC North 3 | North | North Patch 6 | ge3tucnewd7l654ucxf | High Risk Closed | Risk Closed | 44770.7691 | Obs7 | Fire Protection Measures | 44862 | High | Court Manager | Mobility scooter was being charges at the bottom of the stairwell. | Following a discussion with the resident and Nikola and myself the scooter was removed and parked in the buggy park, in the space provided the resident confirmed she would do this from now on
2206 | Applegarth Court | APPLEGARTH_S001 | H21 | Scheme | 2022-07-28 15:38 | FRA_2206280720221530.pdf | BrigdenN | 2206280720221530 | Extra Care | Extra Care North | EC North 3 | North | North Patch 6 | m9y3b38zdjel654ucyi | Medium Risk closed | Risk Closed | 44775.5249 | Obs7 | Fire Protection Measures | 45135 | Medium | Court Manager | Communal Fire Doors outside flats 10, 20 & 32 need adjusting as they are not closing properly. | Completed by Handyperson
2206 | Applegarth Court | APPLEGARTH_S001 | H21 | Scheme | 2022-07-28 15:38 | FRA_2206280720221530.pdf | BrigdenN | 2206280720221530 | Extra Care | Extra Care North | EC North 3 | North | North Patch 6 | mmloilu3sgjl654ucwo | Medium Risk closed | Risk Closed | 44825.9322 | Obs7 | Fire Protection Measures | 45135 | Medium | Court Manager | Combustible materials need to be cleared from the fire escape route | items and pieces of equipment removed/returned from fire escape route
2206 | Applegarth Court | APPLEGARTH_S001 | H21 | Scheme | 2022-07-28 15:38 | FRA_2206280720221530.pdf | BrigdenN | 2206280720221530 | Extra Care | Extra Care North | EC North 3 | North | North Patch 6 | p4utl8bv6qol654ucsq | Medium Risk closed | Risk Closed | 44770.7732 | Obs7 | Fire Protection Measures | 45135 | Medium | Court Manager | Fire door to lounge is being wedged open. | The wedge has been removed, so that this can no longer be propped open by any resident
2206 | Applegarth Court | APPLEGARTH_S001 | H21 | Scheme | 2022-07-28 15:38 | FRA_2206280720221530.pdf | BrigdenN | 2206280720221530 | Extra Care | Extra Care North | EC North 3 | North | North Patch 6 | ta2fa394oasl654ucvy | Medium Risk closed | Risk Closed | 44770.7714 | Obs7 | Fire Protection Measures | 45135 | Medium | Court Manager | Fire Exit in dining room is being blocked by dining table. | The dining table has been moved and the Restaurant staff have been informed to ensure this is kept clear
2206 | Applegarth Court | APPLEGARTH_S001 | H21 | Scheme | 2022-07-28 15:38 | FRA_2206280720221530.pdf | BrigdenN | 2206280720221530 | Extra Care | Extra Care North | EC North 3 | North | North Patch 6 | uocic1qpi48l654unqh | Medium Risk closed | Risk Closed | 44770.7729 | Obs11 | Fire Fighting Equipment | 45135 | Medium | Court Manager | Fire blanket needs to be kept in kitchen area, so it is easily accessible in the event of a fire. | Nikola and I went to speak to the Restaurant staff about ensuring that the fire blanket was accessible to all, in the event of a fire, this was moved into the main kitchen area.
2206 | Applegarth Court | APPLEGARTH_S001 | H21 | Scheme | 2022-07-28 15:38 | FRA_2206280720221530.pdf | BrigdenN | 2206280720221530 | Extra Care | Extra Care North | EC North 3 | North | North Patch 6 | r0wduujjp8al654ucqb | Medium Risk closed | Risk Closed | 44863.8873 | Obs6 | Fire Hazards - Elimination & Control | 45135 | Medium | Court Manager | Combustible items need to be moved from stair well area. | All items have been removed
2206 | Applegarth Court | APPLEGARTH_S001 | H21 | Scheme | 2022-07-28 15:38 | FRA_2206280720221530.pdf | BrigdenN | 2206280720221530 | Extra Care | Extra Care North | EC North 3 | North | North Patch 6 | xeem8x9v31jl654ucr1 | Medium Risk closed | Risk Closed | 44771.5234 | Obs6 | Fire Hazards - Elimination & Control | 44772 | Medium | Court Manager | Combustible items need to be cleared from the electrical meter room. | These have been cleared and swept
2210 | Yarborough Court | YARBOROUGH_S001 | H21 | Scheme | 2022-10-25 15:54 | FRA_2210251020221517.pdf | BrigdenN | 2210251020221510 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | xw1wndfaujkl9obryu8 | Medium Risk closed | Risk Closed | 44887.641 | Obs16 | Testing And Maintenance | 45224 | Medium | Court Manager | Door to corridor near lift needs adjusting as it does not close properly. | Door has been adjusted on 21.11.22
2210 | Yarborough Court | YARBOROUGH_S001 | H21 | Scheme | 2022-10-25 15:54 | FRA_2210251020221517.pdf | BrigdenN | 2210251020221510 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | r2rauj8vmpsl9ob0r39 | Low Risk closed | Risk Closed | 44862.43 | Obs7 | Fire Protection Measures | 45590 | Low | Court Manager | Remove redundant break glass box above fire alarm panel. | removed box
2210 | Yarborough Court | YARBOROUGH_S001 | H21 | Scheme | 2022-10-25 15:54 | FRA_2210251020221517.pdf | BrigdenN | 2210251020221510 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | jv4i9wd192pl9oaq7ds | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Other | Flats 2, 5, 24 & 25 are all high risk tenants. Flats 5 & 24 have oxygen. | NULL
2210 | Yarborough Court | YARBOROUGH_S001 | H21 | Scheme | 2022-10-25 15:54 | FRA_2210251020221517.pdf | BrigdenN | 2210251020221510 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | 49o1cogqjb9l9oawftl | Low Risk closed | Risk Closed | 44860.346 | Obs7 | Fire Protection Measures | 45590 | Low | Court Manager | Trip hazzard to be removed from corridor area. | Removed item
2211 | Henry Vernone Court | HENRYVERN_S001 | H21 | Scheme | 2022-08-10 16:45 | FRA_2211100820221641.pdf | BrigdenN | 2211100820221640 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | 6a11xfg91wvl6ns4tuw | Medium Risk closed | Risk Closed | 44788.6115 | Obs6 | Fire Hazards - Elimination & Control | 44790 | Medium | Court Manager | Please remove all trip hazzards from fire escape routes | Moved inside and talked to resident
2211 | Henry Vernone Court | HENRYVERN_S001 | H21 | Scheme | 2022-08-10 16:45 | FRA_2211100820221641.pdf | BrigdenN | 2211100820221640 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | je4x0hx7g7l6ns4tps | Medium Risk closed | Risk Closed | 44788.6716 | Obs5 | Evacuation Strategy And Training | 45148 | Medium | Court Manager | Court manager needs to complete her fire safety managers course | I completed my fire safety manager certificate 7 January 2022
2211 | Henry Vernone Court | HENRYVERN_S001 | H21 | Scheme | 2022-08-10 16:45 | FRA_2211100820221641.pdf | BrigdenN | 2211100820221640 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | gf2qeezzr1l6ns4ts7 | High Risk Closed | Risk Closed | 44788.6133 | Obs6 | Fire Hazards - Elimination & Control | 44517 | High | Court Manager | Mobility scooter needs to be immediately removed from the fire escape route outside no 24 | Removed. The residents have now moved out and taken the scooters with them
2211 | Henry Vernone Court | HENRYVERN_S001 | H21 | Scheme | 2022-08-10 16:45 | FRA_2211100820221641.pdf | BrigdenN | 2211100820221640 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | ig0q70feshdl6ns4tu3 | Medium Risk closed | Risk Closed | 44788.6159 | Obs6 | Fire Hazards - Elimination & Control | 45148 | Medium | Court Manager | Please clear all combustible items from left motor room area. | I have written to all residents to ask who the Christmas decorations belong too and to store them in their flat.
2211 | Henry Vernone Court | HENRYVERN_S001 | H21 | Scheme | 2022-08-10 16:45 | FRA_2211100820221641.pdf | BrigdenN | 2211100820221640 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | j9csizj9ucll6ns4trk | High Risk Closed | Risk Closed | 44788.6173 | Obs6 | Fire Hazards - Elimination & Control | 44875 | High | Court Manager | Charging cable to mobility scooter was left turned on but not connected to scooter outside no 24 | Scooters have been removed
2211 | Henry Vernone Court | HENRYVERN_S001 | H21 | Scheme | 2022-08-10 16:45 | FRA_2211100820221641.pdf | BrigdenN | 2211100820221640 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | r8cgy3krj6l6ns4tt3 | Medium Risk closed | Risk Closed | 44788.6104 | Obs6 | Fire Hazards - Elimination & Control | 44790 | Medium | Court Manager | Table and chsirs need to be removed from the fire escapecroute outside flat no 31 | The table and chairs are often brought out on sunny days and I have reminded the resident both verbally and in writing to taken them back inside once finished with. At time of inspection they have been taken inside the flat.
2211 | Henry Vernone Court | HENRYVERN_S001 | H21 | Scheme | 2022-08-10 16:45 | FRA_2211100820221641.pdf | BrigdenN | 2211100820221640 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | qg3apb3junl6ns4tw8 | Medium Risk closed | Risk Closed | 44788.6581 | Obs6 | Fire Hazards - Elimination & Control | 44790 | Medium | Court Manager | Please remove all trip hazzards from fire escape routes | Trip hazards such as garden ornaments in doorways elcome mats I have sent a general letter to request residents remove them immediately
2211 | Henry Vernone Court | HENRYVERN_S001 | H21 | Scheme | 2022-08-10 16:45 | FRA_2211100820221641.pdf | BrigdenN | 2211100820221640 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | ngxopl5v9tcl6ns4tqs | Medium Risk closed | Risk Closed | 44788.6162 | Obs6 | Fire Hazards - Elimination & Control | 44790 | Medium | Court Manager | No evidence of PAT testing on mobile scooters. | Scooters are no longer here
2211 | Henry Vernone Court | HENRYVERN_S001 | H21 | Scheme | 2022-08-10 16:45 | FRA_2211100820221641.pdf | BrigdenN | 2211100820221640 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | uvblt63uo29l6ns4tov | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Other | Flat numbers 1, 19, 24, 26, 32, 34 are all high risk tenants | NULL
2280 | Meadow View | MEADOWVIEW_S001 | H21 | Scheme | 2022-09-21 10:52 | FRA_2280210920220937.pdf | BrigdenN | 2280210920220930 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 6 | 7gm2brbhnw8l8bds8yu | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Other | Flat no s 2, 11, 25 and 27 have been identified as high risk. | NULL
2302 | Evans Williams Court | EVANSWILL_S001 | H21 | Scheme | 2022-11-03 11:48 | FRA_2302031120221010.pdf | ComleyB | 2302031120221010 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 6fjh27igo1fla0z5v05 | Low Risk closed | Risk Closed | 44889.4321 | Obs15 | Management Of Fire Safety | 45599 | Low | Court Manager | Page missing from Fire Safety training records. Ensure risk management information is latest file. | file up dated
2302 | Evans Williams Court | EVANSWILL_S001 | H21 | Scheme | 2022-11-03 11:48 | FRA_2302031120221010.pdf | ComleyB | 2302031120221010 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | 9o52c6fbjfela0xobgb | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45233 | Medium | Surveyor | Meter cupboards to be fire lined to create fire compartmentation between cupboards, corridors and flats. | NULL
2302 | Evans Williams Court | EVANSWILL_S001 | H21 | Scheme | 2022-11-03 11:48 | FRA_2302031120221010.pdf | ComleyB | 2302031120221010 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | o0ij67jevula0xrlor | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45233 | Medium | Surveyor | Electrical fuse board on communal corridor to be boxed in and fire proofed. | NULL
2302 | Evans Williams Court | EVANSWILL_S001 | H21 | Scheme | 2022-11-03 11:48 | FRA_2302031120221010.pdf | ComleyB | 2302031120221010 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | nmtgwmlnyila103vkl | Low Risk closed | Risk Closed | 44889.4327 | Obs8 | Measures To Limit Fire Spread And Development | 45599 | Low | Court Manager | Flat 21 front door not fully closing, keep may require adjusting. | Work order raised 1573636, new door closer needed, replaced and door checked, completed 21st Nov 22
2302 | Evans Williams Court | EVANSWILL_S001 | H21 | Scheme | 2022-11-03 11:48 | FRA_2302031120221010.pdf | ComleyB | 2302031120221010 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | rs6hrza0omila0zs261 | Low Risk closed | Risk Closed | 44889.4308 | Obs8 | Measures To Limit Fire Spread And Development | 45599 | Low | Court Manager | Flat 13 front door not closing. Keep may need adjusting. | work order raised 1573635 new door closer needed and replaced, 21st Nov 22
2302 | Evans Williams Court | EVANSWILL_S001 | H21 | Scheme | 2022-11-03 11:48 | FRA_2302031120221010.pdf | ComleyB | 2302031120221010 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | l4otloyu77bla0zzmjt | Low Risk closed | Risk Closed | 44889.4318 | Obs8 | Measures To Limit Fire Spread And Development | 45599 | Low | Court Manager | Flat 18 front flat door not self closing, cardboard to be removed from door, may require ease and adjusting. | Work order raised 1573637 mount joy attended removed cardboard from door and checked closure completed 18th Nov 22
2302 | Evans Williams Court | EVANSWILL_S001 | H21 | Scheme | 2022-11-03 11:48 | FRA_2302031120221010.pdf | ComleyB | 2302031120221010 | Retirement Housing | Mid South | Hampshire South and IOW | South | South Patch 5 | zl7foexcaala0z9oaj | Observation Only | Risk Open | NULL | Obs15 | Management Of Fire Safety | NULL | N/A | Other | Compliance checks stored on PEBBLES | NULL
2402 | Duchess of Kent Court | DUCHESSOFKEN_S001 | H21 | Scheme | 2022-03-25 07:18 | FRA_2402250320220708.pdf | BhopalP | 2402250320220700 | Retirement Housing | London Kent | Kent North | South | South Patch 6 | xakaxacisel1630lrg | Observation Only | Risk Closed | 44652.4905 | Obs5 | Evacuation Strategy And Training | NULL | N/A | Court Manager | Zoned evacuation strategy whereas if alarms sound in a zone all flats in that zone should evacuation. | no action required - regular reminders of fire safety in newsletters and court meetings
2403 | Lord Cornwallis Court | LORDCORN_S001 | H21 | Scheme | 2022-07-21 11:09 | FRA_2403210720221026.pdf | LingF | 2403210720221020 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | vpt1rmt4hsbl5utwdkx | Observation Only | Risk Closed | 44820.3814 | Obs9 | Escape Lighting | NULL | N/A | Surveyor | Lightening to a good standard and in accordance to requirements | Info
2403 | Lord Cornwallis Court | LORDCORN_S001 | H21 | Scheme | 2022-07-21 11:09 | FRA_2403210720221026.pdf | LingF | 2403210720221020 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | w5ofl92jtwtl5utwdk1 | Observation Only | Risk Closed | 44820.3812 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Surveyor | Corridors 1/7 and 8/14 are not ventilated but have two direction of travel, 23m. | Info
2403 | Lord Cornwallis Court | LORDCORN_S001 | H21 | Scheme | 2022-07-21 11:09 | FRA_2403210720221026.pdf | LingF | 2403210720221020 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | z9ivh6e77ml5uu6l9y | Observation Only | Risk Closed | 44820.3813 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel no faults showing | Info
2403 | Lord Cornwallis Court | LORDCORN_S001 | H21 | Scheme | 2022-07-21 11:09 | FRA_2403210720221026.pdf | LingF | 2403210720221020 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | guhdzaslrdal5uubqnw | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45494 | Low | Court Manager | Fire stopping required around SVP within service cupboard adj F18. Timber casing will need to be removed and suitable intumescent collar where necessary | NULL
2403 | Lord Cornwallis Court | LORDCORN_S001 | H21 | Scheme | 2022-07-21 11:09 | FRA_2403210720221026.pdf | LingF | 2403210720221020 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | gep6jzadvkbl5utwdid | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | No high risk residents noted within occupancy profile although one occupant has a requirement for oxygen but chooses not to leave their flat | NULL
2403 | Lord Cornwallis Court | LORDCORN_S001 | H21 | Scheme | 2022-07-21 11:09 | FRA_2403210720221026.pdf | LingF | 2403210720221020 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | g1erc4h9ypl5utwdls | Low Risk to be actioned | Risk Open | NULL | Obs16 | Testing And Maintenance | 45494 | Low | Court Manager | No record of Elights drain down test. | NULL
2403 | Lord Cornwallis Court | LORDCORN_S001 | H21 | Scheme | 2022-07-21 11:09 | FRA_2403210720221026.pdf | LingF | 2403210720221020 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | qu4f3n8nv1hl5uuelpj | Low Risk closed | Risk Closed | 44820.3811 | Obs8 | Measures To Limit Fire Spread And Development | 45494 | Low | Surveyor | Single direction of travel, distance in excess of 20m. Grd and 1st floor corridors . Flats 22/15 _ 23/30. Stump put policy, all doors fd30s. | Info
2403 | Lord Cornwallis Court | LORDCORN_S001 | H21 | Scheme | 2022-07-21 11:09 | FRA_2403210720221026.pdf | LingF | 2403210720221020 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | 97reebgfcel5uu8t26 | Low Risk to be actioned | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | 45494 | Low | Court Manager | Relocate fire zone chart | NULL
2403 | Lord Cornwallis Court | LORDCORN_S001 | H21 | Scheme | 2022-07-21 11:09 | FRA_2403210720221026.pdf | LingF | 2403210720221020 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | 3m4366nedfl5uutwfp | Observation Only | Risk Open | NULL | Obs1 | The Building | NULL | N/A | Court Manager | Main entrance, tile panels, general building facade | NULL
2403 | Lord Cornwallis Court | LORDCORN_S001 | H21 | Scheme | 2022-07-21 11:09 | FRA_2403210720221026.pdf | LingF | 2403210720221020 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | 32cywzpex3sl5utwdj4 | Observation Only | Risk Closed | 44820.381 | Obs5 | Evacuation Strategy And Training | NULL | N/A | Surveyor | F3 noted as a fire Marshall to assist with the silencing of alarms following FRS attendance | Info
2405 | Dossett Court | DOSSETT_S001 | H21 | Scheme | 2022-02-04 11:18 | FRA_2405040220221059.pdf | LingF | 2405040220221050 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | bo7jlm9bt05kz8apl8u | Observation Only | Risk Closed | 44613.4769 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | F17 _ Suffers with mental impairment would be able to leave their flat may be confused. | resident has a personal fire risk assessment in place
2405 | Dossett Court | DOSSETT_S001 | H21 | Scheme | 2022-02-04 11:18 | FRA_2405040220221059.pdf | LingF | 2405040220221050 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | qtnujcu1oekz8apl6w | Observation Only | Risk Closed | 44742.6018 | Obs1 | The Building | NULL | N/A | Surveyor | General elevation view showing extent of cladding system | Info only
2405 | Dossett Court | DOSSETT_S001 | H21 | Scheme | 2022-02-04 11:18 | FRA_2405040220221059.pdf | LingF | 2405040220221050 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | u0dz24gz1pckz8aplaa | Medium Risk closed | Risk Closed | 44613.4772 | Obs8 | Measures To Limit Fire Spread And Development | 44961 | Medium | Court Manager | F11 door closer not operational | Works order on, this will be fixed
2405 | Dossett Court | DOSSETT_S001 | H21 | Scheme | 2022-02-04 11:18 | FRA_2405040220221059.pdf | LingF | 2405040220221050 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | t2n5y19t3f9kz8aplb6 | Observation Only | Risk Closed | 44742.6017 | Obs9 | Escape Lighting | NULL | N/A | Surveyor | System appears to meet requirements of BS:5266 | Info only
2405 | Dossett Court | DOSSETT_S001 | H21 | Scheme | 2022-02-04 11:18 | FRA_2405040220221059.pdf | LingF | 2405040220221050 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | l614g8z2lykz8apl7f | Observation Only | Risk Closed | 44706.3997 | Obs1 | The Building | NULL | N/A | Surveyor | Newer style traditional brick block construction | Info only
2405 | Dossett Court | DOSSETT_S001 | H21 | Scheme | 2022-02-04 11:18 | FRA_2405040220221059.pdf | LingF | 2405040220221050 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | ktgxyr15y9okz8apld8 | Observation Only | Risk Closed | 44600.5399 | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | Residents informed of rezoning strategy and how to respond to the alarms in the event of a fire. | n/a - letters where given out at the time to advise residents of the changes
2405 | Dossett Court | DOSSETT_S001 | H21 | Scheme | 2022-02-04 11:18 | FRA_2405040220221059.pdf | LingF | 2405040220221050 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | knaqnlawwbekz8apl86 | Observation Only | Risk Closed | 44706.3995 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel | Info only
2405 | Dossett Court | DOSSETT_S001 | H21 | Scheme | 2022-02-04 11:18 | FRA_2405040220221059.pdf | LingF | 2405040220221050 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | mhlzn8k6dzkkz8apl9k | Observation Only | Risk Closed | 44600.5405 | Obs5 | Evacuation Strategy And Training | NULL | N/A | Court Manager | F4 _ noted as responsible resident will silence and reset the panel following FRS attendance and authorisation | flat 4 is the registered responsible resident , this has been in place since I have been manager
2405 | Dossett Court | DOSSETT_S001 | H21 | Scheme | 2022-02-04 11:18 | FRA_2405040220221059.pdf | LingF | 2405040220221050 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | lt3mhnggpskz8aplc6 | Observation Only | Risk Closed | 44742.6015 | Obs10 | Fire Safety And Notices | NULL | N/A | Surveyor | Signage appears to meet requirements of BS:5499 | Info only
2406 | Rivers Court | RIVERS_S001 | H21 | Scheme | 2022-02-23 09:53 | FRA_2406230220220927.pdf | LingF | 2406230220220920 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | li1i22dfwbnkzzcs6kg | Observation Only | Risk Closed | 44637.5525 | Obs5 | Evacuation Strategy And Training | NULL | N/A | Court Manager | CM to discuss rezoned fire strategy with residents | This is a duplicate task
2406 | Rivers Court | RIVERS_S001 | H21 | Scheme | 2022-02-23 09:53 | FRA_2406230220220927.pdf | LingF | 2406230220220920 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | n7lr7n4d7gkzzcs6j6 | Observation Only | Risk Closed | 44742.6022 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Rear blocks alarm panel | Info only
2406 | Rivers Court | RIVERS_S001 | H21 | Scheme | 2022-02-23 09:53 | FRA_2406230220220927.pdf | LingF | 2406230220220920 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | k1ld9fkxlvkzzcs6l3 | Low Risk closed | Risk Closed | 44637.5522 | Obs6 | Fire Hazards - Elimination & Control | 45345 | Low | Court Manager | Remove chair from elec cupboard | CM moved 17/03/22
2406 | Rivers Court | RIVERS_S001 | H21 | Scheme | 2022-02-23 09:53 | FRA_2406230220220927.pdf | LingF | 2406230220220920 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | fkoaxsxskpkzzcs6pb | Observation Only | Risk Closed | 44645.5502 | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | CM to discuss rezoned fire strategy with residents | Discussed at residents meeting on 24/03/22
2406 | Rivers Court | RIVERS_S001 | H21 | Scheme | 2022-02-23 09:53 | FRA_2406230220220927.pdf | LingF | 2406230220220920 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | isr7z6mko3jkzzcs6nm | Medium Risk closed | Risk Closed | 44690.6259 | Obs8 | Measures To Limit Fire Spread And Development | 44980 | Medium | Court Manager | F12 _ Flat door does not close | Tenant has had underlay removed door now closes. All ok
2406 | Rivers Court | RIVERS_S001 | H21 | Scheme | 2022-02-23 09:53 | FRA_2406230220220927.pdf | LingF | 2406230220220920 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | st2ketrqmyekzzcs6gw | Observation Only | Risk Closed | 44763.4646 | Obs1 | The Building | NULL | N/A | Surveyor | Window infill panels | Info
2406 | Rivers Court | RIVERS_S001 | H21 | Scheme | 2022-02-23 09:53 | FRA_2406230220220927.pdf | LingF | 2406230220220920 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | orf5ycoy96kzzcs6o9 | Low Risk closed | Risk Closed | 44635.5157 | Obs8 | Measures To Limit Fire Spread And Development | 45345 | Low | Court Manager | Fill around fire cable adj 3 | repairs completed 15/03/22
2406 | Rivers Court | RIVERS_S001 | H21 | Scheme | 2022-02-23 09:53 | FRA_2406230220220927.pdf | LingF | 2406230220220920 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | cs16rd8wg28kzzcs6hl | Observation Only | Risk Closed | 44763.4645 | Obs1 | The Building | NULL | N/A | Surveyor | General elevation view showing extent of cladding panels and bay windows | Info
2406 | Rivers Court | RIVERS_S001 | H21 | Scheme | 2022-02-23 09:53 | FRA_2406230220220927.pdf | LingF | 2406230220220920 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | dlfpc7jv0fbkzzcs6iq | Observation Only | Risk Closed | 44763.4648 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Main fire panel and zone chart | Info
2406 | Rivers Court | RIVERS_S001 | H21 | Scheme | 2022-02-23 09:53 | FRA_2406230220220927.pdf | LingF | 2406230220220920 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | ehefg4806xokzzcs6i4 | Observation Only | Risk Closed | 44763.4647 | Obs1 | The Building | NULL | N/A | Surveyor | Single stair (4flats) more recent blocks built 1985 | Info
2406 | Rivers Court | RIVERS_S001 | H21 | Scheme | 2022-02-23 09:53 | FRA_2406230220220927.pdf | LingF | 2406230220220920 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | aq60nnys7njkzzcs6mc | Low Risk closed | Risk Closed | 44635.5138 | Obs8 | Measures To Limit Fire Spread And Development | 45345 | Low | Court Manager | Make good around fire cable adj guestroom | Repair completed on 15/03/2022
2406 | Rivers Court | RIVERS_S001 | H21 | Scheme | 2022-02-23 09:53 | FRA_2406230220220927.pdf | LingF | 2406230220220920 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | al7pcae41bgkzzcs6jr | Observation Only | Risk Closed | 44635.5147 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | F9 _ cluttered flat, CM aware of issues and has engaged with social services regarding issues around anti social behaviour. Resident does not cook or smoke. F13 _ bed bound resident, does not smoke or cook, supported by family and carers. F20 _ hoarder, does not allow CM in to the property. | All information up to date. Once resident returns from hospital from flat 9 will do new PCFRA as mobility etc may have changed
2406 | Rivers Court | RIVERS_S001 | H21 | Scheme | 2022-02-23 09:53 | FRA_2406230220220927.pdf | LingF | 2406230220220920 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | zx85b10o4zkzzcs6mw | Low Risk closed | Risk Closed | 44637.5518 | Obs8 | Measures To Limit Fire Spread And Development | 45345 | Low | Court Manager | Continue door head to intersect with floor slab, using ablative fire slab | repair completed 17/03/22
2407 | Canon Appleton Court | CANONAPPL_S001 | H21 | Scheme | 2022-05-17 14:57 | FRA_2407170520221415.pdf | LingF | 2407170520221410 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | 9nsi436vwckl3a6h3w8 | Observation Only | Risk Closed | 44706.5131 | Obs7 | Fire Protection Measures | NULL | N/A | Court Manager | Two sections of walkway are dead ends, although not possible to achieve two directions of travel occupants, due to the design of the building and fire measures in place are advised to stay put. | nothing required
2407 | Canon Appleton Court | CANONAPPL_S001 | H21 | Scheme | 2022-05-17 14:57 | FRA_2407170520221415.pdf | LingF | 2407170520221410 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | did1xgf6x95l3a79v7s | Observation Only | Risk Closed | 44700.5946 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | F2: Hearing impairment has flashing beacons and pillow, CM to investigate additional beacons F5: Suffers with dementia occupant has 24hr support. F4: Suffers with dementia, living independently, CM to monitor and manage. | referred flat 2 to KFR with consent awaiting home visit
2407 | Canon Appleton Court | CANONAPPL_S001 | H21 | Scheme | 2022-05-17 14:57 | FRA_2407170520221415.pdf | LingF | 2407170520221410 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | bpihthfst1l3a6h3ww | Observation Only | Risk Closed | 44763.4685 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Surveyor | Flat doors open to external balcony walkways, these are not designated as fire doors. | Info
2407 | Canon Appleton Court | CANONAPPL_S001 | H21 | Scheme | 2022-05-17 14:57 | FRA_2407170520221415.pdf | LingF | 2407170520221410 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | 6u1f90b3teul3a6h3xo | Low Risk closed | Risk Closed | 44707.4749 | Obs10 | Fire Safety And Notices | 45429 | Low | Court Manager | Missing directional signage on stairwell and around walkways | ordered signs and put up 26.5.22
2407 | Canon Appleton Court | CANONAPPL_S001 | H21 | Scheme | 2022-05-17 14:57 | FRA_2407170520221415.pdf | LingF | 2407170520221410 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | 7nxc11naunql3a6h3uc | Observation Only | Risk Closed | 44763.4684 | Obs1 | The Building | NULL | N/A | Surveyor | Main entrance | Info
2407 | Canon Appleton Court | CANONAPPL_S001 | H21 | Scheme | 2022-05-17 14:57 | FRA_2407170520221415.pdf | LingF | 2407170520221410 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | pr4im6r5hzjl3a7opsa | Low Risk closed | Risk Closed | 44699.6255 | Obs6 | Fire Hazards - Elimination & Control | 45429 | Low | Court Manager | F8: scooter being charged through kitchen window, requires to be plugged into a dedicated external socket. | have spoken to the resident today (18.5.22) and he is happy to arrange to have one fitted
2407 | Canon Appleton Court | CANONAPPL_S001 | H21 | Scheme | 2022-05-17 14:57 | FRA_2407170520221415.pdf | LingF | 2407170520221410 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | tiegw2ec2sl3a6h3vo | Low Risk closed | Risk Closed | 44699.4628 | Obs7 | Fire Protection Measures | 45429 | Low | Court Manager | Guestroom is located off the lounge, measures in place to reduce the risk include - FA system, fire door to the GR, Located on grd floor. When windows are replaced suggest converting the window to an external door. | none required - to be considered when new windows due
2407 | Canon Appleton Court | CANONAPPL_S001 | H21 | Scheme | 2022-05-17 14:57 | FRA_2407170520221415.pdf | LingF | 2407170520221410 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | hgj3ii6mlal3a6h3to | Observation Only | Risk Closed | 44763.4683 | Obs1 | The Building | NULL | N/A | Surveyor | General building facade | Info
2407 | Canon Appleton Court | CANONAPPL_S001 | H21 | Scheme | 2022-05-17 14:57 | FRA_2407170520221415.pdf | LingF | 2407170520221410 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | l26e5g0lirbl3a6h3v0 | Observation Only | Risk Closed | 44763.4686 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel shows in full operational mode | Info
2409 | Trefor Jones Court | TREFORJONE_S001 | H21 | Scheme | 2022-08-10 11:49 | FRA_2409100820221049.pdf | LingF | 2409100820221040 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | kzey8zgggfkl6nfjsw4 | Observation Only | Risk Closed | 44820.3815 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Surveyor | Outgoing CM has not kept accurate records, buggy managers working to try and understand residents profile. No HR residents are known at this stage, Only 3 flats have morning calls, 19, 26, 36. | Info
2409 | Trefor Jones Court | TREFORJONE_S001 | H21 | Scheme | 2022-08-10 11:49 | FRA_2409100820221049.pdf | LingF | 2409100820221040 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | k648q611dkrl6ngnxg8 | Observation Only | Risk Closed | 44820.3816 | Obs1 | The Building | NULL | N/A | Surveyor | General elevation view showing extent of cladding and infill panels | Info
2409 | Trefor Jones Court | TREFORJONE_S001 | H21 | Scheme | 2022-08-10 11:49 | FRA_2409100820221049.pdf | LingF | 2409100820221040 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | mcqxsunu32ll6nghc7i | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45148 | Medium | Court Manager | Stairwell door opp F29 not closing into frame fully | NULL
2409 | Trefor Jones Court | TREFORJONE_S001 | H21 | Scheme | 2022-08-10 11:49 | FRA_2409100820221049.pdf | LingF | 2409100820221040 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | h6h740hi607l6nfjsvc | Observation Only | Risk Closed | 44820.3817 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Panel and zone chart | Info
2409 | Trefor Jones Court | TREFORJONE_S001 | H21 | Scheme | 2022-08-10 11:49 | FRA_2409100820221049.pdf | LingF | 2409100820221040 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | pzztbdwlgkl6nfjsxo | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45148 | Medium | Court Manager | F14 _ Replace faulty door closer F2 _ Replace door closer F4 _ Replace door closer F6 _ Replace door closer F7 _ Replace door closer | NULL
2409 | Trefor Jones Court | TREFORJONE_S001 | H21 | Scheme | 2022-08-10 11:49 | FRA_2409100820221049.pdf | LingF | 2409100820221040 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | 7q7cdbmooafl6nfjswv | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45148 | Medium | Court Manager | Flammable items within main electric distribution cupboard | NULL
2409 | Trefor Jones Court | TREFORJONE_S001 | H21 | Scheme | 2022-08-10 11:49 | FRA_2409100820221049.pdf | LingF | 2409100820221040 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | ejw31g0j77al6nfjsyg | Observation Only | Risk Open | NULL | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | Buddy CM working to upgrade fire folder. | NULL
2409 | Trefor Jones Court | TREFORJONE_S001 | H21 | Scheme | 2022-08-10 11:49 | FRA_2409100820221049.pdf | LingF | 2409100820221040 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | af7vnqtdjtl6ngoxo0 | Observation Only | Risk Closed | 44820.3818 | Obs1 | The Building | NULL | N/A | Surveyor | Infill panels | Info
2410 | Leslie Chalk House | LESLIECHAL_S001 | H21 | Scheme | 2022-01-20 12:35 | FRA_2410200120221119.pdf | LingF | 2410200120221110 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | 7fsa0og90a9kymxy68e | Medium Risk closed | Risk Closed | 44686.3548 | Obs6 | Fire Hazards - Elimination & Control | 44946 | Medium | Court Manager | Laundry consumer unit | New consumer unit put in
2410 | Leslie Chalk House | LESLIECHAL_S001 | H21 | Scheme | 2022-01-20 12:35 | FRA_2410200120221119.pdf | LingF | 2410200120221110 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | 040pzt1ianyqkymvsv5k | Observation Only | Risk Closed | 44706.3994 | Obs14 | Access By Emergency Services | NULL | N/A | Surveyor | Residents would assemble in either the front or rear car park areas. | Info only
2410 | Leslie Chalk House | LESLIECHAL_S001 | H21 | Scheme | 2022-01-20 12:35 | FRA_2410200120221119.pdf | LingF | 2410200120221110 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | qlbs0jdr0mkymxa3cm | Low Risk closed | Risk Closed | 44706.399 | Obs8 | Measures To Limit Fire Spread And Development | 45311 | Low | Surveyor | Evidence of pink expanding foam used as fire stopping above suspended ceiling. At time of scheme makeover allow to remove and replace | Info only
2410 | Leslie Chalk House | LESLIECHAL_S001 | H21 | Scheme | 2022-01-20 12:35 | FRA_2410200120221119.pdf | LingF | 2410200120221110 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | o00g8h4abakymwtcya | Observation Only | Risk Closed | 44623.4765 | Obs5 | Evacuation Strategy And Training | NULL | N/A | Court Manager | Flats 30/17 nominated fire responders whose dutybwould be to reset and silence the alarms following FRS attendance and authorisation. | Checked with each resident is still ok to do this
2410 | Leslie Chalk House | LESLIECHAL_S001 | H21 | Scheme | 2022-01-20 12:35 | FRA_2410200120221119.pdf | LingF | 2410200120221110 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | t8zii4pebbfkymy8ksl | Observation Only | Risk Closed | 44706.3989 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel and zone chart | Info only
2410 | Leslie Chalk House | LESLIECHAL_S001 | H21 | Scheme | 2022-01-20 12:35 | FRA_2410200120221119.pdf | LingF | 2410200120221110 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | fmpyywr4t4kymybxlb | Medium Risk closed | Risk Closed | 44651.4436 | Obs6 | Fire Hazards - Elimination & Control | 44946 | Medium | Court Manager | Reduce and remove high levels of flammable Items within comms cupboard. Provide metal storage cupboards for cleaners materials. | All cleared out metal draws for cleaning products and guest room bedding and towels
2410 | Leslie Chalk House | LESLIECHAL_S001 | H21 | Scheme | 2022-01-20 12:35 | FRA_2410200120221119.pdf | LingF | 2410200120221110 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | iiv3mh0uxakymxh54y | Low Risk closed | Risk Closed | 44629.4105 | Obs10 | Fire Safety And Notices | 45311 | Low | Court Manager | Additional fire exit sign required to direct F6 | All hanging
2410 | Leslie Chalk House | LESLIECHAL_S001 | H21 | Scheme | 2022-01-20 12:35 | FRA_2410200120221119.pdf | LingF | 2410200120221110 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | jcebi95xfankymw86li | Observation Only | Risk Closed | 44587.3695 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | F28/F29 _ occupants suffering with dementia would respond to a fire alarm activation. CM has frequent support plan reviews. | I have spoken to both residents and they have both said that when they hear the fire alarm they know to leave their flat and move to the front of the building near the lift
2410 | Leslie Chalk House | LESLIECHAL_S001 | H21 | Scheme | 2022-01-20 12:35 | FRA_2410200120221119.pdf | LingF | 2410200120221110 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | zb6amelqknskymy6e1u | Observation Only | Risk Closed | 44706.3992 | Obs1 | The Building | NULL | N/A | Surveyor | Front elevation view showing extent of tile hung cladding system | Info only
2415 | Crispe House | CRISPEHOUS_S001 | H21 | Scheme | 2021-12-16 10:13 | FRA_2415161220210911.pdf | LingF | 2415161220210910 | Extra Care | EC Kent | Kent 2 | South | South Patch 3 | xktfdrs774bkx8qtxy8 | Observation Only | Risk Closed | 44578.6537 | Obs11 | Fire Fighting Equipment | NULL | N/A | Surveyor | No portable FFE provided | Info only
2415 | Crispe House | CRISPEHOUS_S001 | H21 | Scheme | 2021-12-16 10:13 | FRA_2415161220210911.pdf | LingF | 2415161220210910 | Extra Care | EC Kent | Kent 2 | South | South Patch 3 | n8r1wg61uw8kx8qtxtu | Observation Only | Risk Closed | 44578.6541 | Obs1 | The Building | NULL | N/A | Surveyor | General elevation view showing extent of cladding panels and balcony structures | Info only
2415 | Crispe House | CRISPEHOUS_S001 | H21 | Scheme | 2021-12-16 10:13 | FRA_2415161220210911.pdf | LingF | 2415161220210910 | Extra Care | EC Kent | Kent 2 | South | South Patch 3 | o2qpmveb85ikx8qtxz0 | Observation Only | Risk Closed | 44578.6539 | Obs12 | Automatic Fire Systems i.e. Suppression System | NULL | N/A | Surveyor | Sprinkler system | Info only
2415 | Crispe House | CRISPEHOUS_S001 | H21 | Scheme | 2021-12-16 10:13 | FRA_2415161220210911.pdf | LingF | 2415161220210910 | Extra Care | EC Kent | Kent 2 | South | South Patch 3 | oa5x827exx8kx8qtxvt | Medium Risk closed | Risk Closed | 44593.3653 | Obs7 | Fire Protection Measures | 44911 | Medium | Court Manager | Motorised hoist and charging apparatus on escape routes. | Told onsite support manager it cannot be left there and was removed immediately, with a note in their comms book to remind staff.
2415 | Crispe House | CRISPEHOUS_S001 | H21 | Scheme | 2021-12-16 10:13 | FRA_2415161220210911.pdf | LingF | 2415161220210910 | Extra Care | EC Kent | Kent 2 | South | South Patch 3 | 2ygfqr4xazqkx8s6d3v | Observation Only | Risk Closed | 44578.6536 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Surveyor | Customers are supported by 24/7 Care support from the neighbouring scheme. This includes the night time hours. | Info only
2415 | Crispe House | CRISPEHOUS_S001 | H21 | Scheme | 2021-12-16 10:13 | FRA_2415161220210911.pdf | LingF | 2415161220210910 | Extra Care | EC Kent | Kent 2 | South | South Patch 3 | ahwues0dqq5kx8qtxum | Low Risk to be actioned | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | 45276 | Low | Court Manager | No detection within the common parts (stairwell and landing) of the building. Install a suitable single zone system covering escape routes and loft spaces linked to OOH service provider | NULL
2415 | Crispe House | CRISPEHOUS_S001 | H21 | Scheme | 2021-12-16 10:13 | FRA_2415161220210911.pdf | LingF | 2415161220210910 | Extra Care | EC Kent | Kent 2 | South | South Patch 3 | fa0yv4ps26nkx8qtxxg | Observation Only | Risk Closed | 44578.654 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Surveyor | Scheme has recently undergone a comprehensive passive fire upgrade works | Info only
2415 | Crispe House | CRISPEHOUS_S001 | H21 | Scheme | 2021-12-16 10:13 | FRA_2415161220210911.pdf | LingF | 2415161220210910 | Extra Care | EC Kent | Kent 2 | South | South Patch 3 | dikhcnhv9amkx8qtxwk | Observation Only | Risk Closed | 44578.6538 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Surveyor | MOV ON escape routes | Info only
2417 | Thomas Place | THOMASPLAC_S001 | H21 | Scheme | 2022-10-20 18:25 | FRA_2417201020221425.pdf | LingF | 2417201020221420 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | f5gmoajgabvl9h3ihna | Low Risk closed | Risk Closed | 44862.3828 | Obs8 | Measures To Limit Fire Spread And Development | 45585 | Low | Court Manager | F33 _ check operation of door closer | Order raised to OGC on 7 day urgent response. OGC attended 24 10 22 Parts are on order.
2417 | Thomas Place | THOMASPLAC_S001 | H21 | Scheme | 2022-10-20 18:25 | FRA_2417201020221425.pdf | LingF | 2417201020221420 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | eka4gfh7ioul9h7emna | Observation Only | Risk Closed | 44855.657 | Obs13 | Other Relevant Fixed Systems | NULL | N/A | Court Manager | Service dates | Dates all in order/scheduled
2417 | Thomas Place | THOMASPLAC_S001 | H21 | Scheme | 2022-10-20 18:25 | FRA_2417201020221425.pdf | LingF | 2417201020221420 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | as5ta09j2atl9h3n9fo | Low Risk closed | Risk Closed | 44862.3832 | Obs15 | Management Of Fire Safety | 45585 | Low | Court Manager | Prior to returning to stay put, care team shall require refresher training on the evac policy and procedure | Refresher training booked 1st November
2417 | Thomas Place | THOMASPLAC_S001 | H21 | Scheme | 2022-10-20 18:25 | FRA_2417201020221425.pdf | LingF | 2417201020221420 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | 2xjenc0sbq2l9h3ihoe | Medium Risk closed | Risk Closed | 44855.6513 | Obs8 | Measures To Limit Fire Spread And Development | 45219 | Medium | Court Manager | 22 _ ease adjust door to close into frame | 7 day urgent response order to address issue with door.
2417 | Thomas Place | THOMASPLAC_S001 | H21 | Scheme | 2022-10-20 18:25 | FRA_2417201020221425.pdf | LingF | 2417201020221420 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | 31mg61f77rkl9h3ihme | Low Risk closed | Risk Closed | 44862.3826 | Obs5 | Evacuation Strategy And Training | 45585 | Low | Court Manager | The ongoing cladding rectification works, internal passive fire upgrade works, and ongoing CM compliance testing, and support from care teams have returned the scheme back to a state where stay put can be implemented. 1: Two flats remain with ESP insulation around them there is no insulation on the level below or above, removing the risk of fire spread with the cladding system. 2: Occupants within two noted above do not pose a greater hazard for starting a fire due to their care support package, occupants are able to evac to a relative place of safety with verbal instructions to evacuate. 3: Remaining areas where insulation remains (estimated less that 10%) do not pose a risk of fire spread preventing evac and egress, 4: Height of remain insulation is below 10metres for fire fighting. | n/a
2417 | Thomas Place | THOMASPLAC_S001 | H21 | Scheme | 2022-10-20 18:25 | FRA_2417201020221425.pdf | LingF | 2417201020221420 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | qt8wjqhqt4cl9h3ihlp | Low Risk closed | Risk Closed | 44862.3829 | Obs4 | The Occupant - Information Provided By The Court Manager | 45585 | Low | Court Manager | The building is partially occupied. F3 _ mental impairment, mobile. F6_ two occupants, both blind, would require assistance to evacuate, flat has no ESP insulation around. F10 _ no mobility would require assistance to evacuate, flat has no ESP insulation around. F12_ would require verbal instructions to evacuate, mobile. F13_ would require verbal instructions to evacuate, mobile. F18_ no mobility, would require assistance to evacuate, flat has no ESP insulation around. F21_ two occupants, able to self evac to a relative place of safety. F28_ cluttered flat, KFRS aware safe walk zones within flat. F33_ oxygen usage within property. F53 _ resident requires support to manage a chaotic lifestyle, mental impairment. | n/a
2417 | Thomas Place | THOMASPLAC_S001 | H21 | Scheme | 2022-10-20 18:25 | FRA_2417201020221425.pdf | LingF | 2417201020221420 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | jp7uraz933l9h3ihnu | Medium Risk closed | Risk Closed | 44855.6554 | Obs8 | Measures To Limit Fire Spread And Development | 45219 | Medium | Court Manager | 53 _ occupant appears to latch door slightly ajar this prevents the door closing into frame fully. | Spoke to resident and advised him why this is not safe practice and advised him to ensure his door is shut correctly.
2417 | Thomas Place | THOMASPLAC_S001 | H21 | Scheme | 2022-10-20 18:25 | FRA_2417201020221425.pdf | LingF | 2417201020221420 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | gshkp50j9fpl9h7d4xu | Observation Only | Risk Closed | 44855.6565 | Obs13 | Other Relevant Fixed Systems | NULL | N/A | Court Manager | Service dates | Service dates - all within time.
2417 | Thomas Place | THOMASPLAC_S001 | H21 | Scheme | 2022-10-20 18:25 | FRA_2417201020221425.pdf | LingF | 2417201020221420 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | yu6tgk2i15ol9h3l20e | Observation Only | Risk Closed | 44855.6541 | Obs14 | Access By Emergency Services | NULL | N/A | Court Manager | KFRS are aware of the scheme and general building issues, scheme remains on their high alert register. Scheme manager updates them with occupancy changes. | Continue to update KFRS on a daily basis as to occupancy status
2418 | Minerva House | MINERVAHOUS_S001 | H21 | Scheme | 2022-11-11 15:25 | FRA_2418111120221021.pdf | LingF | 2418111120221020 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | zkmh8ur4mfqlacgd7nx | Observation Only | Risk Open | NULL | Obs1 | The Building | NULL | N/A | Surveyor | Undercroft parking and linked walkway | NULL
2418 | Minerva House | MINERVAHOUS_S001 | H21 | Scheme | 2022-11-11 15:25 | FRA_2418111120221021.pdf | LingF | 2418111120221020 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | iwzvkt6ar89lacd7w28 | Low Risk closed | Risk Closed | 44883.4742 | Obs10 | Fire Safety And Notices | 45607 | Low | Court Manager | Fire action signage not H21 | The signage has been replaced with Housing 21 Logo signage.
2418 | Minerva House | MINERVAHOUS_S001 | H21 | Scheme | 2022-11-11 15:25 | FRA_2418111120221021.pdf | LingF | 2418111120221020 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | j3xdwnmhblacdcgyy | Low Risk closed | Risk Closed | 44901.4946 | Obs8 | Measures To Limit Fire Spread And Development | 45607 | Low | Court Manager | Holes within service riser ceiling 4th floor, fill with intumescent putty or similar fire rated material, note: pink foam not to be used. | OGC attended & fixed 23/11/22
2418 | Minerva House | MINERVAHOUS_S001 | H21 | Scheme | 2022-11-11 15:25 | FRA_2418111120221021.pdf | LingF | 2418111120221020 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | l4hm9kxufyplacgay7o | Observation Only | Risk Open | NULL | Obs1 | The Building | NULL | N/A | Surveyor | General elevation view showing type and location of balconies | NULL
2418 | Minerva House | MINERVAHOUS_S001 | H21 | Scheme | 2022-11-11 15:25 | FRA_2418111120221021.pdf | LingF | 2418111120221020 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | muyuk0y0ffdlacndb5b | Medium Risk closed | Risk Closed | 44908.3997 | Obs8 | Measures To Limit Fire Spread And Development | 45241 | Medium | Court Manager | Discuss with leaseholders and make arrangements to have door closers refitted and operational where these have been disabled. | Surveyor and court manager to visit each flat in January to check every door, and where necessary works orders raised to repair. Letters have been sent to each flat to this effect.
2418 | Minerva House | MINERVAHOUS_S001 | H21 | Scheme | 2022-11-11 15:25 | FRA_2418111120221021.pdf | LingF | 2418111120221020 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | ljln1qu1ilglaccyvbr | Observation Only | Risk Open | NULL | Obs13 | Other Relevant Fixed Systems | NULL | N/A | Surveyor | AOV system | NULL
2418 | Minerva House | MINERVAHOUS_S001 | H21 | Scheme | 2022-11-11 15:25 | FRA_2418111120221021.pdf | LingF | 2418111120221020 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | lye66utsv2laccoh39 | Observation Only | Risk Open | NULL | Obs7 | Fire Protection Measures | NULL | N/A | Surveyor | Single stair building with exits from both grd and 4th floors due to linking walkway to the street. | NULL
2418 | Minerva House | MINERVAHOUS_S001 | H21 | Scheme | 2022-11-11 15:25 | FRA_2418111120221021.pdf | LingF | 2418111120221020 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | pepg01wcjw9laccrt9i | Low Risk closed | Risk Closed | 44908.3981 | Obs8 | Measures To Limit Fire Spread And Development | 45607 | Low | Court Manager | Corridor door closer adj F26 not closing very slower into the frame, allow to adjust to close quicker. | Work order raised. OGC attended. Part required, which has been ordered.
2418 | Minerva House | MINERVAHOUS_S001 | H21 | Scheme | 2022-11-11 15:25 | FRA_2418111120221021.pdf | LingF | 2418111120221020 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | 2zsij8uv15dlacdlb5s | Medium Risk closed | Risk Closed | 44901.4941 | Obs8 | Measures To Limit Fire Spread And Development | 45241 | Medium | Court Manager | Faulty door lock on fire door, unable to be locked shut. Service riser grd & 2nd floors | OGC attended 05/12/22 & fixed
2418 | Minerva House | MINERVAHOUS_S001 | H21 | Scheme | 2022-11-11 15:25 | FRA_2418111120221021.pdf | LingF | 2418111120221020 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | 1m3kk2xodpqlacftrnk | Medium Risk closed | Risk Closed | 44883.4755 | Obs4 | The Occupant - Information Provided By The Court Manager | 45241 | Medium | Court Manager | F15 _ living with complications brought on by advanced cognitive degeneration, gentleman has 3x daily care support visits, CM not informed of what these involve, meals etc or whether gentleman cooks, flat is kept well ordered. Gentleman has been assessed by Social services as able to live independently with support, CM has concerns around this assessment and whether they would respond to a fire within their flat. CM has tried to engage with family members, no support or involement at this stage Agreement for FRS to be advised and a home safety visit arranged. | Referral sent to KFRS to attend home visit for flat 15.
2418 | Minerva House | MINERVAHOUS_S001 | H21 | Scheme | 2022-11-11 15:25 | FRA_2418111120221021.pdf | LingF | 2418111120221020 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | 4sl8ufwd3xalacdu9z1 | Observation Only | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel and zone chart in full operational mode | NULL
2418 | Minerva House | MINERVAHOUS_S001 | H21 | Scheme | 2022-11-11 15:25 | FRA_2418111120221021.pdf | LingF | 2418111120221020 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | f270ps3tysalacevgi1 | Observation Only | Risk Open | NULL | Obs13 | Other Relevant Fixed Systems | NULL | N/A | Surveyor | Powered bin chute protection system, linked to the fire alarm system, in the event of an actuation within the bin room the chute/room will be isolated from the building. | NULL
2420 | Prospect Place | PROSPECTPLAC_S001 | H21 | Scheme | 2022-08-23 09:48 | FRA_2420220820221220.pdf | LingF | 2420220820221220 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | f7qougpk16l74o2wnd | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45160 | Medium | Court Manager | Cars blocking access to fire doors restricting access to fire fight. Change signage to both 'fire door keep clear' and discuss parking restrictions with management company | NULL
2420 | Prospect Place | PROSPECTPLAC_S001 | H21 | Scheme | 2022-08-23 09:48 | FRA_2420220820221220.pdf | LingF | 2420220820221220 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | atpxkld7q3bl74o2wge | Low Risk to be actioned | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | 45526 | Low | Court Manager | Fire alarm system does not have MCP or test points on each floor, CM can only test on thenGRD floor where there are call points. System is tested 6monthly by service contractor who tests each floor, CM to ensure service contractor tests each floor and random flats on each floor. Service contractor have raised concerns about the system design, this is being investigated. | NULL
2420 | Prospect Place | PROSPECTPLAC_S001 | H21 | Scheme | 2022-08-23 09:48 | FRA_2420220820221220.pdf | LingF | 2420220820221220 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | 9uilj123axvl74o2wkc | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45526 | Low | Court Manager | CM to ensure dryer filters are cleaned frequently | NULL
2420 | Prospect Place | PROSPECTPLAC_S001 | H21 | Scheme | 2022-08-23 09:48 | FRA_2420220820221220.pdf | LingF | 2420220820221220 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | 40pwbck8gt1l74o2wht | Observation Only | Risk Closed | 44854.7683 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel in full operational mode | Info
2420 | Prospect Place | PROSPECTPLAC_S001 | H21 | Scheme | 2022-08-23 09:48 | FRA_2420220820221220.pdf | LingF | 2420220820221220 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | 6bgfy197x7gl74o2we1 | Observation Only | Risk Closed | 44854.7683 | Obs1 | The Building | NULL | N/A | Surveyor | External facade showing balcony structures | Info
2420 | Prospect Place | PROSPECTPLAC_S001 | H21 | Scheme | 2022-08-23 09:48 | FRA_2420220820221220.pdf | LingF | 2420220820221220 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | 2vculyk155il74o2wpb | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45160 | Medium | Court Manager | Broken drop down fire bar outer binroom door | NULL
2420 | Prospect Place | PROSPECTPLAC_S001 | H21 | Scheme | 2022-08-23 09:48 | FRA_2420220820221220.pdf | LingF | 2420220820221220 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | 2n34hp6rf6ql74o2wdg | Observation Only | Risk Closed | 44854.7687 | Obs1 | The Building | NULL | N/A | Surveyor | Large 1st floor balcony garden area. | Info
2420 | Prospect Place | PROSPECTPLAC_S001 | H21 | Scheme | 2022-08-23 09:48 | FRA_2420220820221220.pdf | LingF | 2420220820221220 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | qhbgywiywol74o2wqz | Low Risk to be actioned | Risk Open | NULL | Obs12 | Automatic Fire Systems i.e. Suppression System | 45526 | Low | Court Manager | Check operation of the fire shutter, in fault showing | NULL
2420 | Prospect Place | PROSPECTPLAC_S001 | H21 | Scheme | 2022-08-23 09:48 | FRA_2420220820221220.pdf | LingF | 2420220820221220 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | qd2s9htcncfl74o2wfe | Observation Only | Risk Closed | 44854.7686 | Obs1 | The Building | NULL | N/A | Surveyor | General elevation view | Info
2420 | Prospect Place | PROSPECTPLAC_S001 | H21 | Scheme | 2022-08-23 09:48 | FRA_2420220820221220.pdf | LingF | 2420220820221220 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | ojebzv8j3o8l74o2wte | Observation Only | Risk Open | NULL | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | No record of fire safety training record within fire folder last training recieved 1/2021. | NULL
2420 | Prospect Place | PROSPECTPLAC_S001 | H21 | Scheme | 2022-08-23 09:48 | FRA_2420220820221220.pdf | LingF | 2420220820221220 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | nazvdxiwvjll74o2wub | Observation Only | Risk Open | NULL | Obs16 | Testing And Maintenance | NULL | N/A | Court Manager | Dry riser _ 10/8/21 Catering equipment deep clean _ 29/4/21 Lightening protection _ 13/6/22 AOV _ 1/6/22 GAS _ 5/8/22 PAT _ 3/3/21 | NULL
2420 | Prospect Place | PROSPECTPLAC_S001 | H21 | Scheme | 2022-08-23 09:48 | FRA_2420220820221220.pdf | LingF | 2420220820221220 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | nbp5kv9zqtal74o2wpz | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45160 | Medium | Court Manager | Doors from main foyer to lift poorly fitting meeting edge and bottom | NULL
2420 | Prospect Place | PROSPECTPLAC_S001 | H21 | Scheme | 2022-08-23 09:48 | FRA_2420220820221220.pdf | LingF | 2420220820221220 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | t3w31sbugrgl74o2wer | Observation Only | Risk Closed | 44854.7682 | Obs1 | The Building | NULL | N/A | Surveyor | External facade showing investigation detailing render system on to concrete block walls | Info
2420 | Prospect Place | PROSPECTPLAC_S001 | H21 | Scheme | 2022-08-23 09:48 | FRA_2420220820221220.pdf | LingF | 2420220820221220 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | tj3f2qhadotl74o2wsm | Observation Only | Risk Closed | 44854.7688 | Obs15 | Management Of Fire Safety | NULL | N/A | Surveyor | Elighting _ 3/8/22 Alarms _ 17/8/22 FFE _ 3/8/22 Doors _ 3/8/22 Training _ 15/1/21 | Info
2420 | Prospect Place | PROSPECTPLAC_S001 | H21 | Scheme | 2022-08-23 09:48 | FRA_2420220820221220.pdf | LingF | 2420220820221220 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | tps7d9hcmhl74o2wcp | Low Risk closed | Risk Closed | 44854.7684 | Obs1 | The Building | 45526 | Low | Surveyor | HPL CLADDING SYTEM | Info
2420 | Prospect Place | PROSPECTPLAC_S001 | H21 | Scheme | 2022-08-23 09:48 | FRA_2420220820221220.pdf | LingF | 2420220820221220 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | ttz7q14dwlil74o2wmr | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45160 | Medium | Court Manager | F35 _ close down gap along front door bottom edge | NULL
2420 | Prospect Place | PROSPECTPLAC_S001 | H21 | Scheme | 2022-08-23 09:48 | FRA_2420220820221220.pdf | LingF | 2420220820221220 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | qzi2n168xxgl74o2wv2 | Medium Risk to be actioned | Risk Open | NULL | Obs16 | Testing And Maintenance | 45160 | Medium | Court Manager | Test regime required for refuge call point when alarm tested | NULL
2420 | Prospect Place | PROSPECTPLAC_S001 | H21 | Scheme | 2022-08-23 09:48 | FRA_2420220820221220.pdf | LingF | 2420220820221220 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | ghx6ruyh8del74ocd9h | Observation Only | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | NULL | N/A | Court Manager | General note _ record evac training with external companies providing a service at Prospect place. (catering, czre and hair salon) | NULL
2420 | Prospect Place | PROSPECTPLAC_S001 | H21 | Scheme | 2022-08-23 09:48 | FRA_2420220820221220.pdf | LingF | 2420220820221220 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | h9eu7553hgl74o2wlh | Observation Only | Risk Closed | 44854.7681 | Obs7 | Fire Protection Measures | NULL | N/A | Surveyor | General note _ scheme has undergone a comprehensive passive fire upgrade works throughout the property to address poorly fitting doors and passive fire stopping | Info
2420 | Prospect Place | PROSPECTPLAC_S001 | H21 | Scheme | 2022-08-23 09:48 | FRA_2420220820221220.pdf | LingF | 2420220820221220 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | fqlwr397tk6l74o2wo3 | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45160 | Medium | Court Manager | Fire stopping (collars and ablative board) required around Service penetrations passing through concrete slab ceiling within undercroft car paking area. To match adjacent ceiling on neighbour block | NULL
2420 | Prospect Place | PROSPECTPLAC_S001 | H21 | Scheme | 2022-08-23 09:48 | FRA_2420220820221220.pdf | LingF | 2420220820221220 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | fm4lu5y2xa7l74o2wj0 | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | F6_ smoker, understands risk associated, wheel chair user unable to propel, FRS aware and have provided smoking safety aids, carpet and fabric treatment. F14_ unable to propel in wheelchair, has family assistance during the day. F52_ smoker, poor mobility, FRS aware and have provided aids. | NULL
2420 | Prospect Place | PROSPECTPLAC_S001 | H21 | Scheme | 2022-08-23 09:48 | FRA_2420220820221220.pdf | LingF | 2420220820221220 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | furqcqsl76ll74ofz01 | Observation Only | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Discuss measures to undertake PAT testing of scooters Sockets within scooter room are time controlled. | NULL
2420 | Prospect Place | PROSPECTPLAC_S001 | H21 | Scheme | 2022-08-23 09:48 | FRA_2420220820221220.pdf | LingF | 2420220820221220 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | g7jw4cwa70al74o2wom | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45160 | Medium | Court Manager | Broken freeswing Door closer, inner bin room door. | NULL
2420 | Prospect Place | PROSPECTPLAC_S001 | H21 | Scheme | 2022-08-23 09:48 | FRA_2420220820221220.pdf | LingF | 2420220820221220 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | xizn6ypqtnel74o2wc3 | Observation Only | Risk Closed | 44854.7685 | Obs1 | The Building | NULL | N/A | Surveyor | Refuge points on each landing | Info
2420 | Prospect Place | PROSPECTPLAC_S001 | H21 | Scheme | 2022-08-23 09:48 | FRA_2420220820221220.pdf | LingF | 2420220820221220 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | y48j08yqq2dl74o2wm2 | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45160 | Medium | Court Manager | Manage locations of chairs on mezzanine level, ensure they don't restrict fire doors | NULL
2425 | Newport Court | NEWPORT_S001 | H21 | Scheme | 2022-05-25 20:41 | FRA_2425250520222030.pdf | LingF | 2425250520222030 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | y4ygwxjo6rql3lzdtqn | Observation Only | Risk Closed | 44763.4692 | Obs15 | Management Of Fire Safety | NULL | N/A | Surveyor | KFRS undertook fire safety audit 21/4/2022. Minor items noted no enforcement or immediate actions required. | Info
2425 | Newport Court | NEWPORT_S001 | H21 | Scheme | 2022-05-25 20:41 | FRA_2425250520222030.pdf | LingF | 2425250520222030 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | yaba14atkael3lzdtps | Observation Only | Risk Closed | 44763.4689 | Obs14 | Access By Emergency Services | NULL | N/A | Surveyor | FRS recently undertaken scheme fire audit | Info
2425 | Newport Court | NEWPORT_S001 | H21 | Scheme | 2022-05-25 20:41 | FRA_2425250520222030.pdf | LingF | 2425250520222030 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | nh5cgiu8y5l3lzdtly | Medium Risk closed | Risk Closed | 44728.5164 | Obs8 | Measures To Limit Fire Spread And Development | 45071 | Medium | Court Manager | F21 _ Refix door closer or swap with a free swing | Door closure refixed by handy person job completed 16/06/22
2425 | Newport Court | NEWPORT_S001 | H21 | Scheme | 2022-05-25 20:41 | FRA_2425250520222030.pdf | LingF | 2425250520222030 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | qoshz5opjul3lzdtmk | Observation Only | Risk Closed | 44763.4693 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Surveyor | Manual opening vents on corridors for horizontal circulation | Info
2425 | Newport Court | NEWPORT_S001 | H21 | Scheme | 2022-05-25 20:41 | FRA_2425250520222030.pdf | LingF | 2425250520222030 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | oye7hyfcm1l3lzdtor | Low Risk closed | Risk Closed | 44707.4367 | Obs9 | Escape Lighting | 45437 | Low | Court Manager | FRS have been identified the low level of Elighting on upper porch ways. There is a degree of borrowed light through large glazed screens. Installation of lights to be programmed into SIP | To be programmed in to the next SIP
2425 | Newport Court | NEWPORT_S001 | H21 | Scheme | 2022-05-25 20:41 | FRA_2425250520222030.pdf | LingF | 2425250520222030 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | 1ysn7mammbcl3lzdtio | Observation Only | Risk Closed | 44763.4691 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Panel and zone chart in full operational mode | Info
2425 | Newport Court | NEWPORT_S001 | H21 | Scheme | 2022-05-25 20:41 | FRA_2425250520222030.pdf | LingF | 2425250520222030 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | 0sqyuvjm8p1hl3lzdtkb | Observation Only | Risk Closed | 44707.4373 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | 54 _ not able to mobilise, care staff 3 visits/day. Resident does not cook, flat is not cluttered but required to be kept tidy. Non smoker, heavy drinker. PCFRA completed. 41 _ slow walker, unsteady on feet, uses ready meals doesn't cook, can evac in event of a fire, flat is clear and tidy. | PCFRA completed and fire box updated to be reviewed regularly
2425 | Newport Court | NEWPORT_S001 | H21 | Scheme | 2022-05-25 20:41 | FRA_2425250520222030.pdf | LingF | 2425250520222030 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | 6ry2xjj0qqml3lzdtnt | Low Risk closed | Risk Closed | 44707.4381 | Obs8 | Measures To Limit Fire Spread And Development | 45437 | Low | Court Manager | Motorized scooter on external walkway, restricted exit point from adjacent flat and flats on 1st floor | buggy/ scooter store programmed in to SIP
2425 | Newport Court | NEWPORT_S001 | H21 | Scheme | 2022-05-25 20:41 | FRA_2425250520222030.pdf | LingF | 2425250520222030 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | dpj4r14tuhol3lzdtl3 | Observation Only | Risk Closed | 44763.469 | Obs7 | Fire Protection Measures | NULL | N/A | Surveyor | Scheme designed around individual stair cases serving four flats, hence the high number andnlow number of exit doors. Exit doors are located within the communal areas. | Info
2425 | Newport Court | NEWPORT_S001 | H21 | Scheme | 2022-05-25 20:41 | FRA_2425250520222030.pdf | LingF | 2425250520222030 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | dr5hh2k2fool3lzdtjf | Observation Only | Risk Closed | 44763.4692 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Zone chart | Info
2425 | Newport Court | NEWPORT_S001 | H21 | Scheme | 2022-05-25 20:41 | FRA_2425250520222030.pdf | LingF | 2425250520222030 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | dfrn0jxx867l3lzdtn6 | Low Risk closed | Risk Closed | 44707.4406 | Obs8 | Measures To Limit Fire Spread And Development | 45437 | Low | Court Manager | Fire stopping around pipes required within bin room, 2 points | 1536687 work order completed on 9th May 22
2426 | Countess Mountbatten Court | COUNTESSMOUN_S001 | H21 | Scheme | 2022-06-14 13:34 | FRA_2426140620221326.pdf | LingF | 2426140620221320 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | f3b5s1fl3yol4e52bay | Observation Only | Risk Closed | 44746.4005 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | F18: poor mobility, would self evac to a relative place of safety, does not pose a high risk due to personal circumstances. F10: personal circumstances raises additional risks, has 2x care visits/day, does not cook however CM looking at measures to isolate, FRS aware have undertaken home safety visits, non smoker. F25: Poor mobility, would need assistance to leave the building but could leave flat unassisted. F13: incident of cooking related activation, occupant is being supported by H21. | All okay and listed with PCFRA .
2426 | Countess Mountbatten Court | COUNTESSMOUN_S001 | H21 | Scheme | 2022-06-14 13:34 | FRA_2426140620221326.pdf | LingF | 2426140620221320 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | beax75pp9m9l4e52bf5 | Observation Only | Risk Closed | 44763.4695 | Obs9 | Escape Lighting | NULL | N/A | Surveyor | Lightening to good levels throughout building | Info
2426 | Countess Mountbatten Court | COUNTESSMOUN_S001 | H21 | Scheme | 2022-06-14 13:34 | FRA_2426140620221326.pdf | LingF | 2426140620221320 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | rir724u6uh7l4e52bcn | Observation Only | Risk Closed | 44790.4555 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Court Manager | Investigate makeup of screens around 1st floor corridor doors, make up to be determined | Frank was happy with work , to be closed down
2426 | Countess Mountbatten Court | COUNTESSMOUN_S001 | H21 | Scheme | 2022-06-14 13:34 | FRA_2426140620221326.pdf | LingF | 2426140620221320 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | g6kjc4t5eirl4e52ba7 | Observation Only | Risk Closed | 44763.4696 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel and zone chart | Info
2426 | Countess Mountbatten Court | COUNTESSMOUN_S001 | H21 | Scheme | 2022-06-14 13:34 | FRA_2426140620221326.pdf | LingF | 2426140620221320 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | gvalz52ppt9l4e52bd0 | Observation Only | Risk Closed | 44756.4007 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Court Manager | CM has raised an order to address issues above grd floor doors, to be followed up with contractor | All work now completed.
2426 | Countess Mountbatten Court | COUNTESSMOUN_S001 | H21 | Scheme | 2022-06-14 13:34 | FRA_2426140620221326.pdf | LingF | 2426140620221320 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | iend4cop96l4e52bdd | Low Risk closed | Risk Closed | 44750.6513 | Obs8 | Measures To Limit Fire Spread And Development | 45457 | Low | Court Manager | Replace smoke seals within lounge doors to be combined fire and cold smoke | All completed and replaced with smoke seals .
2426 | Countess Mountbatten Court | COUNTESSMOUN_S001 | H21 | Scheme | 2022-06-14 13:34 | FRA_2426140620221326.pdf | LingF | 2426140620221320 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | jxrbvcgjjmkl4e52be9 | Low Risk closed | Risk Closed | 44756.4005 | Obs8 | Measures To Limit Fire Spread And Development | 45457 | Low | Court Manager | Stair door opp F12, repair required to smoke bar preventing door closing fully | Repaired , door bar was bit loose but tightened up .
2426 | Countess Mountbatten Court | COUNTESSMOUN_S001 | H21 | Scheme | 2022-06-14 13:34 | FRA_2426140620221326.pdf | LingF | 2426140620221320 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | jrq3py6kd6rl4e52bc7 | Observation Only | Risk Closed | 44763.4694 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Surveyor | Each corridor compartment has an MOV | Info
2426 | Countess Mountbatten Court | COUNTESSMOUN_S001 | H21 | Scheme | 2022-06-14 13:34 | FRA_2426140620221326.pdf | LingF | 2426140620221320 | Retirement Housing | London Kent | Kent North | South | South Patch 3 | xpw74td6bml4e52bbm | Observation Only | Risk Closed | 44746.4009 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Garden store grd floor, CM monitoring objects being stored and has access at all times. | All okay , no concerns
2429 | Charles Lister Court | CHARLESLIST_S001 | H21 | Scheme | 2022-08-30 16:11 | FRA_2429300820221609.pdf | LingF | 2429300820221600 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | w4kmfrb6cgjl7gbs4mc | Low Risk closed | Risk Closed | 44804.3377 | Obs8 | Measures To Limit Fire Spread And Development | 45534 | Low | Court Manager | Cross corridor doors adj F23 not closing into frame fully | works order raised with the handy person for this work to be completed
2429 | Charles Lister Court | CHARLESLIST_S001 | H21 | Scheme | 2022-08-30 16:11 | FRA_2429300820221609.pdf | LingF | 2429300820221600 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | z7r2lblciejl7gbs4ji | Low Risk closed | Risk Closed | 44804.486 | Obs2 | Means Of Giving Warning In Case Of Fire | 45534 | Low | Court Manager | F41 _ suffering with hearinf loss unable to hear fire alarm | Person centred fire risk assessment completed
2429 | Charles Lister Court | CHARLESLIST_S001 | H21 | Scheme | 2022-08-30 16:11 | FRA_2429300820221609.pdf | LingF | 2429300820221600 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | ra35fhvad6nl7gbs4k9 | Observation Only | Risk Closed | 44854.7693 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel in full operational mode | Info
2429 | Charles Lister Court | CHARLESLIST_S001 | H21 | Scheme | 2022-08-30 16:11 | FRA_2429300820221609.pdf | LingF | 2429300820221600 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | s1evzphsjabl7gbs4le | Observation Only | Risk Closed | 44804.3372 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | F39 _ reduced mobility would require assistance to evacuate F7 _ reduced mobility would require assistance to evacuate | Person Centred Fire Risk assessments completed on both residents . Regular visits from the fire service to flat 39 as he is a smoker
2429 | Charles Lister Court | CHARLESLIST_S001 | H21 | Scheme | 2022-08-30 16:11 | FRA_2429300820221609.pdf | LingF | 2429300820221600 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | 6ybh4w97pxtl7gbs4if | Observation Only | Risk Closed | 44854.7692 | Obs1 | The Building | NULL | N/A | Surveyor | General elevation view showing extent of cladding | Info
2430 | Gerald Palmby Court | GERALDPALM_S001 | H21 | Scheme | 2022-01-17 14:57 | FRA_2430170120221450.pdf | LingF | 2430170120221450 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | 2xbep90ang7kyit0gpe | Observation Only | Risk Closed | 44578.6556 | Obs1 | The Building | NULL | N/A | Surveyor | General elevation view, construction method and roof type | Info only
2430 | Gerald Palmby Court | GERALDPALM_S001 | H21 | Scheme | 2022-01-17 14:57 | FRA_2430170120221450.pdf | LingF | 2430170120221450 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | 3t8pinnlofgkyit2dfo | Observation Only | Risk Closed | 44578.6554 | Obs16 | Testing And Maintenance | NULL | N/A | Surveyor | AOV _ 12/2021 GAS _ 9/2021 FAT _ 6/2021 5YR HARD WIRE _ 11/2019 | Info only
2430 | Gerald Palmby Court | GERALDPALM_S001 | H21 | Scheme | 2022-01-17 14:57 | FRA_2430170120221450.pdf | LingF | 2430170120221450 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | 9yqid2nj58ukyit0gtm | Low Risk closed | Risk Closed | 44579.4387 | Obs7 | Fire Protection Measures | 45308 | Low | Court Manager | Ensure all riser cupboards remain locked noted as unlocked and open in a number of locations. | Cupboards have been locked.
2430 | Gerald Palmby Court | GERALDPALM_S001 | H21 | Scheme | 2022-01-17 14:57 | FRA_2430170120221450.pdf | LingF | 2430170120221450 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | dbcnhtfvthlkyit0grv | Observation Only | Risk Closed | 44578.6557 | Obs5 | Evacuation Strategy And Training | NULL | N/A | Surveyor | F27 idetified as a responsible tenant to silence the alarms following FRS attendance and authorisation | Info only
2430 | Gerald Palmby Court | GERALDPALM_S001 | H21 | Scheme | 2022-01-17 14:57 | FRA_2430170120221450.pdf | LingF | 2430170120221450 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | rzyzaz71tnfkyit0gu6 | Medium Risk closed | Risk Closed | 44579.4753 | Obs7 | Fire Protection Measures | 44943 | Medium | Court Manager | Water damaged fire door, riser duct, adj F11. Replace to meet requirements of FD30s nominal fire door. | Order raised with OGC on the 18th January 2022 - marked as urgent 7 day response Order no: 1513140
2430 | Gerald Palmby Court | GERALDPALM_S001 | H21 | Scheme | 2022-01-17 14:57 | FRA_2430170120221450.pdf | LingF | 2430170120221450 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | smk5qp6eax8kyit0gr3 | Observation Only | Risk Closed | 44578.6558 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Surveyor | F13 _ Poor mobility able to evac from flat to a relative place of safety, idetified as a hoarder. F17 _ additional support provided by KFRS due to poor hearing. | Info only
2430 | Gerald Palmby Court | GERALDPALM_S001 | H21 | Scheme | 2022-01-17 14:57 | FRA_2430170120221450.pdf | LingF | 2430170120221450 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | p4tcaraywtkyit0gqc | Observation Only | Risk Closed | 44578.656 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel and zone chart | Info only
2430 | Gerald Palmby Court | GERALDPALM_S001 | H21 | Scheme | 2022-01-17 14:57 | FRA_2430170120221450.pdf | LingF | 2430170120221450 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | js8twzd2jikyit0gv0 | Observation Only | Risk Closed | 44578.6559 | Obs13 | Other Relevant Fixed Systems | NULL | N/A | Surveyor | Style of AOV | Info only
2430 | Gerald Palmby Court | GERALDPALM_S001 | H21 | Scheme | 2022-01-17 14:57 | FRA_2430170120221450.pdf | LingF | 2430170120221450 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | fhxss4iimvjkyit0gsp | Medium Risk closed | Risk Closed | 44579.4758 | Obs7 | Fire Protection Measures | 44943 | Medium | Court Manager | Refix door holder adj F37 | Order raised and completed with Paul Handyman on the 18.01.2022 order no: 1513136
2433 | Irene Astor Court | IRENEASTO_S001 | H21 | Scheme | 2022-05-25 20:30 | FRA_2433250520222020.pdf | LingF | 2433250520222020 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | l54ljnabwaal3lz18l5 | Observation Only | Risk Closed | 44763.4688 | Obs1 | The Building | NULL | N/A | Surveyor | General elevation view | Info
2433 | Irene Astor Court | IRENEASTO_S001 | H21 | Scheme | 2022-05-25 20:30 | FRA_2433250520222020.pdf | LingF | 2433250520222020 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | p29ru6d46l9l3lz18ly | Observation Only | Risk Closed | 44763.4687 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel and zone chart | Info
2433 | Irene Astor Court | IRENEASTO_S001 | H21 | Scheme | 2022-05-25 20:30 | FRA_2433250520222020.pdf | LingF | 2433250520222020 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | tpbg5uibtml3lz18qp | Observation Only | Risk Closed | 44763.4689 | Obs13 | Other Relevant Fixed Systems | NULL | N/A | Surveyor | Chain operated AOV system covering entrance foyers on each floor and stairwell | Info
2433 | Irene Astor Court | IRENEASTO_S001 | H21 | Scheme | 2022-05-25 20:30 | FRA_2433250520222020.pdf | LingF | 2433250520222020 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | a1fvxcosekml3lz18mq | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | F2/10 _ Both wheel chair user can self evac to a relative place of safety. F29_ partially blind can self evac. F16 _ early stages of hoarding tendencies, CM working with occupant to reduce fire load | NULL
2433 | Irene Astor Court | IRENEASTO_S001 | H21 | Scheme | 2022-05-25 20:30 | FRA_2433250520222020.pdf | LingF | 2433250520222020 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | 0dlouy54k19l3lz18rm | Low Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45437 | Low | Court Manager | CM to update fire training following period of absence. | NULL
2433 | Irene Astor Court | IRENEASTO_S001 | H21 | Scheme | 2022-05-25 20:30 | FRA_2433250520222020.pdf | LingF | 2433250520222020 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | uxpcqsk8gml3lz18nf | Observation Only | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | NULL | N/A | Court Manager | CM to ensure new residents are aware of fire evac procedures | NULL
2433 | Irene Astor Court | IRENEASTO_S001 | H21 | Scheme | 2022-05-25 20:30 | FRA_2433250520222020.pdf | LingF | 2433250520222020 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | xvah89lqy2l3lz18pp | Medium Risk closed | Risk Closed | 44795.3687 | Obs9 | Escape Lighting | 45071 | Medium | Court Manager | CM reported a number of Elights are not operational when undertaking testing _ record locations and order repairs accordingly | All batteries replaced by Openview 29/07/22.
2433 | Irene Astor Court | IRENEASTO_S001 | H21 | Scheme | 2022-05-25 20:30 | FRA_2433250520222020.pdf | LingF | 2433250520222020 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | xeckhzuyk6fl3lz18oz | Medium Risk closed | Risk Closed | 44838.3709 | Obs8 | Measures To Limit Fire Spread And Development | 45071 | Medium | Court Manager | F16_ ease adjust door to ensure fully closing into frame fully | WO 1557590 raised to ease and adjust front door which has now been completed.
2433 | Irene Astor Court | IRENEASTO_S001 | H21 | Scheme | 2022-05-25 20:30 | FRA_2433250520222020.pdf | LingF | 2433250520222020 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | x9lktllsvvil3lz18oe | Medium Risk closed | Risk Closed | 44813.5764 | Obs8 | Measures To Limit Fire Spread And Development | 45071 | Medium | Court Manager | F25 replace closer, ease adjust door to ensure closing | Raised repair to OGC (wo 1557611) to ease and adjust door. A door seal brush was removed from the bottom of the door. Door closes as it should. Door closer operational.
2434 | Fitzwalter Court | FITZWALTER_S001 | H21 | Scheme | 2022-09-15 09:11 | FRA_2434140920220947.pdf | LingF | 2434140920220940 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | 03gl0il4vhzrl81joz37 | Observation Only | Risk Closed | 44854.7694 | Obs1 | The Building | NULL | N/A | Surveyor | General elevation view showing extent of cladding panels forming bay windows less than | Info
2434 | Fitzwalter Court | FITZWALTER_S001 | H21 | Scheme | 2022-09-15 09:11 | FRA_2434140920220947.pdf | LingF | 2434140920220940 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | dodp7kre0qkl81jq3l3 | Observation Only | Risk Closed | 44854.7694 | Obs1 | The Building | NULL | N/A | Surveyor | General elevation of linked detached 3bed property located above communal lounge. | Info
2434 | Fitzwalter Court | FITZWALTER_S001 | H21 | Scheme | 2022-09-15 09:11 | FRA_2434140920220947.pdf | LingF | 2434140920220940 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | rsfgi1xoll81dyn96 | Observation Only | Risk Closed | 44858.5547 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | F1_ unable to use stairs can evac to relative place of safety. F20_ unable to open door due to closer, possible free swing closer required. Doesn't cook, support from family. F25_ frail able to self evac to a relative place of safety F29_ frail, able to self evac to a relative place of safety, smoker no evidence of safeguarding prompts. | W/O 1568827 raised for a Free swing closer to be added to Flat 20.
2434 | Fitzwalter Court | FITZWALTER_S001 | H21 | Scheme | 2022-09-15 09:11 | FRA_2434140920220947.pdf | LingF | 2434140920220940 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | rfmmjbmbd2rl81hvr2l | Low Risk closed | Risk Closed | 44844.3556 | Obs8 | Measures To Limit Fire Spread And Development | 45549 | Low | Court Manager | 25_ intumescent strip missing flat door 22 _ intu brush strip along bottom of flat door. 29 _ ease adjust lock to allow full closing | Works completed.
2434 | Fitzwalter Court | FITZWALTER_S001 | H21 | Scheme | 2022-09-15 09:11 | FRA_2434140920220947.pdf | LingF | 2434140920220940 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | jeayqwfvnfol81e8ljc | Observation Only | Risk Closed | 44854.7695 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel in full operational mode | Info
2434 | Fitzwalter Court | FITZWALTER_S001 | H21 | Scheme | 2022-09-15 09:11 | FRA_2434140920220947.pdf | LingF | 2434140920220940 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | igl2kj7lewol81eizaz | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45549 | Low | Court Manager | Improve fire stopping around cables within cleaners cupboard _ use envirograf intumescent collar to bunch cables, remove the plate on the ceiling, rake out existing use an intumescent putty to point up around. | NULL
2450 | Chamberlain Manor | CHAMBERLAINMAN_S001 | H21 | Scheme | 2022-03-09 16:27 | FRA_2450090320221430.pdf | LingF | 2450090320221430 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | i3c3av4hnirl0jnr4g4 | Low Risk closed | Risk Closed | 44722.3931 | Obs2 | Means Of Giving Warning In Case Of Fire | 45360 | Low | Court Manager | Additional fire box and residents profile information required at 2nd panel | Fire box now installed
2450 | Chamberlain Manor | CHAMBERLAINMAN_S001 | H21 | Scheme | 2022-03-09 16:27 | FRA_2450090320221430.pdf | LingF | 2450090320221430 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | g714534rypil0jnr4hs | Low Risk closed | Risk Closed | 44699.6259 | Obs8 | Measures To Limit Fire Spread And Development | 45360 | Low | Court Manager | Close down gaps on cross corridor doors adj staff guestroom possible use of extended brush strips | packed hinges to reduce gap work completed by handyperson
2450 | Chamberlain Manor | CHAMBERLAINMAN_S001 | H21 | Scheme | 2022-03-09 16:27 | FRA_2450090320221430.pdf | LingF | 2450090320221430 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | jpxekw80zmjl0jnr4f1 | Observation Only | Risk Closed | 44763.4678 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel and alarm zone chart panel in full working order | Info
2450 | Chamberlain Manor | CHAMBERLAINMAN_S001 | H21 | Scheme | 2022-03-09 16:27 | FRA_2450090320221430.pdf | LingF | 2450090320221430 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | jter6obgybal0jnr4jh | Observation Only | Risk Closed | 44763.4653 | Obs11 | Fire Fighting Equipment | NULL | N/A | Surveyor | FFE provided in accordance to H21 standard installed guide, protection of critical areas only. | Info
2450 | Chamberlain Manor | CHAMBERLAINMAN_S001 | H21 | Scheme | 2022-03-09 16:27 | FRA_2450090320221430.pdf | LingF | 2450090320221430 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | lpew0q0aull0jnrd27 | Observation Only | Risk Closed | 44763.465 | Obs1 | The Building | NULL | N/A | Surveyor | Main entrance showing extent of cladding panels forming bay windows, design is typical of each elevation | Info
2450 | Chamberlain Manor | CHAMBERLAINMAN_S001 | H21 | Scheme | 2022-03-09 16:27 | FRA_2450090320221430.pdf | LingF | 2450090320221430 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | tajuxpup96bl0jnr4ii | Low Risk closed | Risk Closed | 44789.6326 | Obs8 | Measures To Limit Fire Spread And Development | 45360 | Low | Court Manager | Close down gaps on cross corridor adj F32, along bottom of the door | Drop down smoke seals installed to double doors and operational
2450 | Chamberlain Manor | CHAMBERLAINMAN_S001 | H21 | Scheme | 2022-03-09 16:27 | FRA_2450090320221430.pdf | LingF | 2450090320221430 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | q45c5e73ml9l0jnr4he | Observation Only | Risk Closed | 44763.4676 | Obs7 | Fire Protection Measures | NULL | N/A | Surveyor | Stairwells have been designated as refuge points with a speech module linked to the warden call system | Info
2450 | Chamberlain Manor | CHAMBERLAINMAN_S001 | H21 | Scheme | 2022-03-09 16:27 | FRA_2450090320221430.pdf | LingF | 2450090320221430 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | nr1wrdug3dml0jnr4kr | Observation Only | Risk Closed | 44677.5162 | Obs16 | Testing And Maintenance | NULL | N/A | Court Manager | Catering equip: 9/2021 _ GAS: 3/2021 Extract system: 9/2021 Air con units: 2/1/22 Solar panels: Lightening protection: 6/2021 Dry riser: 2/3/22 AOV: 8/2021 GAS: 6/2021 HARD WIRE: 11/2020 | All in within due dates
2450 | Chamberlain Manor | CHAMBERLAINMAN_S001 | H21 | Scheme | 2022-03-09 16:27 | FRA_2450090320221430.pdf | LingF | 2450090320221430 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | bnbh9s5ju09l0jnr4kg | Low Risk closed | Risk Closed | 44685.4841 | Obs15 | Management Of Fire Safety | 45360 | Low | Court Manager | During fire safety meeting residents questioned whether people would remain in their flats, possible reinforced message on court news letter | Stay put policy issued as a reminder as discussed in May newsletter.
2450 | Chamberlain Manor | CHAMBERLAINMAN_S001 | H21 | Scheme | 2022-03-09 16:27 | FRA_2450090320221430.pdf | LingF | 2450090320221430 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | 89q0fw75kwl0jnr4i6 | Low Risk closed | Risk Closed | 44699.6253 | Obs8 | Measures To Limit Fire Spread And Development | 45360 | Low | Court Manager | Close down gaps on cross corridor adj F3 | Packed out hinges completed by handyperson
2450 | Chamberlain Manor | CHAMBERLAINMAN_S001 | H21 | Scheme | 2022-03-09 16:27 | FRA_2450090320221430.pdf | LingF | 2450090320221430 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | 8e4qjg6eatwl0jnr4k4 | Observation Only | Risk Closed | 44763.4651 | Obs13 | Other Relevant Fixed Systems | NULL | N/A | Surveyor | Example of AOV system | Info
2450 | Chamberlain Manor | CHAMBERLAINMAN_S001 | H21 | Scheme | 2022-03-09 16:27 | FRA_2450090320221430.pdf | LingF | 2450090320221430 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | 0grzz4ibw8s7l0jnr4j4 | Low Risk closed | Risk Closed | 44699.6239 | Obs8 | Measures To Limit Fire Spread And Development | 45360 | Low | Court Manager | Close down gaps along bottom of stairwell door adj F27. | Completed by Handyperson
2450 | Chamberlain Manor | CHAMBERLAINMAN_S001 | H21 | Scheme | 2022-03-09 16:27 | FRA_2450090320221430.pdf | LingF | 2450090320221430 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | 1ul17gihqpfl0jnr4gz | Low Risk closed | Risk Closed | 44671.5055 | Obs6 | Fire Hazards - Elimination & Control | 45360 | Low | Court Manager | Communal irons within laundry room | Queried with H&S Manager, Care team onsite TLeader - LN discussed care staff to regularly check irons are not left on, also advised within court newsletter.
2450 | Chamberlain Manor | CHAMBERLAINMAN_S001 | H21 | Scheme | 2022-03-09 16:27 | FRA_2450090320221430.pdf | LingF | 2450090320221430 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | 6xnjerc5jdil0jnr4fd | Observation Only | Risk Closed | 44763.4675 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Secondary panel | Info
2450 | Chamberlain Manor | CHAMBERLAINMAN_S001 | H21 | Scheme | 2022-03-09 16:27 | FRA_2450090320221430.pdf | LingF | 2450090320221430 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | 7x8wqun4mowl0jnr4gl | Observation Only | Risk Closed | 44671.5043 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | F15, would require assistance to to bed bound has hoist for moving, does not smoke or cook, high care dependent. F28, as above. F29, would require assistance to evacuate, high care dependent. F39, non weight bearing, husband suffers with dementia, both would require full assistance. F45, Age related mental and physical impairment, would support to evac. F50, hoarder has reduced items within the flat supported by the care team. F64, one occupant wouldrequire full assistance if left within property on their own. | Information contained within PCFRA - Update F50 no longer a resident
2450 | Chamberlain Manor | CHAMBERLAINMAN_S001 | H21 | Scheme | 2022-03-09 16:27 | FRA_2450090320221430.pdf | LingF | 2450090320221430 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | wpq41mgsy8l0jnr4js | Observation Only | Risk Closed | 44763.4649 | Obs12 | Automatic Fire Systems i.e. Suppression System | NULL | N/A | Surveyor | Door guard device | Info
2450 | Chamberlain Manor | CHAMBERLAINMAN_S001 | H21 | Scheme | 2022-03-09 16:27 | FRA_2450090320221430.pdf | LingF | 2450090320221430 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | yqxj3n5o1kl0jnr4it | Low Risk closed | Risk Closed | 44699.6267 | Obs8 | Measures To Limit Fire Spread And Development | 45360 | Low | Court Manager | Close down gaps on cross corridor adj F21 | Hinges packed out completed by handyperson
2451 | Quarry House | QUARRYHOUS_S001 | H21 | Scheme | 2022-11-08 15:13 | FRA_2451081120221144.pdf | LingF | 2451081120221140 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | x2oqq3jj9qla86h6ic | Observation Only | Risk Closed | 44876.4314 | Obs13 | Other Relevant Fixed Systems | NULL | N/A | Surveyor | AOV roof vent adj F29 | Information only
2451 | Quarry House | QUARRYHOUS_S001 | H21 | Scheme | 2022-11-08 15:13 | FRA_2451081120221144.pdf | LingF | 2451081120221140 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | wm7cat2v0tla868xpu | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45604 | Low | Court Manager | Metal ventilated grills (2 locations) passing through fire door, establish whether this is a fire rated vent with intumescent strips, if not replace with suitable grill with fire integrity. | NULL
2451 | Quarry House | QUARRYHOUS_S001 | H21 | Scheme | 2022-11-08 15:13 | FRA_2451081120221144.pdf | LingF | 2451081120221140 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | 49oyhtg5a2ola86v8vo | Observation Only | Risk Closed | 44876.4311 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Repeater panel and zone chart located1st floor adj F22 | Information only
2451 | Quarry House | QUARRYHOUS_S001 | H21 | Scheme | 2022-11-08 15:13 | FRA_2451081120221144.pdf | LingF | 2451081120221140 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | 4un619n8kckla87w5g4 | Observation Only | Risk Closed | 44876.4307 | Obs1 | The Building | NULL | N/A | Surveyor | General elevation view | Information only
2451 | Quarry House | QUARRYHOUS_S001 | H21 | Scheme | 2022-11-08 15:13 | FRA_2451081120221144.pdf | LingF | 2451081120221140 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | drn15r7kbola877x07 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45604 | Low | Court Manager | Form 60min fire rated ceiling within TV equipment cupboard adj F17, including sealing around cable penetrations, extend detection onto new ceiling. | NULL
2451 | Quarry House | QUARRYHOUS_S001 | H21 | Scheme | 2022-11-08 15:13 | FRA_2451081120221144.pdf | LingF | 2451081120221140 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | e2dor984ccsla85xvjg | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45604 | Low | Court Manager | Fix fire rated brush strips along bottom of office and kitchen door to close down gapping. Gap should be no more than 5mm. | NULL
2451 | Quarry House | QUARRYHOUS_S001 | H21 | Scheme | 2022-11-08 15:13 | FRA_2451081120221144.pdf | LingF | 2451081120221140 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | nizqob9j15la8ckkvz | Observation Only | Risk Closed | 44876.431 | Obs16 | Testing And Maintenance | NULL | N/A | Surveyor | AOV _ 1/2022 LIGHTENING _ 2/2022 DRY RISER _ 6/2022 FAT/PAT _ 5/2021 | Information only
2451 | Quarry House | QUARRYHOUS_S001 | H21 | Scheme | 2022-11-08 15:13 | FRA_2451081120221144.pdf | LingF | 2451081120221140 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | tbgse6ao158la871xdu | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45238 | Low | Court Manager | Close down gap on cross corridor door, door dosent meet with the intumescent strip. Plant a filler piece onto the door to ensure a close fit | NULL
2451 | Quarry House | QUARRYHOUS_S001 | H21 | Scheme | 2022-11-08 15:13 | FRA_2451081120221144.pdf | LingF | 2451081120221140 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | s3uprxrw16la882kk5 | Observation Only | Risk Closed | 44876.4315 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Main fire panel within main entrance | Information only
2451 | Quarry House | QUARRYHOUS_S001 | H21 | Scheme | 2022-11-08 15:13 | FRA_2451081120221144.pdf | LingF | 2451081120221140 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | jp51bs5zf4la87izq6 | Observation Only | Risk Closed | 44876.4308 | Obs13 | Other Relevant Fixed Systems | NULL | N/A | Surveyor | Typical Horizontal smoke vents on internal corridors | Information only
2451 | Quarry House | QUARRYHOUS_S001 | H21 | Scheme | 2022-11-08 15:13 | FRA_2451081120221144.pdf | LingF | 2451081120221140 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | jh9hj0l260ela85c67g | Observation Only | Risk Closed | 44883.4593 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | F3 _ Bed bound, not able to mobilise, non smoker non cooking, high care dependent. F26 _ High care packages, Slow mobility, would require assistance to evacuate, smoker cluttered flat which is being managed, KFRS aware and have provided smoking aids. | F3 and F26 Recorded Person cantered Fire risk assessment carried out and recorded in the fire box info.
2451 | Quarry House | QUARRYHOUS_S001 | H21 | Scheme | 2022-11-08 15:13 | FRA_2451081120221144.pdf | LingF | 2451081120221140 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | gfanein498nla87tnbk | Observation Only | Risk Closed | 44876.4313 | Obs1 | The Building | NULL | N/A | Surveyor | General elevation view showing cladding forming decorative feature panels, cladding fitted to block substrate. | Information only
2451 | Quarry House | QUARRYHOUS_S001 | H21 | Scheme | 2022-11-08 15:13 | FRA_2451081120221144.pdf | LingF | 2451081120221140 | Extra Care | EC Kent | Kent 3 | South | South Patch 3 | i2b1ccqegpfla86djdt | Observation Only | Risk Closed | 44876.4309 | Obs13 | Other Relevant Fixed Systems | NULL | N/A | Surveyor | AOV system showing orange control points. | Information only
2454 | Bellerophon House | BELLEROPHON_S001 | H21 | Scheme | 2021-11-30 07:53 | FRA_2454291120212114.pdf | BhopalP | 2454291120212110 | Extra Care | EC Kent | Kent 1 | South | South Patch 6 | hqyqltq4snakwlsoglp | Low Risk closed | Risk Closed | 44531.4325 | Obs4 | The Occupant - Information Provided By The Court Manager | 45260 | Low | Court Manager | Resident of flat 8 is very heavy smoker. Fire officer regularly visits him. He has been provided with fire retardant bedding and flat carpet has been sprayed with fire retardant product. He has also been provided with smoking aid and only allowed to smoke when carer are present. | All fire risk actions in place. Fire retardant blanket and carpets sprayed. On going monitoring.
2480 | Fordwich Place | FORDWICHPLAC_S001 | H21 | Scheme | 2022-03-14 15:49 | FRA_2480140320221529.pdf | LingF | 2480140320221520 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | hdxg9lp1w5l0qv2frh | Observation Only | Risk Closed | 44672.4249 | Obs5 | Evacuation Strategy And Training | NULL | N/A | Court Manager | CM has removed responsible resident due to lack of training and support from residents. | CM will discuss with residents volunteers to be responsible resident if alarms go off and explain training and procedure at Res Mtg in May
2480 | Fordwich Place | FORDWICHPLAC_S001 | H21 | Scheme | 2022-03-14 15:49 | FRA_2480140320221529.pdf | LingF | 2480140320221520 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | hceb2acguyrl0qv2fpe | Medium Risk closed | Risk Closed | 44697.443 | Obs2 | Means Of Giving Warning In Case Of Fire | 44999 | Medium | Court Manager | No sounder base within each flat, explore options to achieve 65Db at each bed head. | 5.4.22 The Regulatory Reform (fire safety) Order 2005 - Fire Service carried out assessment. Fire Safety compliant, recommendations given on 7 April 2022 19.4.22 Metroline Security, Joe Shishani requested by Frank Ling to carryout Fire Alarm System upgrade assessment and works recommended to meet the above to include sounder bases within each flat to achieve 65Db at bed heads of each flat. Recommendations and proposed costs received. 24.5.22 Resident S20 consultation re upgrade of fire system and plan for works and costs
2480 | Fordwich Place | FORDWICHPLAC_S001 | H21 | Scheme | 2022-03-14 15:49 | FRA_2480140320221529.pdf | LingF | 2480140320221520 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | ubmi2w8tqesl0qv2fq4 | Low Risk closed | Risk Closed | 44858.365 | Obs2 | Means Of Giving Warning In Case Of Fire | 45365 | Low | Court Manager | Extend detection into block B comms room | Resident consultation as part of fire system upgrade NOI/S20 served Costs gathered Tender being written by surveyor as part of upgrade
2480 | Fordwich Place | FORDWICHPLAC_S001 | H21 | Scheme | 2022-03-14 15:49 | FRA_2480140320221529.pdf | LingF | 2480140320221520 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | c9z8e7zs89ml0qv2fny | Observation Only | Risk Closed | 44763.4679 | Obs1 | The Building | NULL | N/A | Surveyor | General elevation view showing extent of tile cladding, feature does not cover the entire 1st floor elevations | Info
2480 | Fordwich Place | FORDWICHPLAC_S001 | H21 | Scheme | 2022-03-14 15:49 | FRA_2480140320221529.pdf | LingF | 2480140320221520 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | 841777q6baxl0qvnxwp | Low Risk closed | Risk Closed | 44858.3642 | Obs13 | Other Relevant Fixed Systems | 45365 | Low | Court Manager | Due to their location It is not possible to open the AOV's on top floors, provide suitable opening devices and ensure available for FRS use in the event of a fire. | opening devices are placed in each block
2480 | Fordwich Place | FORDWICHPLAC_S001 | H21 | Scheme | 2022-03-14 15:49 | FRA_2480140320221529.pdf | LingF | 2480140320221520 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | 8uxr4uuq32gl0qv2fs7 | Low Risk closed | Risk Closed | 44858.3634 | Obs8 | Measures To Limit Fire Spread And Development | 45365 | Low | Court Manager | Main entrance foyers have a timber boarded ceilings, no evidence of this being treated to prevent surface spread of flame. | Resident consultation, NOI/S20 served Contractors contacted for approx. costs Tenders being raised by surveyor
2480 | Fordwich Place | FORDWICHPLAC_S001 | H21 | Scheme | 2022-03-14 15:49 | FRA_2480140320221529.pdf | LingF | 2480140320221520 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | 5a2bgwkfc4fl0qv2ft8 | Low Risk closed | Risk Closed | 44858.3626 | Obs8 | Measures To Limit Fire Spread And Development | 44986 | Low | Court Manager | Noted on previous FRA defective fire stopping within loft spaces, cables passing through compartment walls. | Resident consultation. NOI/s20 served Contractor estimates received Surveyor compiling tender
2480 | Fordwich Place | FORDWICHPLAC_S001 | H21 | Scheme | 2022-03-14 15:49 | FRA_2480140320221529.pdf | LingF | 2480140320221520 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | 3q8u636u2bnl0qv2fqr | Observation Only | Risk Closed | 44697.4535 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | F3: suffers with mental impairment, would not understand to react in a fire situation, does not live alone although both would require support. None smokers, no cooking, private care support, property very tidy. | 9.2.22 Fire Home Safety Service visited and carried out assessment of fire safety with residents ref CRN 020553, notes made on Fire Service system evacuation chairs & assistant needed for both residents. Resident Information Form has emergency contact numbers, son lives locally, and also details assistance required.
2480 | Fordwich Place | FORDWICHPLAC_S001 | H21 | Scheme | 2022-03-14 15:49 | FRA_2480140320221529.pdf | LingF | 2480140320221520 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | 2968dj3qluml0qv2fom | Observation Only | Risk Closed | 44763.4679 | Obs1 | The Building | NULL | N/A | Surveyor | General rear view | Info
2480 | Fordwich Place | FORDWICHPLAC_S001 | H21 | Scheme | 2022-03-14 15:49 | FRA_2480140320221529.pdf | LingF | 2480140320221520 | Retirement Housing | London Kent | Kent South Coast | South | South Patch 3 | w840e0r7c1al0qv2fsr | Observation Only | Risk Closed | 44686.3892 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Court Manager | Manual opening vents on top floor corridor. | Pole openers on landings. Further advice requested from surveyor
2501 | Hargreaves Court | HARGREAVES_S001 | H21 | Scheme | 2022-02-07 15:49 | FRA_2501070220221546.pdf | PriestleyC | 2501070220221540 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | 8slny8u4unykzcv9f7m | Medium Risk closed | Risk Closed | 44694.4989 | Obs8 | Measures To Limit Fire Spread And Development | 44964 | Medium | Court Manager | Fire stopping breached in electric cupboard in small block | I raised a works order.
2501 | Hargreaves Court | HARGREAVES_S001 | H21 | Scheme | 2022-02-07 15:49 | FRA_2501070220221546.pdf | PriestleyC | 2501070220221540 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | cd3ivdzk30bkzcv9f9a | Medium Risk closed | Risk Closed | 44616.6331 | Obs8 | Measures To Limit Fire Spread And Development | 44964 | Medium | Court Manager | Door closer needs fixing flat 24 | Electrician fixed arm back on.
2501 | Hargreaves Court | HARGREAVES_S001 | H21 | Scheme | 2022-02-07 15:49 | FRA_2501070220221546.pdf | PriestleyC | 2501070220221540 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | fabgo7u8jm5kzcv9f5z | Low Risk closed | Risk Closed | 44770.6315 | Obs4 | The Occupant - Information Provided By The Court Manager | 45329 | Low | Court Manager | PCFRA's need updating following new incoming court manager | After attending new PCFRA training, completed PCFRAs for the court.
2501 | Hargreaves Court | HARGREAVES_S001 | H21 | Scheme | 2022-02-07 15:49 | FRA_2501070220221546.pdf | PriestleyC | 2501070220221540 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | ntxb2s2m27kzcv9f6t | Medium Risk closed | Risk Closed | 44677.5815 | Obs5 | Evacuation Strategy And Training | 44964 | Medium | Court Manager | Contents of red fire box needs updating | Updated and destroyed the previous file from 2014
2501 | Hargreaves Court | HARGREAVES_S001 | H21 | Scheme | 2022-02-07 15:49 | FRA_2501070220221546.pdf | PriestleyC | 2501070220221540 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | o7bzn1nt789kzcv9fa7 | Low Risk closed | Risk Closed | 44600.5742 | Obs15 | Management Of Fire Safety | 45329 | Low | Court Manager | Incoming Court Manager to sort fire folder | Ordered a file, printed all relevant fire safety information including FAR.
2501 | Hargreaves Court | HARGREAVES_S001 | H21 | Scheme | 2022-02-07 15:49 | FRA_2501070220221546.pdf | PriestleyC | 2501070220221540 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | pvfz4cu8mkzcv9f8c | Medium Risk closed | Risk Closed | 44677.4414 | Obs8 | Measures To Limit Fire Spread And Development | 44964 | Medium | Court Manager | Door closer needs refixing on flat 17 | Re fixed
2502 | Gill Court | GILL_S001 | H21 | Scheme | 2022-03-04 09:32 | FRA_2502040320220930.pdf | PriestleyC | 2502040320220930 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | nmhq4zt9ytl0c7uzu0 | Low Risk closed | Risk Closed | 44692.4364 | Obs8 | Measures To Limit Fire Spread And Development | 45355 | Low | Court Manager | Door closer not working on flat 22 | Job raised, engineer attended.
2502 | Gill Court | GILL_S001 | H21 | Scheme | 2022-03-04 09:32 | FRA_2502040320220930.pdf | PriestleyC | 2502040320220930 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | g3c43rg3pxsl0c7uzws | Low Risk closed | Risk Closed | 44699.403 | Obs10 | Fire Safety And Notices | 45355 | Low | Court Manager | No "do not use lift in case of fire" sign level 1 | Ordered stickers online
2502 | Gill Court | GILL_S001 | H21 | Scheme | 2022-03-04 09:32 | FRA_2502040320220930.pdf | PriestleyC | 2502040320220930 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | a3eoa48z0kdl0c7uzw5 | Low Risk closed | Risk Closed | 44699.4 | Obs10 | Fire Safety And Notices | 45002 | Low | Court Manager | Fire escape signage required on corridors | Ordered and placed signs
2503 | John Kay Court | JOHNKAY_S001 | H21 | Scheme | 2022-03-21 15:30 | FRA_2503210320221515.pdf | PriestleyC | 2503210320221510 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | n3yesdex3yl10v1x9k | Low Risk closed | Risk Closed | 44711.5244 | Obs11 | Fire Fighting Equipment | 45372 | Low | Court Manager | Fire extinguisher outside lift is not compliant with H21 policy and should be exchanged for P50 type extinguisher | After three months of being on stop. Informing all relevant departments and constantly chasing it arrived today.
2504 | Fairweather Court | FAIRWEATHER_S001 | H21 | Scheme | 2022-03-15 10:37 | FRA_2504150320221035.pdf | PriestleyC | 2504150320221030 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | l0f6av2go9al0s006mh | Low Risk closed | Risk Closed | 44662.4925 | Obs4 | The Occupant - Information Provided By The Court Manager | 45366 | Low | Court Manager | Carry out PCFRA for high risk residents | completed and added to residents files
2504 | Fairweather Court | FAIRWEATHER_S001 | H21 | Scheme | 2022-03-15 10:37 | FRA_2504150320221035.pdf | PriestleyC | 2504150320221030 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | khm8bzis3ssl0s006nc | Low Risk closed | Risk Closed | 44662.4932 | Obs7 | Fire Protection Measures | 45366 | Low | Court Manager | Stored items outside flat 2 are likely to cause a tripping hazard in case of emergency escape | advised resident to remove items, resident complied
2504 | Fairweather Court | FAIRWEATHER_S001 | H21 | Scheme | 2022-03-15 10:37 | FRA_2504150320221035.pdf | PriestleyC | 2504150320221030 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | eiubc6otndnl0s00www | Low Risk closed | Risk Closed | 44736.431 | Obs15 | Management Of Fire Safety | 45366 | Low | Court Manager | Cleaner needs to update fire safety training | new cleaner, training completed with other scheme, (works 2 jobs)
2504 | Fairweather Court | FAIRWEATHER_S001 | H21 | Scheme | 2022-03-15 10:37 | FRA_2504150320221035.pdf | PriestleyC | 2504150320221030 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | 1vk3wz3eqdol0s006o7 | Low Risk closed | Risk Closed | 44662.4935 | Obs10 | Fire Safety And Notices | 45366 | Low | Court Manager | Directional sign outside guest room needs turning round to point towards exit | completed by handyman
2505 | Bretherton Court | BRETHERTON_S001 | H21 | Scheme | 2022-04-19 11:05 | FRA_2505190420221102.pdf | ClarkG | 2505190420221100 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 2 | l01a7xr9upl25z9l1x | Low Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45401 | Low | Court Manager | Number of false alarms with Flat 1 need recording from before new scheme manager started. | NULL
2505 | Bretherton Court | BRETHERTON_S001 | H21 | Scheme | 2022-04-19 11:05 | FRA_2505190420221102.pdf | ClarkG | 2505190420221100 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 2 | ku8z1xykw7ll25z9l13 | Low Risk closed | Risk Closed | 44687.4948 | Obs8 | Measures To Limit Fire Spread And Development | 45401 | Low | Court Manager | Adjust door to Flat 19 as catching with court manager. | All building have resolved the issue, unable to trim door due to fire strip but have removed section of thick underlay which has now enabled door to close correctly. 6/5/22
2505 | Bretherton Court | BRETHERTON_S001 | H21 | Scheme | 2022-04-19 11:05 | FRA_2505190420221102.pdf | ClarkG | 2505190420221100 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 2 | nry7yhmi29pl25z9l06 | Low Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45401 | Low | Court Manager | Red Fire box information to be updated with residents information and Court Fire Plan | NULL
2505 | Bretherton Court | BRETHERTON_S001 | H21 | Scheme | 2022-04-19 11:05 | FRA_2505190420221102.pdf | ClarkG | 2505190420221100 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 2 | oh6rm31rszdl25z9kz5 | Low Risk to be actioned | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | 45401 | Low | Court Manager | New scheme manager to update and check the current PCFRA for all residents. | NULL
2506 | Harvey Longworth Court | HARVEYLONG_S001 | H21 | Scheme | 2022-02-14 15:21 | FRA_2506140220221511.pdf | PriestleyC | 2506140220221510 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 2 | i0caztt3jrkzmu3r8s | Low Risk closed | Risk Closed | 44606.6732 | Obs11 | Fire Fighting Equipment | 45336 | Low | Court Manager | Fire extinguishers should be removed from corridors as per H21 policy at next makeover | N.A. will be actioned at imminent makeover of scheme.
2507 | Bowman Court | BOWMAN_S001 | H21 | Scheme | 2022-03-08 11:42 | FRA_2507080320221047.pdf | PriestleyC | 2507080320221040 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | jelpgqxqs3l0i1bf4a | Medium Risk closed | Risk Closed | 44665.5289 | Obs7 | Fire Protection Measures | 44993 | Medium | Court Manager | Gap around door on corridor adj flat24 too big. Remove exiting timber strip from door frame and replace with thicker hardwood strip. | Handyman attended and replaced timber strip to meet regulations in reducing the gap.
2507 | Bowman Court | BOWMAN_S001 | H21 | Scheme | 2022-03-08 11:42 | FRA_2507080320221047.pdf | PriestleyC | 2507080320221040 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | 448pewdvmdvl0i0xuff | Low Risk closed | Risk Closed | 44628.6399 | Obs11 | Fire Fighting Equipment | 45359 | Low | Court Manager | Remove extinguishers from corridors at next makeover as per H21 policy | Action to be taken as per comments as discussed with surveyor
2507 | Bowman Court | BOWMAN_S001 | H21 | Scheme | 2022-03-08 11:42 | FRA_2507080320221047.pdf | PriestleyC | 2507080320221040 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | va6tx52cpdql0i1tqnu | Low Risk closed | Risk Closed | 44663.6275 | Obs6 | Fire Hazards - Elimination & Control | 45359 | Low | Court Manager | Scooter charger not PAT tested in communal lounge | GOS Electrical attended and PAT Test completed 12/04/2022
2508 | Barnes Court (Burnley) | BARNESBURN_S001 | H21 | Scheme | 2022-05-18 15:38 | FRA_2508180520221528.pdf | PriestleyC | 2508180520221520 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | jjdfhb28m9dl3bokzma | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45430 | Low | Court Manager | Remove furniture stored on corridor adjacent to flat 1 | NULL
2508 | Barnes Court (Burnley) | BARNESBURN_S001 | H21 | Scheme | 2022-05-18 15:38 | FRA_2508180520221528.pdf | PriestleyC | 2508180520221520 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | kr5jeqwz4el3bouao1 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45430 | Low | Court Manager | Door closer needs prefixing to door on flat 42 | NULL
2508 | Barnes Court (Burnley) | BARNESBURN_S001 | H21 | Scheme | 2022-05-18 15:38 | FRA_2508180520221528.pdf | PriestleyC | 2508180520221520 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | s4boewrnodfl3bor56l | Low Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45430 | Low | Court Manager | Need to make on call aware of difference between call outs to individual flats through apello system and communal fire alarm system to minimise false call outs to fire brigade | NULL
2509 | Barker Court | BARKER_S001 | H21 | Scheme | 2022-03-07 14:04 | FRA_2509070320221329.pdf | PriestleyC | 2509070320221320 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | t9b400w2yzol0grv1on | Low Risk closed | Risk Closed | 44645.6323 | Obs7 | Fire Protection Measures | 45358 | Low | Court Manager | Remove doormats from corridors which could be a tripping hazard in case of means of escape | Hand written note was displayed as printer was not working, printer now up and running, individual letters written to all residents asking for the removal of the mats explaining the trip hazard in the event of an emergency.
2509 | Barker Court | BARKER_S001 | H21 | Scheme | 2022-03-07 14:04 | FRA_2509070320221329.pdf | PriestleyC | 2509070320221320 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | pzaldm5g39bl0gqudrd | Medium Risk closed | Risk Closed | 44630.5987 | Obs5 | Evacuation Strategy And Training | 44992 | Medium | Court Manager | Red fire box needs updating with residents information | Updated the red fire box residents information
2509 | Barker Court | BARKER_S001 | H21 | Scheme | 2022-03-07 14:04 | FRA_2509070320221329.pdf | PriestleyC | 2509070320221320 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | 51goqa8e1ssl0gqrwpy | Low Risk to be actioned | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | 45358 | Low | Court Manager | Carry out PCFRA's for individuals | NULL
2509 | Barker Court | BARKER_S001 | H21 | Scheme | 2022-03-07 14:04 | FRA_2509070320221329.pdf | PriestleyC | 2509070320221320 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | 5i2ya8u082ql0grn1y3 | Low Risk closed | Risk Closed | 44679.3681 | Obs8 | Measures To Limit Fire Spread And Development | 45358 | Low | Court Manager | Replace missing smoke seal and adjust closer on flat 25 | arranged for handy person to replace seals, he adjusted the door closer which was not satisfactory, therefore arranged for door closer to be replaced, WO numbers 1529392 & 1534874
2509 | Barker Court | BARKER_S001 | H21 | Scheme | 2022-03-07 14:04 | FRA_2509070320221329.pdf | PriestleyC | 2509070320221320 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | 670ewcr5vf8l0grhcch | Low Risk closed | Risk Closed | 44652.4619 | Obs8 | Measures To Limit Fire Spread And Development | 45358 | Low | Court Manager | Replace some seal on flat 4 dor | raised works order for handyman to replace, he has replaced WO number 1529391
2510 | Fenney Court | FENNEY_S001 | H21 | Scheme | 2022-01-21 11:47 | FRA_2510180120221105.pdf | ClarkG | 2510180120221100 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 2 | 5mofq2c1zbykyk2kp2i | Low Risk closed | Risk Closed | 44852.3401 | Obs1 | The Building | 45309 | Low | Surveyor | Fire stopping required in loft space above Flat 29 | Works completed by Bell Group
2510 | Fenney Court | FENNEY_S001 | H21 | Scheme | 2022-01-21 11:47 | FRA_2510180120221105.pdf | ClarkG | 2510180120221100 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 2 | 2oelqsov0qokyk0g467 | Observation Only | Risk Closed | 44585.4559 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Surveyor | PAT testing completed on 16th December 2020. | No action required
2510 | Fenney Court | FENNEY_S001 | H21 | Scheme | 2022-01-21 11:47 | FRA_2510180120221105.pdf | ClarkG | 2510180120221100 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 2 | 10scewpx3jihkyobyas4 | Low Risk closed | Risk Closed | 44852.3405 | Obs1 | The Building | 45312 | Low | Surveyor | Fire stopping required in the loft space above Flat 20. | Works completed by Bell Group
2510 | Fenney Court | FENNEY_S001 | H21 | Scheme | 2022-01-21 11:47 | FRA_2510180120221105.pdf | ClarkG | 2510180120221100 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 2 | 0gym9a02b72ckyk2gpdr | Low Risk closed | Risk Closed | 44852.34 | Obs1 | The Building | 45309 | Low | Surveyor | Fire Stopping required in loft space above Flat 31 | Works completed by Bell Group
2510 | Fenney Court | FENNEY_S001 | H21 | Scheme | 2022-01-21 11:47 | FRA_2510180120221105.pdf | ClarkG | 2510180120221100 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 2 | dnqbu92ed5qkyoc12q3 | Low Risk closed | Risk Closed | 44852.3396 | Obs1 | The Building | 45312 | Low | Surveyor | Fire stopping required in the loft space above Flat 48. | Works completed by Bell Group
2510 | Fenney Court | FENNEY_S001 | H21 | Scheme | 2022-01-21 11:47 | FRA_2510180120221105.pdf | ClarkG | 2510180120221100 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 2 | fg5zluipyrhkyk2o56e | Low Risk closed | Risk Closed | 44586.4466 | Obs7 | Fire Protection Measures | 45309 | Low | Court Manager | Remove cardboard box stored outside Flat 31 | Had cardboard box removed
2510 | Fenney Court | FENNEY_S001 | H21 | Scheme | 2022-01-21 11:47 | FRA_2510180120221105.pdf | ClarkG | 2510180120221100 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 2 | dbedrwtd7ekkyk29sce | Low Risk closed | Risk Closed | 44600.4887 | Obs6 | Fire Hazards - Elimination & Control | 45309 | Low | Court Manager | Fire Stopping / brickwork required to hole above electric meter adjacent to Flat 25 | removed electric cupboard and replaced with bricks
2510 | Fenney Court | FENNEY_S001 | H21 | Scheme | 2022-01-21 11:47 | FRA_2510180120221105.pdf | ClarkG | 2510180120221100 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 2 | dekoz86hjvkyobzfe5 | Low Risk closed | Risk Closed | 44852.3404 | Obs1 | The Building | 45312 | Low | Surveyor | Fire stopping required in the loft space above Flat 50. | Works completed by Bell Group
2510 | Fenney Court | FENNEY_S001 | H21 | Scheme | 2022-01-21 11:47 | FRA_2510180120221105.pdf | ClarkG | 2510180120221100 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 2 | oyhaxad222akyobqizi | Low Risk closed | Risk Closed | 44852.3402 | Obs1 | The Building | 45312 | Low | Surveyor | Fire Stopping required in loft space above Flat 17. | Works completed by Bell Group
2510 | Fenney Court | FENNEY_S001 | H21 | Scheme | 2022-01-21 11:47 | FRA_2510180120221105.pdf | ClarkG | 2510180120221100 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 2 | or7yay9wdppkyk31xso | Low Risk closed | Risk Closed | 44852.3407 | Obs1 | The Building | 45309 | Low | Surveyor | Fire Stopping required in loft space above Flat 19 | Works completed by Bell Group
2510 | Fenney Court | FENNEY_S001 | H21 | Scheme | 2022-01-21 11:47 | FRA_2510180120221105.pdf | ClarkG | 2510180120221100 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 2 | txq3cnadqplkyobuobu | Low Risk closed | Risk Closed | 44852.3398 | Obs1 | The Building | 45312 | Low | Surveyor | Fire stopping required in the loft above Flat 22 | Works completed by Bell Group
2510 | Fenney Court | FENNEY_S001 | H21 | Scheme | 2022-01-21 11:47 | FRA_2510180120221105.pdf | ClarkG | 2510180120221100 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 2 | vy8qk6256qkyobtnr8 | Low Risk closed | Risk Closed | 44852.3354 | Obs1 | The Building | 45312 | Low | Surveyor | Fire stopping required in the loft space above Flat 8. | Works completed by Bell Group
2510 | Fenney Court | FENNEY_S001 | H21 | Scheme | 2022-01-21 11:47 | FRA_2510180120221105.pdf | ClarkG | 2510180120221100 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 2 | xbp21bw68skyobs8d4 | Low Risk closed | Risk Closed | 44852.3408 | Obs1 | The Building | 45312 | Low | Surveyor | Fire stopping required in the loft space above Flat 10. | Works completed by Bell Group
2514 | William Griffiths Court | WILLIAMGRIF_S001 | H21 | Scheme | 2022-03-08 16:34 | FRA_2514080320221627.pdf | PriestleyC | 2514080320221620 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | ds7edvt2h1l0ichy7p | Low Risk closed | Risk Closed | 44663.4584 | Obs11 | Fire Fighting Equipment | 45359 | Low | Court Manager | Fire extinguishers should be removed at next makeover as per H21 policy | Extinguishers to be removed on next make over.
2514 | William Griffiths Court | WILLIAMGRIF_S001 | H21 | Scheme | 2022-03-08 16:34 | FRA_2514080320221627.pdf | PriestleyC | 2514080320221620 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | 55v5r6s8npql0ichy6u | Low Risk closed | Risk Closed | 44663.4607 | Obs10 | Fire Safety And Notices | 45359 | Low | Court Manager | No "do not use lift in case of fire" sign | Notices are on display outside the lift as requested.
2515 | Pardoe Court | PARDOE_S001 | H21 | Scheme | 2022-04-19 11:03 | FRA_2515190420221057.pdf | ClarkG | 2515190420221050 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 2 | 6fws8f6skppl25z24sm | Low Risk closed | Risk Closed | 44690.5152 | Obs1 | The Building | 45401 | Low | Court Manager | Cables in loft space required fire stopping. | All building contractors completed works required 9th May 22
2515 | Pardoe Court | PARDOE_S001 | H21 | Scheme | 2022-04-19 11:03 | FRA_2515190420221057.pdf | ClarkG | 2515190420221050 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 2 | 7bao8zyraskl25z24u7 | Low Risk closed | Risk Closed | 44690.5361 | Obs7 | Fire Protection Measures | 45401 | Low | Court Manager | Adjust bin store door so it doesn't catch on the floor. | All buildings corrected door catching 6th May 22
2515 | Pardoe Court | PARDOE_S001 | H21 | Scheme | 2022-04-19 11:03 | FRA_2515190420221057.pdf | ClarkG | 2515190420221050 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 2 | bwk6i4lpd1l25z24tj | Low Risk closed | Risk Closed | 44770.9064 | Obs5 | Evacuation Strategy And Training | 45401 | Low | Court Manager | New Scheme manager to update training for cleaners. | Got cleaners updated on my team on Fred, meeting with staff and instructions with print off to clear required training due.
2515 | Pardoe Court | PARDOE_S001 | H21 | Scheme | 2022-04-19 11:03 | FRA_2515190420221057.pdf | ClarkG | 2515190420221050 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 2 | 9gc7fhx42o8l25z24t2 | Low Risk to be actioned | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | 45401 | Low | Court Manager | New scheme manager and will need to review all PCFRA for the residents. | NULL
2515 | Pardoe Court | PARDOE_S001 | H21 | Scheme | 2022-04-19 11:03 | FRA_2515190420221057.pdf | ClarkG | 2515190420221050 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 2 | sp0pvf98txml25z24uj | Low Risk closed | Risk Closed | 44699.4567 | Obs7 | Fire Protection Measures | 45401 | Low | Court Manager | Door Guard required for the hairdressers room. | Works completed 16th May 22
2515 | Pardoe Court | PARDOE_S001 | H21 | Scheme | 2022-04-19 11:03 | FRA_2515190420221057.pdf | ClarkG | 2515190420221050 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 2 | rn73wzzuo3l25z24uy | Observation Only | Risk Open | NULL | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | Update training records as due to out of date. | NULL
2515 | Pardoe Court | PARDOE_S001 | H21 | Scheme | 2022-04-19 11:03 | FRA_2515190420221057.pdf | ClarkG | 2515190420221050 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 2 | vfc9hqgh3wnl25z24tv | Low Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45401 | Low | Court Manager | Information in the red fire box needs updating with current residents information and Court Fire Plan with new scheme managers name. | NULL
2516 | Kingsway | KINGSWAY_S001 | H21 | Scheme | 2022-06-15 14:53 | FRA_2516140620221436.pdf | PriestleyC | 2516140620221430 | Extra Care | Extra Care North | EC North 4 | North | North Patch 2 | yaowm2txvrl4e7joku | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45091 | Medium | Court Manager | Flat entrance door on flat 31 needs easing to close when fire alarm triggers | NULL
2516 | Kingsway | KINGSWAY_S001 | H21 | Scheme | 2022-06-15 14:53 | FRA_2516140620221436.pdf | PriestleyC | 2516140620221430 | Extra Care | Extra Care North | EC North 4 | North | North Patch 2 | mxxhovufapdl4e7jok3 | Medium Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45091 | Medium | Other | Staff training needs arranging and carrying out | NULL
2516 | Kingsway | KINGSWAY_S001 | H21 | Scheme | 2022-06-15 14:53 | FRA_2516140620221436.pdf | PriestleyC | 2516140620221430 | Extra Care | Extra Care North | EC North 4 | North | North Patch 2 | 8ksagtnvmvbl4e7joml | Medium Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45091 | Medium | Court Manager | Training required for all contractors and staff | NULL
2516 | Kingsway | KINGSWAY_S001 | H21 | Scheme | 2022-06-15 14:53 | FRA_2516140620221436.pdf | PriestleyC | 2516140620221430 | Extra Care | Extra Care North | EC North 4 | North | North Patch 2 | ajkzopt5ggll4e7jolj | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45091 | Medium | Court Manager | Door closer does not operate on flat 56 | NULL
2524 | Riddiough Court | RIDDIOUGH_S001 | H21 | Scheme | 2022-03-07 13:30 | FRA_2524070320221329.pdf | PriestleyC | 2524070320221320 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | xxjssf8ehbl0gqpdks | Low Risk closed | Risk Closed | 44641.4679 | Obs8 | Measures To Limit Fire Spread And Development | 45358 | Low | Court Manager | Flat 12 entrance door needs easing | inform tenants daughter that the door needed adjusting owing to carpets being fitted. Work completed 21/03/22
2526 | Bannister Court | BANNISTER_S001 | H21 | Scheme | 2022-05-20 10:08 | FRA_2526190520221118.pdf | PriestleyC | 2526190520221110 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | w5xaq34fczl3cwbvmd | Low Risk to be actioned | Risk Open | NULL | Obs11 | Fire Fighting Equipment | 45065 | Low | Court Manager | Remove fire extinguishers from corridors at next makeover as they are not in line with H21 policy | NULL
2526 | Bannister Court | BANNISTER_S001 | H21 | Scheme | 2022-05-20 10:08 | FRA_2526190520221118.pdf | PriestleyC | 2526190520221110 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | 222ynrfxwxhil3cwnyfh | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45071 | Low | Surveyor | Obtain costs for external scooter store. Scooters currently stored under main staircase and charged during court manager working hours only. | NULL
2526 | Bannister Court | BANNISTER_S001 | H21 | Scheme | 2022-05-20 10:08 | FRA_2526190520221118.pdf | PriestleyC | 2526190520221110 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | jiax35k4b7l3cw3ybj | Low Risk closed | Risk Closed | 44762.3003 | Obs8 | Measures To Limit Fire Spread And Development | 45431 | Low | Court Manager | Ease and adjust flat doors on flats 14 & 16 | Logged repair with hp work completed
2526 | Bannister Court | BANNISTER_S001 | H21 | Scheme | 2022-05-20 10:08 | FRA_2526190520221118.pdf | PriestleyC | 2526190520221110 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 2 | ndopcd4n4jol3cwagm4 | Low Risk closed | Risk Closed | 44762.3009 | Obs10 | Fire Safety And Notices | 45431 | Low | Court Manager | Amend action notices to display "car park" as assembly point | Removed noticed replaced with car park
2530 | Brookside House | BROOKSIDEHOUS_S001 | H21 | Scheme | 2022-08-10 15:46 | FRA_2530080820221559.pdf | ClarkG | 2530080820221550 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | o3bbs6vamprl6kvq8eu | Medium Risk closed | Risk Closed | 44789.3541 | Obs6 | Fire Hazards - Elimination & Control | 45146 | Medium | Court Manager | Mobility scooters stored in communal area adjacent to Flat 148. This needs storing in the secure scooter room or residents flat. | Advised to put inside of flat or in scooter room provided.
2530 | Brookside House | BROOKSIDEHOUS_S001 | H21 | Scheme | 2022-08-10 15:46 | FRA_2530080820221559.pdf | ClarkG | 2530080820221550 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | pzspnd2ewmml6kvq8df | Low Risk closed | Risk Closed | 44789.3549 | Obs5 | Evacuation Strategy And Training | 45512 | Low | Court Manager | New care team staff need to complete Fire Warden training | This has been taken as an actioned by ACMs in their action plan from the last internal audit.
2530 | Brookside House | BROOKSIDEHOUS_S001 | H21 | Scheme | 2022-08-10 15:46 | FRA_2530080820221559.pdf | ClarkG | 2530080820221550 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | rxbb3cxt4w7l6kvq8fn | Medium Risk closed | Risk Closed | 44789.3517 | Obs6 | Fire Hazards - Elimination & Control | 45146 | Medium | Court Manager | Mobility scooters stored in communal areas adjacent to Flat 159. This needs to be stored in the secure scooter room or in the residents flats. | Advised tenant to put scooter inside flat or use the scooter room provided.
2530 | Brookside House | BROOKSIDEHOUS_S001 | H21 | Scheme | 2022-08-10 15:46 | FRA_2530080820221559.pdf | ClarkG | 2530080820221550 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | uo3f0zx9tqel6kvq8ib | Low Risk closed | Risk Closed | 44789.3586 | Obs8 | Measures To Limit Fire Spread And Development | 45512 | Low | Court Manager | Flat Door to Flat 157 is wedged open. We would recommend that no flat doors are wedged open at any time. | Wedge removed. This is due to tenant not being able to open door due to being a wheelchair user. Business case has been raised with H21 to rectify doors throughout Brookside House.
2530 | Brookside House | BROOKSIDEHOUS_S001 | H21 | Scheme | 2022-08-10 15:46 | FRA_2530080820221559.pdf | ClarkG | 2530080820221550 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | mxttu6i5u7l6kvq8e9 | Observation Only | Risk Closed | 44789.3554 | Obs5 | Evacuation Strategy And Training | NULL | N/A | Court Manager | Would recommend that a copy of the Court Fire Plan is kept in the Red Fire box. | Copy inside of red fore box.
2530 | Brookside House | BROOKSIDEHOUS_S001 | H21 | Scheme | 2022-08-10 15:46 | FRA_2530080820221559.pdf | ClarkG | 2530080820221550 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | i6di3eucq4il6kvq8fa | Medium Risk closed | Risk Closed | 44789.3543 | Obs6 | Fire Hazards - Elimination & Control | 45146 | Medium | Court Manager | Mobility scooters stored in communal areas adjacent to Flat 145. This needs to be stored in the secure scooter room or within the residents flat. | Advised to put in flat or scooter room provided.
2530 | Brookside House | BROOKSIDEHOUS_S001 | H21 | Scheme | 2022-08-10 15:46 | FRA_2530080820221559.pdf | ClarkG | 2530080820221550 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | hmc5vf0sn8kl6kvq8ix | Observation Only | Risk Closed | 44789.3524 | Obs9 | Escape Lighting | NULL | N/A | Court Manager | Light fitting not working in Stairwell adjacent to Flat 169. Scheme manager has raised a repair job for openview. | This works order has already been put through to open view who are waiting on a part.
2530 | Brookside House | BROOKSIDEHOUS_S001 | H21 | Scheme | 2022-08-10 15:46 | FRA_2530080820221559.pdf | ClarkG | 2530080820221550 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | fx7lb51mpugl6kvq8g5 | Medium Risk closed | Risk Closed | 44789.3526 | Obs6 | Fire Hazards - Elimination & Control | 45146 | Medium | Court Manager | Mobility scooters stored in communal areas adjacent to Flat 160. This needs to be stored in the secure scooter room or in the residents flat. | Advised to put scooters inside of flat or in scooter room.
2530 | Brookside House | BROOKSIDEHOUS_S001 | H21 | Scheme | 2022-08-10 15:46 | FRA_2530080820221559.pdf | ClarkG | 2530080820221550 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | 7jnjs49dsesl6kvq8hv | Low Risk closed | Risk Closed | 44789.3538 | Obs8 | Measures To Limit Fire Spread And Development | 45512 | Low | Court Manager | Closer to Flat 158 needs adjusting as flat doesn't close properly. | Handy man has completed this request.
2530 | Brookside House | BROOKSIDEHOUS_S001 | H21 | Scheme | 2022-08-10 15:46 | FRA_2530080820221559.pdf | ClarkG | 2530080820221550 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | 6s863xan8i6l6kvq8hb | Low Risk closed | Risk Closed | 44789.3529 | Obs7 | Fire Protection Measures | 45512 | Low | Court Manager | Door to stairwell adjacent to Flat 165 on first floor is catching on the floor. The door needs adjusting so it closes properly. | Closed by Housing Manager.
2530 | Brookside House | BROOKSIDEHOUS_S001 | H21 | Scheme | 2022-08-10 15:46 | FRA_2530080820221559.pdf | ClarkG | 2530080820221550 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | bargg1gpqvjl6kvq8jl | Low Risk to be actioned | Risk Open | NULL | Obs16 | Testing And Maintenance | 45512 | Low | M&E Team | Sprinkler System has not had the annual inspection/checks and is not on the current sprinkler checks. | NULL
2530 | Brookside House | BROOKSIDEHOUS_S001 | H21 | Scheme | 2022-08-10 15:46 | FRA_2530080820221559.pdf | ClarkG | 2530080820221550 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | vgbq0t97eol6kvq8gs | Observation Only | Risk Closed | 44789.3531 | Obs7 | Fire Protection Measures | NULL | N/A | Court Manager | Escape Route at rear of building - recommend the path is kept clear and jet washed. | Handy man is in the process of cleaning this area.
2531 | Ash Grange | ASHGRANGE_S001 | H21 | Scheme | 2022-10-26 11:57 | FRA_2531261020221017.pdf | JohnsonD | 2531261020221010 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | 9uzoi6jysgl9pgwuhd | Medium Risk Overdue | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44868 | Medium | Surveyor | Assessment of the EWI carried out by specialist organizations. Conclusions and recommendations made to senior management for implementation of an EWI replacement programme of works. Report available under separate cover. | NULL
2531 | Ash Grange | ASHGRANGE_S001 | H21 | Scheme | 2022-10-26 11:57 | FRA_2531261020221017.pdf | JohnsonD | 2531261020221010 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | dzvn3u5aqxl9pihd7l | Observation Only | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Court Manager | Note only | NULL
2531 | Ash Grange | ASHGRANGE_S001 | H21 | Scheme | 2022-10-26 11:57 | FRA_2531261020221017.pdf | JohnsonD | 2531261020221010 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | f3v6ba3rvbul9pijq7c | Observation Only | Risk Open | NULL | Obs13 | Other Relevant Fixed Systems | NULL | N/A | Court Manager | Note only | NULL
2531 | Ash Grange | ASHGRANGE_S001 | H21 | Scheme | 2022-10-26 11:57 | FRA_2531261020221017.pdf | JohnsonD | 2531261020221010 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | 6zu05r8wmqjl9pgd2kz | Low Risk to be actioned | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | 45233 | Low | Court Manager | There are 5 high risk residents, 5 medium risk residents with remaining residents categorised as low risk. Please continue to monitor. | NULL
2531 | Ash Grange | ASHGRANGE_S001 | H21 | Scheme | 2022-10-26 11:57 | FRA_2531261020221017.pdf | JohnsonD | 2531261020221010 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | 4sclbqdjoanl9phhktj | Low Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45591 | Low | Court Manager | Liaise withMerseyside fire and rescue services for residents meetings and advice on safety. This will support in house GSM meetings. | NULL
2531 | Ash Grange | ASHGRANGE_S001 | H21 | Scheme | 2022-10-26 11:57 | FRA_2531261020221017.pdf | JohnsonD | 2531261020221010 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | txn8tfeukrbl9pg8kwy | Medium Risk to be actioned | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | 45225 | Medium | M&E Team | See comment above. It is recommended that out of hours system is sense checked for functionality as there has been instances where calls have not been answered quickly. | NULL
2531 | Ash Grange | ASHGRANGE_S001 | H21 | Scheme | 2022-10-26 11:57 | FRA_2531261020221017.pdf | JohnsonD | 2531261020221010 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | s1hoh9y195hl9pilo0o | Observation Only | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Court Manager | Note only | NULL
2531 | Ash Grange | ASHGRANGE_S001 | H21 | Scheme | 2022-10-26 11:57 | FRA_2531261020221017.pdf | JohnsonD | 2531261020221010 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | ozrail0hueml9pieqpr | Observation Only | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Court Manager | Note only | NULL
2532 | Oak Grange | OAKGRANGE_S001 | H21 | Scheme | 2022-10-26 13:32 | FRA_2532261020221217.pdf | JohnsonD | 2532261020221210 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | 6xdky2tzhlil9pm7d1e | Low Risk closed | Risk Closed | 44901.5577 | Obs8 | Measures To Limit Fire Spread And Development | 45591 | Low | Court Manager | Laundry door does not close property. Please ease and adjust as required. | door will be eased and adjusted as required.
2532 | Oak Grange | OAKGRANGE_S001 | H21 | Scheme | 2022-10-26 13:32 | FRA_2532261020221217.pdf | JohnsonD | 2532261020221210 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | 641lro644lll9pl2dhu | Observation Only | Risk Open | NULL | Obs12 | Automatic Fire Systems i.e. Suppression System | NULL | N/A | Other | Note only | NULL
2532 | Oak Grange | OAKGRANGE_S001 | H21 | Scheme | 2022-10-26 13:32 | FRA_2532261020221217.pdf | JohnsonD | 2532261020221210 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | 1z3mpwy89bpl9plaqgc | Observation Only | Risk Closed | 44901.5571 | Obs12 | Automatic Fire Systems i.e. Suppression System | NULL | N/A | Court Manager | Note only | not required
2532 | Oak Grange | OAKGRANGE_S001 | H21 | Scheme | 2022-10-26 13:32 | FRA_2532261020221217.pdf | JohnsonD | 2532261020221210 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | 2ghx6bpc7gtl9pl72oq | Observation Only | Risk Open | NULL | Obs11 | Fire Fighting Equipment | NULL | N/A | Other | Note only | NULL
2532 | Oak Grange | OAKGRANGE_S001 | H21 | Scheme | 2022-10-26 13:32 | FRA_2532261020221217.pdf | JohnsonD | 2532261020221210 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | ap3oa47r0edl9pk7sck | Observation Only | Risk Closed | 44901.5569 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | There has been PCFRA carried out on residents. 1 high risk, 9, medium and low remaining residents categorised as low risk. Please continue to monitor. | will continue to monitor as advised
2532 | Oak Grange | OAKGRANGE_S001 | H21 | Scheme | 2022-10-26 13:32 | FRA_2532261020221217.pdf | JohnsonD | 2532261020221210 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | vlkiwtfh0fbl9pkj6o6 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45240 | Low | Surveyor | External vents adjacent to the main refuse store highlighted as a cause for concern. H21 need to establish any internal ducting and routes for fire and smoke into the building. There is planned works anticipated to address this problem. | NULL
2580 | Ashdale | ASHDALE_S001 | H21 | Scheme | 2022-08-17 11:16 | FRA_2580170820221010.pdf | ClarkG | 2580170820221010 | Retirement Housing | Mid East | Merseyside | North | North Patch 3 | xbwnmftz7lel6xfep41 | Low Risk closed | Risk Closed | 44841.5091 | Obs6 | Fire Hazards - Elimination & Control | 45521 | Low | Court Manager | Overloading of sockets in Managers Office. Need additional sockets to be installed (Would recommend dado trunking installed so additional sockets can be installed in future) | dorma TS62 x 2 have been fitted on Friday 21-9-22
2580 | Ashdale | ASHDALE_S001 | H21 | Scheme | 2022-08-17 11:16 | FRA_2580170820221010.pdf | ClarkG | 2580170820221010 | Retirement Housing | Mid East | Merseyside | North | North Patch 3 | zoeseg21i5cl6xgb54n | Low Risk closed | Risk Closed | 44862.6209 | Obs8 | Measures To Limit Fire Spread And Development | 45521 | Low | Court Manager | Overhead door closer required to be installed for flat 38. | 2 smoke detectors replaced
2601 | Sir Robert Martin Court | SIRROBEMART_S001 | H21 | Scheme | 2022-06-14 13:28 | FRA_2601140620221315.pdf | BatesT | 2601140620221310 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | 8rcblxkskcml4e4zpgj | Low Risk closed | Risk Closed | 44728.4094 | Obs7 | Fire Protection Measures | 45457 | Low | Court Manager | Fire door at f7 not pulling into frame | Contractor adjusted closure
2601 | Sir Robert Martin Court | SIRROBEMART_S001 | H21 | Scheme | 2022-06-14 13:28 | FRA_2601140620221315.pdf | BatesT | 2601140620221310 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | c8lyanjjwjml4e4r1n7 | Low Risk closed | Risk Closed | 44728.4106 | Obs7 | Fire Protection Measures | 45457 | Low | Court Manager | Fire door at f30 far too slow, and not closing fully | Closure adjusted
2601 | Sir Robert Martin Court | SIRROBEMART_S001 | H21 | Scheme | 2022-06-14 13:28 | FRA_2601140620221315.pdf | BatesT | 2601140620221310 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | cvpeoz41odl4e4ngyv | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45457 | Low | Surveyor | A lot of flat doors are on perco closers. Recommend changing to closers that can be adjustable. | NULL
2601 | Sir Robert Martin Court | SIRROBEMART_S001 | H21 | Scheme | 2022-06-14 13:28 | FRA_2601140620221315.pdf | BatesT | 2601140620221310 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | 2eaize6w0sml4e4v742 | Low Risk closed | Risk Closed | 44775.3652 | Obs10 | Fire Safety And Notices | 45457 | Low | Court Manager | Additional running man signage needed at top of stairs by f35 | Ordered new signs and put them up
2601 | Sir Robert Martin Court | SIRROBEMART_S001 | H21 | Scheme | 2022-06-14 13:28 | FRA_2601140620221315.pdf | BatesT | 2601140620221310 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | r3d9t5b24tl4e4omg2 | Medium Risk closed | Risk Closed | 44734.3759 | Obs10 | Fire Safety And Notices | 45091 | Medium | Court Manager | No escape signage in lounge | Order new signs and added x3 in total at fire exit doors
2601 | Sir Robert Martin Court | SIRROBEMART_S001 | H21 | Scheme | 2022-06-14 13:28 | FRA_2601140620221315.pdf | BatesT | 2601140620221310 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | mmjs8vvicibl4e4ngxk | Low Risk to be actioned | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | 45457 | Low | Surveyor | P6 System exists but is limited in that it doesnt extend to every room. Recomend upgrade of system as set up is a bit confused. | NULL
2602 | Ronald West Court | RONALDWEST_S001 | H21 | Scheme | 2022-06-06 12:33 | FRA_2602060620221204.pdf | BatesT | 2602060620221200 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | 5ctor4ek0onl42mm2ml | Low Risk closed | Risk Closed | 44726.4889 | Obs4 | The Occupant - Information Provided By The Court Manager | 45449 | Low | Court Manager | New court manager to review and update any risk assements and evac plans | Reviewed and updated court risk assessment and evac plan
2602 | Ronald West Court | RONALDWEST_S001 | H21 | Scheme | 2022-06-06 12:33 | FRA_2602060620221204.pdf | BatesT | 2602060620221200 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | 5i7zmuweco7l42mm2l0 | Observation Only | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Noted only - repeated from last fra. Connsideration should be made for upgrading the system to a L2M with Part 6 connected to the warden call. | NULL
2602 | Ronald West Court | RONALDWEST_S001 | H21 | Scheme | 2022-06-06 12:33 | FRA_2602060620221204.pdf | BatesT | 2602060620221200 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | czk361im5yll42n301p | Medium Risk closed | Risk Closed | 44749.6008 | Obs8 | Measures To Limit Fire Spread And Development | 45083 | Medium | Court Manager | All flat doors are on perco closers which makes them non-adjustable. Recomend upgrading closers as seen to be propped etc | No doors are being propped open and fire service have visited to do a fire safety talk with all residents including their doors. Upgrading closers not currently authorised to be completed this year.
2602 | Ronald West Court | RONALDWEST_S001 | H21 | Scheme | 2022-06-06 12:33 | FRA_2602060620221204.pdf | BatesT | 2602060620221200 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | bx78nwob43l42mm2oq | High Risk Closed | Risk Closed | 44720.5048 | Obs7 | Fire Protection Measures | 44810 | High | Court Manager | Fire door to lounge closer has been ripped off. Needs refitting asap. | Grant Defer attended 08.06.2022 and repaired the fire door closer to the lounge.
2602 | Ronald West Court | RONALDWEST_S001 | H21 | Scheme | 2022-06-06 12:33 | FRA_2602060620221204.pdf | BatesT | 2602060620221200 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | dtau6tabukl42mm2rf | Low Risk closed | Risk Closed | 44720.506 | Obs15 | Management Of Fire Safety | 45449 | Low | Court Manager | A couple of weeks missed on weekly fire test (understood due to change in management). Ensure suitable cover is in place so that this is not missed. | Will ensure cover arrangements in place for fire test in case of future court manager absence.
2602 | Ronald West Court | RONALDWEST_S001 | H21 | Scheme | 2022-06-06 12:33 | FRA_2602060620221204.pdf | BatesT | 2602060620221200 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | 8x1n8l5dtwkl42mm2pm | Low Risk closed | Risk Closed | 44720.5074 | Obs8 | Measures To Limit Fire Spread And Development | 45449 | Low | Court Manager | With known issues with some flat doors, recommend full assessment across the court with any easing and adjusting completed as necessary. | one fire door has been adjusted to prevent it getting stuck on the hallway carpet on 08.06.22. No other issues found with any other flat doors.
2602 | Ronald West Court | RONALDWEST_S001 | H21 | Scheme | 2022-06-06 12:33 | FRA_2602060620221204.pdf | BatesT | 2602060620221200 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | b9tgm6khi4ql42mnroo | Medium Risk closed | Risk Closed | 44742.3725 | Obs1 | The Building | 45083 | Medium | Court Manager | Fire break doors in compartmentation in loft spaces are open. Recomend closing and securing. | Repair raised with Grant Defer to have bolts fitted onto all doors so they can be closed and secured.
2602 | Ronald West Court | RONALDWEST_S001 | H21 | Scheme | 2022-06-06 12:33 | FRA_2602060620221204.pdf | BatesT | 2602060620221200 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | z09n8mk88sl42mm2nq | Medium Risk closed | Risk Closed | 44733.4095 | Obs5 | Evacuation Strategy And Training | 45083 | Medium | Court Manager | New court manager to complete fire safety manager course | Fire Safety Manager course booked in to attend on 28th July.
2602 | Ronald West Court | RONALDWEST_S001 | H21 | Scheme | 2022-06-06 12:33 | FRA_2602060620221204.pdf | BatesT | 2602060620221200 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | vfwasfl46jl42mm2qo | Low Risk closed | Risk Closed | 44733.4092 | Obs15 | Management Of Fire Safety | 45449 | Low | Court Manager | No record of staff fire training in red book. | Staff training log has been updated and appropriate training completed or signed up for.
2603 | Brown Court (Adlz) | BROWNADLZ_S001 | H21 | Scheme | 2022-06-21 12:04 | FRA_2603210620221127.pdf | BatesT | 2603210620221120 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | xqn06t6z9jel4o0x3rg | Low Risk closed | Risk Closed | 44880.37 | Obs10 | Fire Safety And Notices | 45464 | Low | Court Manager | No running man signage, recomend fitting in blocks | Signage now fitted as directed by Tim Bates
2603 | Brown Court (Adlz) | BROWNADLZ_S001 | H21 | Scheme | 2022-06-21 12:04 | FRA_2603210620221127.pdf | BatesT | 2603210620221120 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | z24ysoq0lll4o19445 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45464 | Low | Court Manager | F9 needs seeing to as above | NULL
2603 | Brown Court (Adlz) | BROWNADLZ_S001 | H21 | Scheme | 2022-06-21 12:04 | FRA_2603210620221127.pdf | BatesT | 2603210620221120 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | zhzstspu2il4o0wa1n | Low Risk closed | Risk Closed | 44785.3777 | Obs15 | Management Of Fire Safety | 45464 | Low | Court Manager | Emergency lighting test and ffe inspection not logged for may | Court Manager off work. Checked back and test was completed by covering manager
2603 | Brown Court (Adlz) | BROWNADLZ_S001 | H21 | Scheme | 2022-06-21 12:04 | FRA_2603210620221127.pdf | BatesT | 2603210620221120 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | b46qk5i5ril4o0w9ye | Medium Risk closed | Risk Closed | 44785.38 | Obs5 | Evacuation Strategy And Training | 45098 | Medium | Court Manager | Red box information is dated 31/1/21 recommend this is updated. | Updated 12/8/2022
2603 | Brown Court (Adlz) | BROWNADLZ_S001 | H21 | Scheme | 2022-06-21 12:04 | FRA_2603210620221127.pdf | BatesT | 2603210620221120 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | 76910oouu8hl4o0wa01 | Low Risk closed | Risk Closed | 44791.4053 | Obs15 | Management Of Fire Safety | 45464 | Low | Court Manager | No staff training logged since 2018 | Downloaded fire Safety Manager Certificate and placed in folder. Carly Smallwood completed update training on 12th August.
2603 | Brown Court (Adlz) | BROWNADLZ_S001 | H21 | Scheme | 2022-06-21 12:04 | FRA_2603210620221127.pdf | BatesT | 2603210620221120 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | 2cbd7rp4dfkl4o1vpzx | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45464 | Low | Court Manager | Closer detached resident to refix | NULL
2603 | Brown Court (Adlz) | BROWNADLZ_S001 | H21 | Scheme | 2022-06-21 12:04 | FRA_2603210620221127.pdf | BatesT | 2603210620221120 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | lsg7nqz2rtl4o0wa0v | Medium Risk closed | Risk Closed | 44785.3814 | Obs15 | Management Of Fire Safety | 45098 | Medium | Court Manager | No evidence of system tests in red book. | Court Manager has been off work. Covering Managers have not been recording weekly tests. Checked compliance and all tests have been completed.
2603 | Brown Court (Adlz) | BROWNADLZ_S001 | H21 | Scheme | 2022-06-21 12:04 | FRA_2603210620221127.pdf | BatesT | 2603210620221120 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | t3s473qhuhl4o0w9xj | Medium Risk closed | Risk Closed | 44785.3798 | Obs5 | Evacuation Strategy And Training | 45098 | Medium | Court Manager | Unknown if responsible person has completed fire safety manager course. | No responsible person at Brown court OOH are dealt with by Securus or the court manager is she is made aware.
2603 | Brown Court (Adlz) | BROWNADLZ_S001 | H21 | Scheme | 2022-06-21 12:04 | FRA_2603210620221127.pdf | BatesT | 2603210620221120 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | ohw6u7z70xql4o25z75 | Medium Risk closed | Risk Closed | 44785.3785 | Obs7 | Fire Protection Measures | 45098 | Medium | Court Manager | Scooter stored outside f31 | Letter sent to resident along with scooter policy. Requested that resident removes scooter and stores in her property straight away
2608 | Mowbray Court | MOWBRAY_S001 | H21 | Scheme | 2022-01-13 14:49 | FRA_2608130120221432.pdf | BatesT | 2608130120221430 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 1 | opw1aldst7ckyd2mq5e | Low Risk closed | Risk Closed | 44615.4229 | Obs10 | Fire Safety And Notices | 45304 | Low | Court Manager | Fire door to lift upstairs has no signage | New sign
2608 | Mowbray Court | MOWBRAY_S001 | H21 | Scheme | 2022-01-13 14:49 | FRA_2608130120221432.pdf | BatesT | 2608130120221430 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 1 | til5q0t712kyd2mq19 | Medium Risk closed | Risk Closed | 44600.6108 | Obs8 | Measures To Limit Fire Spread And Development | 44939 | Medium | Court Manager | Switch room being used as storage, recommend. | Checked and no residents have access to this store cupboard.
2608 | Mowbray Court | MOWBRAY_S001 | H21 | Scheme | 2022-01-13 14:49 | FRA_2608130120221432.pdf | BatesT | 2608130120221430 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 1 | l8u39vrtfqkkyd2mq3a | Medium Risk closed | Risk Closed | 44732.6072 | Obs9 | Escape Lighting | 44939 | Medium | Court Manager | Buggy store at end of site (by f18) has no emergency lighting provision. | New emergency lights fitted today
2608 | Mowbray Court | MOWBRAY_S001 | H21 | Scheme | 2022-01-13 14:49 | FRA_2608130120221432.pdf | BatesT | 2608130120221430 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 1 | l62to2fw1wjkyd2mq0h | Low Risk closed | Risk Closed | 44607.5135 | Obs8 | Measures To Limit Fire Spread And Development | 45304 | Low | Court Manager | Keep locked door by office open | Locked it
2608 | Mowbray Court | MOWBRAY_S001 | H21 | Scheme | 2022-01-13 14:49 | FRA_2608130120221432.pdf | BatesT | 2608130120221430 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 1 | gb3a60e2efpkyd2mq65 | Low Risk closed | Risk Closed | 44615.4019 | Obs10 | Fire Safety And Notices | 45304 | Low | Court Manager | Fire door to stairwell has no signage upstairs | New sign
2608 | Mowbray Court | MOWBRAY_S001 | H21 | Scheme | 2022-01-13 14:49 | FRA_2608130120221432.pdf | BatesT | 2608130120221430 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 1 | 45gqf5a0f1mkyd2mq4l | Low Risk closed | Risk Closed | 44607.6151 | Obs10 | Fire Safety And Notices | 45304 | Low | Court Manager | A number of automatic doors only have signage on one side | Replaced signage on both
2608 | Mowbray Court | MOWBRAY_S001 | H21 | Scheme | 2022-01-13 14:49 | FRA_2608130120221432.pdf | BatesT | 2608130120221430 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 1 | 45pcj5xkfvrkyd2mpxt | Medium Risk closed | Risk Closed | 44638.4772 | Obs6 | Fire Hazards - Elimination & Control | 44939 | Medium | Court Manager | Bbq gas stored in storage room. Recommend external storage. If not will require correct signage and notification in red box. | Gas bottle has been removed off premises and will be stored with residents caravan on caravan site
2608 | Mowbray Court | MOWBRAY_S001 | H21 | Scheme | 2022-01-13 14:49 | FRA_2608130120221432.pdf | BatesT | 2608130120221430 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 1 | a0ytvv1k92hkyd2mq23 | Low Risk closed | Risk Closed | 44770.6246 | Obs8 | Measures To Limit Fire Spread And Development | 45304 | Low | Court Manager | Recommend fitting automated free swing | New automated swing arm fitted 27/7/22
2608 | Mowbray Court | MOWBRAY_S001 | H21 | Scheme | 2022-01-13 14:49 | FRA_2608130120221432.pdf | BatesT | 2608130120221430 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 1 | 9pt1lwhhpujkyd2mpyr | High Risk Closed | Risk Closed | 44574.6452 | Obs7 | Fire Protection Measures | 44664 | High | Court Manager | Scooter for f27 has been left outside flat. Can not be stored on escape route. | Resident is moving the scooter back in to his flat as he is a oxygen user and can not walk from the buggy store and he is aware he can not store it in the corridor at any time.
2608 | Mowbray Court | MOWBRAY_S001 | H21 | Scheme | 2022-01-13 14:49 | FRA_2608130120221432.pdf | BatesT | 2608130120221430 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 1 | 9nzvtb2ezs8kyd2mq6s | Low Risk closed | Risk Closed | 44603.587 | Obs10 | Fire Safety And Notices | 45304 | Low | Court Manager | Refuse store being used as buggy store, but still signposted as refuse. Sign to be removed to ensure room isn't used for both functions. | Removed sign
2608 | Mowbray Court | MOWBRAY_S001 | H21 | Scheme | 2022-01-13 14:49 | FRA_2608130120221432.pdf | BatesT | 2608130120221430 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 1 | e76r9md0g96kyd2mpzm | Low Risk closed | Risk Closed | 44607.5129 | Obs8 | Measures To Limit Fire Spread And Development | 45304 | Low | Court Manager | Quiet room door not pulling shut | Adjustment on door
2608 | Mowbray Court | MOWBRAY_S001 | H21 | Scheme | 2022-01-13 14:49 | FRA_2608130120221432.pdf | BatesT | 2608130120221430 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 1 | xz0xwiub9jmkyd2mpx3 | Medium Risk closed | Risk Closed | 44588.4174 | Obs6 | Fire Hazards - Elimination & Control | 44939 | Medium | Court Manager | Some scooters still need pat testing for communal storage | All scooters are now PAT tested
2608 | Mowbray Court | MOWBRAY_S001 | H21 | Scheme | 2022-01-13 14:49 | FRA_2608130120221432.pdf | BatesT | 2608130120221430 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 1 | w8ntwn11rjmkyd2mq80 | Low Risk closed | Risk Closed | 44575.6102 | Obs15 | Management Of Fire Safety | 45304 | Low | Court Manager | Fires and false alarm activations not noted within red book. (Although recorded on internal H&S system). | I have put a copy in the red Fire safety folder.
2701 | Ancaster Court | ANCASTER_S001 | H21 | Scheme | 2022-07-06 13:04 | FRA_2701060720221058.pdf | BatesT | 2701060720221050 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | erks1v5eiuzl59jjk32 | Low Risk closed | Risk Closed | 44770.5147 | Obs8 | Measures To Limit Fire Spread And Development | 45479 | Low | Court Manager | F30 missing small section of smoke seal | Work completed by Sleaford Building Services 28/07/22
2701 | Ancaster Court | ANCASTER_S001 | H21 | Scheme | 2022-07-06 13:04 | FRA_2701060720221058.pdf | BatesT | 2701060720221050 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | a3hrdthul4el59fsz27 | Low Risk closed | Risk Closed | 44883.4765 | Obs6 | Fire Hazards - Elimination & Control | 45479 | Low | Court Manager | Limited PAT testing to chargers in scooter store. All need to be pat tested. | PAT testing Completed by Hallgate Lincs
2701 | Ancaster Court | ANCASTER_S001 | H21 | Scheme | 2022-07-06 13:04 | FRA_2701060720221058.pdf | BatesT | 2701060720221050 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | 4qtmck7p7rzl59gv3g2 | Observation Only | Risk Closed | 44750.5255 | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | Training records of domestic staff to be updated in red folder. | Contacted FRED and have now updated red folder with necessary records
2701 | Ancaster Court | ANCASTER_S001 | H21 | Scheme | 2022-07-06 13:04 | FRA_2701060720221058.pdf | BatesT | 2701060720221050 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | 7mmzx6o2s3al59joodb | Medium Risk to be actioned | Risk Open | NULL | Obs1 | The Building | 45113 | Medium | Surveyor | Switch room requires further fire stopping to be implemented - currently lacking. | NULL
2701 | Ancaster Court | ANCASTER_S001 | H21 | Scheme | 2022-07-06 13:04 | FRA_2701060720221058.pdf | BatesT | 2701060720221050 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | 32536ffz84ol59jlfow | Low Risk closed | Risk Closed | 44760.3774 | Obs10 | Fire Safety And Notices | 45479 | Low | Court Manager | Action in event of signage missing at call point at front door | Printed and laminated from Wilma.
2701 | Ancaster Court | ANCASTER_S001 | H21 | Scheme | 2022-07-06 13:04 | FRA_2701060720221058.pdf | BatesT | 2701060720221050 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | l4fjuu22klbl59jm1i8 | Low Risk closed | Risk Closed | 44749.4174 | Obs10 | Fire Safety And Notices | 45479 | Low | Court Manager | Mobility scooter storage has both keep shut and keep locked sign. Needs one removing. | Removed keep shut sign and kept keep locked sign in place
2701 | Ancaster Court | ANCASTER_S001 | H21 | Scheme | 2022-07-06 13:04 | FRA_2701060720221058.pdf | BatesT | 2701060720221050 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | kor9enfb7mkl59h3twd | Observation Only | Risk Closed | 44748.6548 | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | New court manager - recommend contacting FRS to arrange fire safety talk for residents. | Email sent to fire.safety@lincoln.fire-uk.gov requesting suitable dates for FRS to come and carry out a resident engagement morning.
2701 | Ancaster Court | ANCASTER_S001 | H21 | Scheme | 2022-07-06 13:04 | FRA_2701060720221058.pdf | BatesT | 2701060720221050 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | rcwf1s5pferl59jpqcm | Low Risk closed | Risk Closed | 44749.4182 | Obs8 | Measures To Limit Fire Spread And Development | 45479 | Low | Court Manager | Lounge door has keep shut signage, but is fitted with lock. Needs to be keep locked sign or locking mechanism removed. | Locking mechanism has been removed.
2701 | Ancaster Court | ANCASTER_S001 | H21 | Scheme | 2022-07-06 13:04 | FRA_2701060720221058.pdf | BatesT | 2701060720221050 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | onq67gn10tvl59jkbie | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45479 | Low | Surveyor | A number of flat doors have perco closers that are none adjustable. Recommend these be replaced with adjustable closers. | NULL
2701 | Ancaster Court | ANCASTER_S001 | H21 | Scheme | 2022-07-06 13:04 | FRA_2701060720221058.pdf | BatesT | 2701060720221050 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | qr300oc5gdel59g6qmi | Low Risk closed | Risk Closed | 44748.6581 | Obs6 | Fire Hazards - Elimination & Control | 45479 | Low | Court Manager | No arrangement for tumble dryer - recommend domestic staff clean once a week. | Conversation had with court cleaner. Weekly filter clean mutually agreed.
2702 | Welby-Everard Court | WELBYEVER_S001 | H21 | Scheme | 2022-07-22 12:52 | FRA_2702220720221124.pdf | BatesT | 2702220720221120 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 1 | q40v2dsubhpl5wei3rt | Low Risk closed | Risk Closed | 44776.6062 | Obs10 | Fire Safety And Notices | 45495 | Low | Court Manager | Door signage missing on guest room and reverse of stairwell exit door next to lounge | Signs have been put on both sides of guest room door and on the other side of the fire door between the buggy store and the communal lounge
2702 | Welby-Everard Court | WELBYEVER_S001 | H21 | Scheme | 2022-07-22 12:52 | FRA_2702220720221124.pdf | BatesT | 2702220720221120 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 1 | k9n2uz3b6ypl5wc4jp4 | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45158 | Low | Surveyor | Running man sign missing from outside lounge | NULL
2702 | Welby-Everard Court | WELBYEVER_S001 | H21 | Scheme | 2022-07-22 12:52 | FRA_2702220720221124.pdf | BatesT | 2702220720221120 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 1 | 0nelk7ktjmunl5weh644 | Medium Risk closed | Risk Closed | 44784.5163 | Obs6 | Fire Hazards - Elimination & Control | 45129 | Medium | Court Manager | Stored furniture in warden call server room | Furniture removed and swept the room out. Leaving only the BT candles etc left there
2702 | Welby-Everard Court | WELBYEVER_S001 | H21 | Scheme | 2022-07-22 12:52 | FRA_2702220720221124.pdf | BatesT | 2702220720221120 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 1 | 56qj5p7s0m9l5wcgahl | Medium Risk closed | Risk Closed | 44784.5214 | Obs5 | Evacuation Strategy And Training | 45129 | Medium | Court Manager | Nominated wardens have not kept up with monthly refresher training. Needs to be brought back up to speed asap or wardens changed or relinquished of duties. | Nominated wardens have had a change of circs each. Spoke to both and they still want to do the nominated warden role and have agreed from next Thursday 18th August that we will go through the fire checks etc.
2702 | Welby-Everard Court | WELBYEVER_S001 | H21 | Scheme | 2022-07-22 12:52 | FRA_2702220720221124.pdf | BatesT | 2702220720221120 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 1 | 8hea6zd3vdul5wbuwby | Observation Only | Risk Closed | 44769.5864 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | No Scooters or Oxygen onsite | None. There are no scooters or oxygen tanks on site
2702 | Welby-Everard Court | WELBYEVER_S001 | H21 | Scheme | 2022-07-22 12:52 | FRA_2702220720221124.pdf | BatesT | 2702220720221120 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 1 | z7669e1pblwl5weabg1 | Low Risk closed | Risk Closed | 44789.6092 | Obs8 | Measures To Limit Fire Spread And Development | 45495 | Low | Court Manager | Cold smoke seal missing on door of flat 12 | Stuck some smoke seal to the upper door frame
2703 | Miller Court | MILLER_S001 | H21 | Scheme | 2022-04-26 14:32 | FRA_2703260420221345.pdf | BatesT | 2703260420221340 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | w66g6jjon1l2g55nfz | Low Risk closed | Risk Closed | 44687.6112 | Obs8 | Measures To Limit Fire Spread And Development | 45408 | Low | Court Manager | Lounge "keep locked" door unlocked | Ensure that door is kept locked in future, Domestic Staff also advised.
2703 | Miller Court | MILLER_S001 | H21 | Scheme | 2022-04-26 14:32 | FRA_2703260420221345.pdf | BatesT | 2703260420221340 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | 9155kkj83wsl2g5bs61 | Medium Risk closed | Risk Closed | 44704.6488 | Obs8 | Measures To Limit Fire Spread And Development | 45042 | Medium | Court Manager | Buggy store fire door does not pull closed. Ease and adjust. | Door now closes correctly.
2703 | Miller Court | MILLER_S001 | H21 | Scheme | 2022-04-26 14:32 | FRA_2703260420221345.pdf | BatesT | 2703260420221340 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | fgf20smi1il2g557r2 | Observation Only | Risk Closed | 44687.6095 | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | Escape lighting tests have been logged as contractor maintenance. | This has been changed and input on correct form now.
2703 | Miller Court | MILLER_S001 | H21 | Scheme | 2022-04-26 14:32 | FRA_2703260420221345.pdf | BatesT | 2703260420221340 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | 2h9quqs25exl2g557rs | Observation Only | Risk Closed | 44778.7479 | Obs15 | Management Of Fire Safety | NULL | N/A | Other | Multiple activations have been logged when in essence they were one event for 10-2-22. Have not counted every instance of activation, just the event of workmen causing dust next to detector. | n/a observation only
2703 | Miller Court | MILLER_S001 | H21 | Scheme | 2022-04-26 14:32 | FRA_2703260420221345.pdf | BatesT | 2703260420221340 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | h65xq62nh6fl2g557qa | Observation Only | Risk Closed | 44685.6844 | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | New court manager training not detailed in red book | Inputted details in the red fire folder.
2703 | Miller Court | MILLER_S001 | H21 | Scheme | 2022-04-26 14:32 | FRA_2703260420221345.pdf | BatesT | 2703260420221340 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | i9xc10wo24ml2g5nv5u | Observation Only | Risk Closed | 44687.6106 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Court Manager | Magnet on cross corridor door by f5 not energising | When did walk about with Surveyor the door did stay open with magnet it sometimes does this on odd occasions. Monitor and WO put on.
2703 | Miller Court | MILLER_S001 | H21 | Scheme | 2022-04-26 14:32 | FRA_2703260420221345.pdf | BatesT | 2703260420221340 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | ncr7acs623l2g5hf37 | Low Risk closed | Risk Closed | 44701.6908 | Obs6 | Fire Hazards - Elimination & Control | 45408 | Low | Court Manager | Buggy charger not pat tested | Charger now pat tested.
2703 | Miller Court | MILLER_S001 | H21 | Scheme | 2022-04-26 14:32 | FRA_2703260420221345.pdf | BatesT | 2703260420221340 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | ns35thf7hbl2g59fdw | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45408 | Low | Surveyor | Buggy store door is automated on hold open, however whilst open obstructs exit route. Recommend remodel, possibly to be opening inward | NULL
2704 | Grounds Court | GROUNDS_S001 | H21 | Scheme | 2022-08-09 12:30 | FRA_2704090820221038.pdf | BatesT | 2704090820221030 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | tc2392sey46l6m2smpn | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45513 | Low | Court Manager | Some flat doors use perco closers, whilst these are working correctly they are fine, however recommend that with any issues they be swapped for closers that can be adjusted. | NULL
2704 | Grounds Court | GROUNDS_S001 | H21 | Scheme | 2022-08-09 12:30 | FRA_2704090820221038.pdf | BatesT | 2704090820221030 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | 261pe326fukl6m1bazf | Low Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45513 | Low | Court Manager | No records of fires or false alarms within red book. New staff confirms any will / should have been logged on system but with staff change no evidence can be shown. Ideally these should be logged in red book. | NULL
2704 | Grounds Court | GROUNDS_S001 | H21 | Scheme | 2022-08-09 12:30 | FRA_2704090820221038.pdf | BatesT | 2704090820221030 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | 7cjcy9398m1l6m08z6m | Observation Only | Risk Closed | 44788.3698 | Obs15 | Management Of Fire Safety | NULL | N/A | Other | Limited historical records in red fire book, but clear that records are now being kept, previous records available on computer system. | info only. No actions required
2704 | Grounds Court | GROUNDS_S001 | H21 | Scheme | 2022-08-09 12:30 | FRA_2704090820221038.pdf | BatesT | 2704090820221030 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | 8kohvqtv4yzl6m1nwz0 | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45513 | Low | Court Manager | Low level of running men signage present - generally available at direction changes but not over cross corridor partitions. Recommend review and fitting additional. | NULL
2704 | Grounds Court | GROUNDS_S001 | H21 | Scheme | 2022-08-09 12:30 | FRA_2704090820221038.pdf | BatesT | 2704090820221030 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | amvk5f0sqs4l6m1s9cs | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45147 | Medium | Court Manager | Old office store room is full of storage materials, alongside warden call equipment. Requires much better organisation to provide space between ignition and fuel - ideally would be put out of commission as a storage room due to ignition source within. | NULL
2704 | Grounds Court | GROUNDS_S001 | H21 | Scheme | 2022-08-09 12:30 | FRA_2704090820221038.pdf | BatesT | 2704090820221030 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | w3940erj8azl6m2vnlb | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45147 | Medium | Court Manager | Electric closer on f9 has been disconnected from electrics. Whilst it is assumed that this device is "fail safe" it needs to be confirmed that closing is correct and ideally reconnected. | NULL
2705 | Burland Court | BURLAND_S001 | H21 | Scheme | 2022-07-20 13:34 | FRA_2705200720221233.pdf | BatesT | 2705200720221230 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 1 | d3e13eeqms2l5tk57p5 | Low Risk closed | Risk Closed | 44831.5258 | Obs7 | Fire Protection Measures | 45493 | Low | Court Manager | Issue with flats 25, 26, & 38 - single exit route around elevated walkway not protected. Recommend fitting 30min external doors and windows. | Referred back to Surveyor to get quotes.
2706 | Sheppard Court | SHEPPARD_S001 | H21 | Scheme | 2022-01-10 12:28 | FRA_2706100120221107.pdf | BatesT | 2706100120221100 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | i1rjrr5jl6rky8nnlbe | Low Risk closed | Risk Closed | 44580.688 | Obs8 | Measures To Limit Fire Spread And Development | 45301 | Low | Court Manager | Communal door by F17 - intumescent strip missing | Intumescent strip replaced
2706 | Sheppard Court | SHEPPARD_S001 | H21 | Scheme | 2022-01-10 12:28 | FRA_2706100120221107.pdf | BatesT | 2706100120221100 | Retirement Housing | Mid East | Lincolnshire and Leicestershire | Central | Central Patch 6 | gstz6lfom1zky8nod4y | Low Risk closed | Risk Closed | 44580.6871 | Obs8 | Measures To Limit Fire Spread And Development | 45301 | Low | Court Manager | Communal door lounge has had smoke seals cut away - recommend replacement. | Smoke seals have been replaced
2801 | Graeme Bryson Court | GRAEMEBRYS_S001 | H21 | Scheme | 2021-12-01 14:26 | FRA_2801011220211317.pdf | ClarkG | 2801011220211310 | Retirement Housing | Mid East | Merseyside | North | North Patch 3 | h790y9yjppnkwnlzhfk | Low Risk closed | Risk Closed | 44536.5514 | Obs8 | Measures To Limit Fire Spread And Development | 45261 | Low | Court Manager | Door closure on Ground Floor lobby needs repairing and re-fixing to floor. Magnetic door closer still works. | Raised works order to CBE on 02/12/21 Ref No 1503738. Completed on 06/12/2.
2801 | Graeme Bryson Court | GRAEMEBRYS_S001 | H21 | Scheme | 2021-12-01 14:26 | FRA_2801011220211317.pdf | ClarkG | 2801011220211310 | Retirement Housing | Mid East | Merseyside | North | North Patch 3 | t3ka0umtbqnkwnm5ico | Low Risk closed | Risk Closed | 44536.5524 | Obs1 | The Building | 45261 | Low | Court Manager | Hole into loft space where old light fitting located needs filling with fire rated materials. | Raised works order to CBE on 02/12/21 Ref No 1503742. Completed on 06/12/21
2801 | Graeme Bryson Court | GRAEMEBRYS_S001 | H21 | Scheme | 2021-12-01 14:26 | FRA_2801011220211317.pdf | ClarkG | 2801011220211310 | Retirement Housing | Mid East | Merseyside | North | North Patch 3 | ca3vp5e3uqkwnk0j7l | Observation Only | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | M&E Team | PAT testing completed on 24th November 2020 | NULL
2803 | Burrows Court | BURROWS_S001 | H21 | Scheme | 2022-10-07 12:41 | FRA_2803071020221203.pdf | ClarkG | 2803071020221200 | Retirement Housing | Mid East | Merseyside | North | North Patch 3 | csvbk8sydntl8ye1oxj | Observation Only | Risk Closed | 44846.6248 | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | Scheme manager to record false alarms going forward. | Started to record false alarms, the first one being 12/10/22
2804 | Crawshaw Court | CRAWSHAW_S001 | H21 | Scheme | 2022-07-01 13:19 | FRA_2804010720221314.pdf | ClarkG | 2804010720221310 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | bywvvhezpqfl52f6juu | Low Risk closed | Risk Closed | 44903.6107 | Obs10 | Fire Safety And Notices | 45474 | Low | Court Manager | Additional external fire signage required to guide people to the muster point. | installed
2804 | Crawshaw Court | CRAWSHAW_S001 | H21 | Scheme | 2022-07-01 13:19 | FRA_2804010720221314.pdf | ClarkG | 2804010720221310 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | 7uo0fk9jnmbl52f48kv | Low Risk closed | Risk Closed | 44852.3411 | Obs7 | Fire Protection Measures | 45474 | Low | Surveyor | Communal lounge and dining Area's require Door Guards installing. | Works completed by Novus
2804 | Crawshaw Court | CRAWSHAW_S001 | H21 | Scheme | 2022-07-01 13:19 | FRA_2804010720221314.pdf | ClarkG | 2804010720221310 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | fw81blym0acl52f48k5 | Low Risk closed | Risk Closed | 44790.4705 | Obs7 | Fire Protection Measures | 45474 | Low | Surveyor | Communal fire doors adjacent to Flat 36 & 29 do not close fully. | Works completed by Novus
2804 | Crawshaw Court | CRAWSHAW_S001 | H21 | Scheme | 2022-07-01 13:19 | FRA_2804010720221314.pdf | ClarkG | 2804010720221310 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | huu7cjd9vgl52f48lr | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45474 | Low | Court Manager | Flat 50 requires an intumescent strips installing on the top of the door frame. | NULL
2804 | Crawshaw Court | CRAWSHAW_S001 | H21 | Scheme | 2022-07-01 13:19 | FRA_2804010720221314.pdf | ClarkG | 2804010720221310 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | kwklro46qjl52f48mq | Low Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45474 | Low | Court Manager | Training records do not have the dates for the training completion. | NULL
2804 | Crawshaw Court | CRAWSHAW_S001 | H21 | Scheme | 2022-07-01 13:19 | FRA_2804010720221314.pdf | ClarkG | 2804010720221310 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | m1yno8m8jkil52f5q8o | Low Risk closed | Risk Closed | 44852.3415 | Obs10 | Fire Safety And Notices | 45474 | Low | Surveyor | Fire exit signs required in communal lounge and dining area. | No Works required
2806 | Brian Cummings Court | BRIANCUMMINGS_S001 | H21 | Scheme | 2022-06-22 16:01 | FRA_2806220620221231.pdf | ClarkG | 2806220620221230 | Retirement Housing | Mid East | Merseyside | North | North Patch 3 | g76dv3nu3uwl4pim92v | Low Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45465 | Low | Court Manager | Cleaner to complete the Fire Training on FRED. | NULL
2806 | Brian Cummings Court | BRIANCUMMINGS_S001 | H21 | Scheme | 2022-06-22 16:01 | FRA_2806220620221231.pdf | ClarkG | 2806220620221230 | Retirement Housing | Mid East | Merseyside | North | North Patch 3 | 63xw4vugg8cl4pim923 | Low Risk closed | Risk Closed | 44757.4836 | Obs8 | Measures To Limit Fire Spread And Development | 45465 | Low | Court Manager | Door closer needs changing as on Flat 33 & 21 as resident can't open door with closer attached. | Raise repair for the new door closer's on flats 21 and 33. Works completed 15/06/2022
2807 | George Moore Court | GEORGEMOORE_S001 | H21 | Scheme | 2022-07-06 12:06 | FRA_2807060720221151.pdf | ClarkG | 2807060720221150 | Retirement Housing | Mid East | Merseyside | North | North Patch 3 | strfg5a9itl59hdsx3 | Low Risk closed | Risk Closed | 44768.5012 | Obs6 | Fire Hazards - Elimination & Control | 45479 | Low | Court Manager | Boxing in at high level in Kitchen needs fitting back. | Works carried out boxing in at high level in kitchen, fire stopped.
2807 | George Moore Court | GEORGEMOORE_S001 | H21 | Scheme | 2022-07-06 12:06 | FRA_2807060720221151.pdf | ClarkG | 2807060720221150 | Retirement Housing | Mid East | Merseyside | North | North Patch 3 | z9h8jq8ig3l59hr50j | Low Risk closed | Risk Closed | 44760.3528 | Obs6 | Fire Hazards - Elimination & Control | 45479 | Low | Court Manager | Furniture stored in first floor lift lobby needs removing. | Furniture removed
2808 | James Horrigan Court | JAMESHORRIGAN_S001 | H21 | Scheme | 2022-07-01 10:15 | FRA_2808300620221123.pdf | ClarkG | 2808300620221120 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | filfr1opw6vl5109gsg | Low Risk closed | Risk Closed | 44883.461 | Obs2 | Means Of Giving Warning In Case Of Fire | 45473 | Low | Court Manager | Fire detection required in communal corridor between flats 50 - 53. Job has been raised by the court manager with Openview | Works order raised with protect and openview and works completed 20.10.22
2808 | James Horrigan Court | JAMESHORRIGAN_S001 | H21 | Scheme | 2022-07-01 10:15 | FRA_2808300620221123.pdf | ClarkG | 2808300620221120 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | l6zbeh21aol51057tg | Low Risk closed | Risk Closed | 44756.3882 | Obs8 | Measures To Limit Fire Spread And Development | 45473 | Low | Court Manager | Overhead door closer required for flat 48 | Door closer fitted on 12.07.22, now completed.
2809 | Roger Arden Court | ROGERARDEN_S001 | H21 | Scheme | 2022-06-28 13:10 | FRA_2809280620221256.pdf | ClarkG | 2809280620221250 | Retirement Housing | Mid East | Merseyside | North | North Patch 3 | 6pd4ny9kl6fl4y45hfo | Low Risk closed | Risk Closed | 44743.5811 | Obs8 | Measures To Limit Fire Spread And Development | 45471 | Low | Court Manager | Intumescent strips required for flat doors in flats 2, 3 | Works complete
2809 | Roger Arden Court | ROGERARDEN_S001 | H21 | Scheme | 2022-06-28 13:10 | FRA_2809280620221256.pdf | ClarkG | 2809280620221250 | Retirement Housing | Mid East | Merseyside | North | North Patch 3 | 3nx08aw85qol4y45tnp | Low Risk closed | Risk Closed | 44743.5878 | Obs7 | Fire Protection Measures | 45471 | Low | Court Manager | Door Guard on Mobility scooters room door is loose, it needs securing to the door. | All fine
2810 | Edenhurst Court | EDENHURST_S001 | H21 | Scheme | 2022-07-01 13:14 | FRA_2810010720221301.pdf | ClarkG | 2810010720221300 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | a5dea5i7u7kl52f0bi4 | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45474 | Low | Court Manager | Additionally external fire escape signage recommended to guide residents to muster point. | NULL
2810 | Edenhurst Court | EDENHURST_S001 | H21 | Scheme | 2022-07-01 13:14 | FRA_2810010720221301.pdf | ClarkG | 2810010720221300 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | kggrc635tfrl52eose9 | Low Risk closed | Risk Closed | 44882.7409 | Obs6 | Fire Hazards - Elimination & Control | 45474 | Low | Court Manager | MDF board in Communal lobby / Lounge area. This needs removing. | removed
2810 | Edenhurst Court | EDENHURST_S001 | H21 | Scheme | 2022-07-01 13:14 | FRA_2810010720221301.pdf | ClarkG | 2810010720221300 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 3 | ykzhb7z3p9sl52emr3q | Low Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45474 | Low | Court Manager | No completion dates on the training records. | NULL
2811 | Maurice Jones Court | MAURICEJONE_S001 | H21 | Scheme | 2022-07-25 14:31 | FRA_2811250720220731.pdf | JohnsonD | 2811250720220730 | Retirement Housing | Mid East | Merseyside | North | North Patch 7 | mv31thc4n99l60sauct | Medium Risk closed | Risk Closed | 44785.4324 | Obs6 | Fire Hazards - Elimination & Control | 45132 | Medium | Court Manager | Resident at Flat 2 is a heavy smoker. Please monitor in relation to risk. Consider implementation of safety measures such as water filled ashtrays. | Fire brigade attended for a home safety. PCFRA completed. regular contact with resident
2901 | Hayden Court | HAYDEN_S001 | H21 | Scheme | 2022-10-18 12:26 | FRA_2901181020220953.pdf | macpheem | 2901181020220950 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 2 | eg18cam9z7bl9dzef3m | Observation Only | Risk Open | NULL | Obs9 | Escape Lighting | NULL | N/A | Surveyor | Project to upgrade EL planned for coming months. | NULL
2901 | Hayden Court | HAYDEN_S001 | H21 | Scheme | 2022-10-18 12:26 | FRA_2901181020220953.pdf | macpheem | 2901181020220950 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 2 | w0cdt5qgd7gl9e3vhrd | Low Risk closed | Risk Closed | 44865.4102 | Obs6 | Fire Hazards - Elimination & Control | 45583 | Low | Court Manager | PAT testing overdue. Requires booking in. | Checked and PAT testing was done at Hayden Court on 06/01/21 - certificates can be found in G Drive
2901 | Hayden Court | HAYDEN_S001 | H21 | Scheme | 2022-10-18 12:26 | FRA_2901181020220953.pdf | macpheem | 2901181020220950 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 2 | vxh4pvlbm0ml9e2k08o | Observation Only | Risk Closed | 44853.3582 | Obs3 | Details Of Fire Loss | NULL | N/A | Court Manager | 1 Nr fire (May 2022) Contained to one flat kitchen. Limited damage / smoke only. | CM not onsite at time of fire - dealt with by carer, fire extinguisher discharged and subsequently replaced. CM organised disablement of electric hob and oven. FRS plan to do a risk assessment with resident at request of social services who are providing care for resident.
2902 | Lord Walsingham Court | LORDWALS_S001 | H21 | Scheme | 2022-09-29 11:56 | FRA_2902290920221138.pdf | macpheem | 2902290920221130 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 3 | vz0298q81jfl8mxamxr | Observation Only | Risk Closed | 44862.4233 | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | Last EL test - 26/09/22 | Door adjusted near flat 107 by Lee (Blustar) 28/10/22 completed
2902 | Lord Walsingham Court | LORDWALS_S001 | H21 | Scheme | 2022-09-29 11:56 | FRA_2902290920221138.pdf | macpheem | 2902290920221130 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 3 | eklw0i870hul8mxamx7 | Observation Only | Risk Closed | 44862.4228 | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | Last FA test 26/09/22 | Fire draught excluder has been fitted on fire door near flat 80 completed 28/10/22
2902 | Lord Walsingham Court | LORDWALS_S001 | H21 | Scheme | 2022-09-29 11:56 | FRA_2902290920221138.pdf | macpheem | 2902290920221130 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 3 | lux9yinrfehl8mxd02x | Low Risk Overdue | Risk Open | NULL | Obs9 | Escape Lighting | 44777 | Low | Surveyor | Aged EL installations require upgrading. | NULL
2902 | Lord Walsingham Court | LORDWALS_S001 | H21 | Scheme | 2022-09-29 11:56 | FRA_2902290920221138.pdf | macpheem | 2902290920221130 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 3 | g8foblsdx0tl8mxjcxr | Low Risk closed | Risk Closed | 44838.4203 | Obs15 | Management Of Fire Safety | 45564 | Low | Court Manager | Some of the fire action plans on the walls don't have the assembly point details filled in. | all signs now filled in & compliant
2903 | Freestone Court | FREESTONE_S001 | H21 | Scheme | 2022-08-01 11:56 | FRA_2903010820221008.pdf | colej | 2903010820221000 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 3 | m574aykf3wl6al2909 | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45141 | Low | Court Manager | The approved H21 fire action notices are not in place at the manual emergency call points. It is recommended these are implemented to give clarity to both residents and visitors of the procedure and assembly point in the event of a fire. It is suggested that the guest room has a fire action notice on the inside of the door. | NULL
2903 | Freestone Court | FREESTONE_S001 | H21 | Scheme | 2022-08-01 11:56 | FRA_2903010820221008.pdf | colej | 2903010820221000 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 3 | rcj8u1qugpl6amc6uu | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45139 | Medium | Court Manager | The intake cupboard for the warden call equipment has lots of items stored in it. It is recommended that the amount of items are reduced. It is also recommended that the items being stored on top of the network cabinet are removed as soon as possible as this poses a significant risk. All combustible materials need to be away from places of ignition. | NULL
2903 | Freestone Court | FREESTONE_S001 | H21 | Scheme | 2022-08-01 11:56 | FRA_2903010820221008.pdf | colej | 2903010820221000 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 3 | nb8ibmyrtsql6am4dg9 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45505 | Low | Court Manager | The escape route leading from flat 16 to the alternative stairwell by flats 14 & 15 has a bench located on the landing. Although this is not impeding the width of the escape route it could cause a trip hazard in the event of reduced visabilty caused through smoke. It is suggested that the court manager discusses an alternative location within the grounds of the court with the resident. The bench is in memory of a loved one. | NULL
2903 | Freestone Court | FREESTONE_S001 | H21 | Scheme | 2022-08-01 11:56 | FRA_2903010820221008.pdf | colej | 2903010820221000 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 3 | 0h2gcsjd583il6alxw6p | Observation Only | Risk Open | NULL | Obs7 | Fire Protection Measures | NULL | N/A | Court Manager | At the time of inspection it was noted that numerous flats have door mats outside of the front entrance doors. Although these do not impede the escape route widths, they could present a trip hazard in the event of reduced visibility caused from smoke. It is suggested that this is monitored and all matts allowed on the court are not of a thickness exceeding 10-15mm. | NULL
2903 | Freestone Court | FREESTONE_S001 | H21 | Scheme | 2022-08-01 11:56 | FRA_2903010820221008.pdf | colej | 2903010820221000 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 3 | yt64yzh57f8l6aluoxa | Low Risk to be actioned | Risk Open | NULL | Obs1 | The Building | 45141 | Low | Court Manager | It was noted that there is a hole for cables passing from the electrical intake cupboard by flat number 9. This should be sealed with an appropriate intumescent sealant or a sand cement based product to prevent the spread of smoke of fire. | NULL
2904 | Cunningham Court | CUNNINGHAM_S001 | H21 | Scheme | 2021-12-20 11:20 | FRA_2904201220211031.pdf | colej | 2904201220211030 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 3 | uxc0tghan6ekxejipeq | Low Risk closed | Risk Closed | 44551.3742 | Obs6 | Fire Hazards - Elimination & Control | 45280 | Low | Court Manager | The storage of the refuse bins located in close proximity to the boiler room could reconsidered and moved away from the building if possible. However, It was noted that these were not in plain sight that would pose a serious risk of an arson attack. | other places were considered but no alternative found
2904 | Cunningham Court | CUNNINGHAM_S001 | H21 | Scheme | 2021-12-20 11:20 | FRA_2904201220211031.pdf | colej | 2904201220211030 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 3 | 0pnynv9woswkxekhpky | High Risk Closed | Risk Closed | 44552.5988 | Obs8 | Measures To Limit Fire Spread And Development | 44640 | High | Court Manager | Flat 17. The door closer arm is disconnected and needs reinstating to ensure the door fully self closes in the event of a fire. | WO ORDER RAISED
2904 | Cunningham Court | CUNNINGHAM_S001 | H21 | Scheme | 2021-12-20 11:20 | FRA_2904201220211031.pdf | colej | 2904201220211030 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 3 | fbyboxax0jkxek5iqj | Low Risk closed | Risk Closed | 44552.5987 | Obs8 | Measures To Limit Fire Spread And Development | 45280 | Low | Court Manager | Flat 7. The door closer activation cable has come away from the main unit and needs re attaching. | WO been raised
2904 | Cunningham Court | CUNNINGHAM_S001 | H21 | Scheme | 2021-12-20 11:20 | FRA_2904201220211031.pdf | colej | 2904201220211030 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 3 | n5qfizw02ackxejg5cs | Low Risk closed | Risk Closed | 44552.5992 | Obs15 | Management Of Fire Safety | 45280 | Low | Court Manager | There were no visible records of the number of false alarm reports within the fire safety management folder. The court manager advised there were approximately 5 false alarms for activation caused by the cooking of toast. | records to be kept
2904 | Cunningham Court | CUNNINGHAM_S001 | H21 | Scheme | 2021-12-20 11:20 | FRA_2904201220211031.pdf | colej | 2904201220211030 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 3 | qj4906lyzwkxekq3at | High Risk Closed | Risk Closed | 44552.599 | Obs8 | Measures To Limit Fire Spread And Development | 44640 | High | Court Manager | Flat 30. The internal self closing device has been disabled and needs re instating to ensure the door fully self closes in the event of a fire to protect the escape routes. | WO raised
2904 | Cunningham Court | CUNNINGHAM_S001 | H21 | Scheme | 2021-12-20 11:20 | FRA_2904201220211031.pdf | colej | 2904201220211030 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 3 | j6c048evqy8kxejuwjx | High Risk Closed | Risk Closed | 44550.5114 | Obs8 | Measures To Limit Fire Spread And Development | 44257 | High | Court Manager | Flat 2. The door closer arm is missing and requires reinstating to ensure the door self closes fully in the event of A fire to protect the escape route. | this is on order
2905 | Valentine Barker Court | VALENTINEBAR_S001 | H21 | Scheme | 2022-10-24 11:52 | FRA_2905211020220625.pdf | colej | 2905211020220620 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 3 | zr48saa0ianl9mlqidv | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45223 | Medium | Court Manager | The residents store cupboard adjacent to flat 25 and the store adjacent to 37 has a passive vent above the fire door. In the event of a fire this would allow the spread of smoke and fire into the corridor. It is recommended that it is removed and blocked up. It was also noted that there is no fire detection in place and needs to be installed. | NULL
2906 | Bob Carter Court | BOBCART_S001 | H21 | Scheme | 2022-09-14 14:44 | FRA_2906140920221410.pdf | macpheem | 2906140920221410 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 2 | jat8kpeilrml81o0daa | Observation Only | Risk Closed | 44832.641 | Obs14 | Access By Emergency Services | NULL | N/A | Court Manager | The ultimate fire assembly point is the front car park but with zoned evacuation policy residents may assemble internally in an unaffected zone e.g. the communal lounge. | When updating fire risk assessments residents will be advised that if they need to evacuate their zone because of an alarm they can assemble in the lounge if it is not in the affected zone, rather than go outside to the assembly point.
2906 | Bob Carter Court | BOBCART_S001 | H21 | Scheme | 2022-09-14 14:44 | FRA_2906140920221410.pdf | macpheem | 2906140920221410 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 2 | 0cyoiqyzilrl81n54dm | Low Risk closed | Risk Closed | 44889.6267 | Obs11 | Fire Fighting Equipment | 45549 | Low | Court Manager | Flat 30 Misting equipment due to PCRA and Rob Kent-Small (fire safety officer) advice. Installed Oct 2021. Requires maintaining whilst in place. | Service on misting unit completed 24/11/22
2907 | Robert Smith Court | ROBERTSMIT_S001 | H21 | Scheme | 2022-07-25 13:58 | FRA_2907250720221037.pdf | colej | 2907250720221030 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 2 | 6rj7g7mohepl60k27o8 | Observation Only | Risk Open | NULL | Obs9 | Escape Lighting | NULL | N/A | Court Manager | Information purposes only. The previous comment of poor emergency lighting was noted at the last inspection and suggested that it should be upgraded. The communal and emergency lighting has been surveyed and is part of the planned works upgrade for this financial year. | NULL
2907 | Robert Smith Court | ROBERTSMIT_S001 | H21 | Scheme | 2022-07-25 13:58 | FRA_2907250720221037.pdf | colej | 2907250720221030 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 2 | ejve81arx1ml60l8r4s | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45498 | Low | Court Manager | It was noted that the escape door located in the kitchenette leading to the side garden is key operated. It is recommended that the lock is changed to a thumbturn operation to aid exiting in the event of a fire. | NULL
2907 | Robert Smith Court | ROBERTSMIT_S001 | H21 | Scheme | 2022-07-25 13:58 | FRA_2907250720221037.pdf | colej | 2907250720221030 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 2 | dylm3ogxeh7l60mxaso | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45498 | Low | Court Manager | It is recommended that the laundry door lock is changed to a thumbturn operation for ease of escape in the event of a fire. | NULL
2907 | Robert Smith Court | ROBERTSMIT_S001 | H21 | Scheme | 2022-07-25 13:58 | FRA_2907250720221037.pdf | colej | 2907250720221030 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 2 | bphyo741rswl60mmohs | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45498 | Low | Court Manager | The court manager advised that the Fireco door closer battery has failed but an order is placed for the local contractor to rectify. | NULL
2907 | Robert Smith Court | ROBERTSMIT_S001 | H21 | Scheme | 2022-07-25 13:58 | FRA_2907250720221037.pdf | colej | 2907250720221030 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 2 | 8e4wulpmfcml60op6gq | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45498 | Low | Court Manager | The laundry door has intumescent strips missing at tge top and bottom of the hinged edge. These require replacing. | NULL
2907 | Robert Smith Court | ROBERTSMIT_S001 | H21 | Scheme | 2022-07-25 13:58 | FRA_2907250720221037.pdf | colej | 2907250720221030 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 2 | v7iywcm6suil60npwe6 | Medium Risk to be actioned | Risk Open | NULL | Obs9 | Escape Lighting | 45132 | Medium | Surveyor | It was noted during the assessment, there is a central battery emergency lighting system located on the first floor. There is a sky light directly above that has the potential to leak onto the unit. This has been noted by the building surveyor and will be addressed as part of the lighting upgrade works to be managed or removed. | NULL
2908 | Edmund Bacon Court | EDMUNDBACO_S001 | H21 | Scheme | 2022-10-19 11:22 | FRA_2908191020220902.pdf | macpheem | 2908191020220900 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 2 | xs777v4qfhl9ff4wvz | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | 4 Nr residents deemed high risk. Person centred risk assessments done and stored in fire box. | NULL
2908 | Edmund Bacon Court | EDMUNDBACO_S001 | H21 | Scheme | 2022-10-19 11:22 | FRA_2908191020220902.pdf | macpheem | 2908191020220900 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 2 | 5rzwsc92p5ol9ff45oe | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45584 | Low | Court Manager | PAT testing appears overdue. | NULL
2909 | Dennis Sneezum Court | DENNISSNEE_S001 | H21 | Scheme | 2022-11-10 15:39 | FRA_2909091120221359.pdf | colej | 2909091120221350 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 3 | yu8stna70volab7z5jk | High Risk Closed | Risk Closed | 44909.3448 | Obs8 | Measures To Limit Fire Spread And Development | 44967 | High | Court Manager | Door not closing fully into the frame unaided. The door threshold is obstructing the door. This requires minor adjustment. | NEW CARPET GRIPPER IS NOW FITTED
2910 | Edwin Vincent Court | EDWINVINC_S001 | H21 | Scheme | 2022-08-22 13:29 | FRA_2910220820221118.pdf | colej | 2910220820221110 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 2 | v22m7gujkpjl74lv8hc | Observation Only | Risk Open | NULL | Obs1 | The Building | NULL | N/A | Surveyor | Fire compartmentation seems reasonable, with no major issues. There is a zoned evacuation policy with roof space detection. Any unknown failings should not result in a major incident. | NULL
2910 | Edwin Vincent Court | EDWINVINC_S001 | H21 | Scheme | 2022-08-22 13:29 | FRA_2910220820221118.pdf | colej | 2910220820221110 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 2 | 4ib28yp7dfjl74lwmgj | Low Risk closed | Risk Closed | 44840.3462 | Obs6 | Fire Hazards - Elimination & Control | 45526 | Low | Court Manager | The store cupboard adjacent to the Appello server room has a cable hanging down over the doorway. This requires refixing with metal fire resisting clips. | handyman has re-fixed the cable over the door
2910 | Edwin Vincent Court | EDWINVINC_S001 | H21 | Scheme | 2022-08-22 13:29 | FRA_2910220820221118.pdf | colej | 2910220820221110 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 2 | 368em6f2yipl74pacxr | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45160 | Medium | Court Manager | The office door off of the communal lounge does not have a self closing device. It is recommended that one is fitted to ensure the door self closes to protect the communal area if the room is vacated in the event of a fire. | NULL
2910 | Edwin Vincent Court | EDWINVINC_S001 | H21 | Scheme | 2022-08-22 13:29 | FRA_2910220820221118.pdf | colej | 2910220820221110 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 2 | 8adr9u11zail74lv8jj | Observation Only | Risk Open | NULL | Obs11 | Fire Fighting Equipment | NULL | N/A | Surveyor | Fire fighting equipment is adequate for the building and occupants. It is in line with the Housing 21 policy and guidance from our leading authority, Cambridgeshire Fire & Rescue. | NULL
2910 | Edwin Vincent Court | EDWINVINC_S001 | H21 | Scheme | 2022-08-22 13:29 | FRA_2910220820221118.pdf | colej | 2910220820221110 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 2 | 9z258pasf2l74lv8iu | Medium Risk closed | Risk Closed | 44886.5053 | Obs8 | Measures To Limit Fire Spread And Development | 45160 | Medium | Court Manager | Flat 20. The door closer is missing and requires reinstating to ensure the door closes unaided. | handyman has reconnected closer
2910 | Edwin Vincent Court | EDWINVINC_S001 | H21 | Scheme | 2022-08-22 13:29 | FRA_2910220820221118.pdf | colej | 2910220820221110 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 2 | cmr7hmi6r7dl74op1sl | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45160 | Medium | Court Manager | Flat 3. The internal door closer is not operational and requires reinstating to ensure the door closes unaided. | NULL
2910 | Edwin Vincent Court | EDWINVINC_S001 | H21 | Scheme | 2022-08-22 13:29 | FRA_2910220820221118.pdf | colej | 2910220820221110 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 2 | k8elicyoxwhl74lv8ia | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45160 | Medium | Court Manager | Flat 21. The door is dragging on the carpet at the 90 degree position. The door requires an ease and adjust to ensure it self closes unaided. | NULL
2910 | Edwin Vincent Court | EDWINVINC_S001 | H21 | Scheme | 2022-08-22 13:29 | FRA_2910220820221118.pdf | colej | 2910220820221110 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 2 | qghhrvsvfgrl74ombb9 | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45160 | Medium | Court Manager | Flat 12. The internal door closer is not operational and requires reinstating to ensure the door closes unaided. | NULL
2910 | Edwin Vincent Court | EDWINVINC_S001 | H21 | Scheme | 2022-08-22 13:29 | FRA_2910220820221118.pdf | colej | 2910220820221110 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 2 | th778ot1f8bl74lv8k8 | Observation Only | Risk Open | NULL | Obs14 | Access By Emergency Services | NULL | N/A | Surveyor | Acces to the car park and rear of the court is under a low arch too low for a fire engine, however the distance to the far end of the building is not excessive. | NULL
2912 | Terence Airey Court | TERENCEAIRE_S001 | H21 | Scheme | 2022-10-20 13:53 | FRA_2912201020221345.pdf | macpheem | 2912201020221340 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 2 | 8dtf58sznnll9h235mh | Low Risk closed | Risk Closed | 44869.6842 | Obs14 | Access By Emergency Services | 45585 | Low | Court Manager | Prevent parking obstructing turning circle in car park. | sent a letter round to all residents telling them not to park on pavement and to ask visitors not to either
2912 | Terence Airey Court | TERENCEAIRE_S001 | H21 | Scheme | 2022-10-20 13:53 | FRA_2912201020221345.pdf | macpheem | 2912201020221340 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 2 | 65t0o1oh1h8l9h24utp | Observation Only | Risk Closed | 44861.4626 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | 4 Nr recorded residents as high risk. | PCFRA's already completed, info in fire box for emergency services
2912 | Terence Airey Court | TERENCEAIRE_S001 | H21 | Scheme | 2022-10-20 13:53 | FRA_2912201020221345.pdf | macpheem | 2912201020221340 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 2 | 7nfmdhrfkm9l9h235kq | Observation Only | Risk Closed | 44861.4631 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Court Manager | T&G boarded ceiling with fire resistant coating. | None. T&G ceiling in lounge was given a fire resistant coating in 2017 during the makeover
2912 | Terence Airey Court | TERENCEAIRE_S001 | H21 | Scheme | 2022-10-20 13:53 | FRA_2912201020221345.pdf | macpheem | 2912201020221340 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 2 | 771u0ziq2zll9h235lh | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45585 | Low | Court Manager | Missing assembly point details on fire action signs. | NULL
2912 | Terence Airey Court | TERENCEAIRE_S001 | H21 | Scheme | 2022-10-20 13:53 | FRA_2912201020221345.pdf | macpheem | 2912201020221340 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 2 | xjlihd6v23l9h266r8 | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45585 | Low | Court Manager | Mobility scooters charged in communal areas require to be PAT tested. | NULL
2916 | Meadow Walk | MEADOWWALK_S001 | H21 | Scheme | 2022-07-19 17:11 | FRA_2916180720221601.pdf | colej | 2916180720221600 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 1 | yp80jlykwll5qvzb5w | Observation Only | Risk Closed | 44784.3554 | Obs5 | Evacuation Strategy And Training | NULL | N/A | Court Manager | This is continually being populated as new residents occupy the building. | Reported
2916 | Meadow Walk | MEADOWWALK_S001 | H21 | Scheme | 2022-07-19 17:11 | FRA_2916180720221601.pdf | colej | 2916180720221600 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 1 | 62mw1s5ys9l5sd36op | Low Risk closed | Risk Closed | 44784.3549 | Obs6 | Fire Hazards - Elimination & Control | 45492 | Low | Court Manager | It was noted at the time of inspection the external access door to the scooter room does not operate and appears to be locked through a faulty mechanism. The court manager is following this up with the contractors to rectify. | Reported
2916 | Meadow Walk | MEADOWWALK_S001 | H21 | Scheme | 2022-07-19 17:11 | FRA_2916180720221601.pdf | colej | 2916180720221600 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 1 | bd0afgafp5l5s2v0ko | Low Risk closed | Risk Closed | 44784.3556 | Obs10 | Fire Safety And Notices | 45492 | Low | Court Manager | It is recommended that the lift lobbies have additional signage located on all floor outside the lifts stating not to use the lift in the event of a fire. There is currently just a small pictogram on the lift call point that is not overly clear to users. | Reported
2916 | Meadow Walk | MEADOWWALK_S001 | H21 | Scheme | 2022-07-19 17:11 | FRA_2916180720221601.pdf | colej | 2916180720221600 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 1 | spum1sw8iyl5s0g7bg | Medium Risk closed | Risk Closed | 44784.3551 | Obs10 | Fire Safety And Notices | 44762 | Medium | Court Manager | It was noted at the time of inspection the lack of fire action notices displayed around the court. It is recommended these are displayed at all manual call points to alert residents and visitors of what do do in the event of a fire and to identify the main assembly point. | Reported
2916 | Meadow Walk | MEADOWWALK_S001 | H21 | Scheme | 2022-07-19 17:11 | FRA_2916180720221601.pdf | colej | 2916180720221600 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 1 | kg3izmvse2l5s337po | Low Risk closed | Risk Closed | 44784.3553 | Obs7 | Fire Protection Measures | 45492 | Low | Court Manager | It was noted at the time of inspection, numerous properties have door mats outside the front doors. These were observed to have shifted and move away from the doors. These can be considered a trip hazard to people in the event of a fire and smoke filled corridors. It is recommend these are removed.There is no requirement for these once inside the main building. | Reporteď
2980 | Silfield Gardens | SILFIELDGARD_S001 | H21 | Scheme | 2022-11-02 14:48 | FRA_2980021120221015.pdf | colej | 2980021120221010 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 3 | u9r5ng4ihqil9zhgkve | Observation Only | Risk Closed | 44868.4438 | Obs5 | Evacuation Strategy And Training | NULL | N/A | Court Manager | During a training session on 7th January 2021 the requirement of a red fire box was discussed and it was determined it was not necessary at this court due to the setup of the flats. | No action required
2980 | Silfield Gardens | SILFIELDGARD_S001 | H21 | Scheme | 2022-11-02 14:48 | FRA_2980021120221015.pdf | colej | 2980021120221010 | Retirement Housing | East Anglia | Norfolk | Central | Central Patch 3 | 0ucifdy2e6vl9zqasf5 | Low Risk closed | Risk Closed | 44869.5203 | Obs8 | Measures To Limit Fire Spread And Development | 45598 | Low | Court Manager | It has been noted that the furnishings in the communal lounge have no fire retardant labels evident. Due to the age of the furnishings it has been advised they are replaced as part of the proposed makeover decoration programme at the earliest opportunity. | Refurbishment to be done, likely to be next financial year
3001 | Sir John Brown Court | SIRJOHNBROW_S001 | H21 | Scheme | 2022-05-26 16:04 | FRA_3001260520221554.pdf | doerrd | 3001260520221550 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | 6iethow2smtl3n4ywo1 | Low Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45438 | Low | Surveyor | Following a visit from the fire brigade the evacuation plan has been questioned due to compartmentation of the first floor flats these concerns are being discussed with CFRS to clarify if the evac plan has to change. | NULL
3001 | Sir John Brown Court | SIRJOHNBROW_S001 | H21 | Scheme | 2022-05-26 16:04 | FRA_3001260520221554.pdf | doerrd | 3001260520221550 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | 98iu825mfndl3n4zdun | Medium Risk closed | Risk Closed | 44732.5797 | Obs16 | Testing And Maintenance | 45072 | Medium | Court Manager | The lounge electrical cupboard has several holes around consumer units and cable penetrations. These need to be filled with intumescent putty or foam. | Electrical contractor has been out and has applied relevant fire resistant
3001 | Sir John Brown Court | SIRJOHNBROW_S001 | H21 | Scheme | 2022-05-26 16:04 | FRA_3001260520221554.pdf | doerrd | 3001260520221550 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | tt3cqscv3del3n51hce | Medium Risk closed | Risk Closed | 44729.4311 | Obs16 | Testing And Maintenance | 45072 | Medium | Court Manager | The lounge electrical cupboard hasn't got a lock on the door. This needs to be locked to prevent tampering with alarm power supplies. The consumer unit to the flat above is housed in here as well, this would need to be moved to the flat above. | booked MTH maintenance nearest date is 23rd of June to replace lock. waiting for a quote to remove fuse board to clients flat.
3001 | Sir John Brown Court | SIRJOHNBROW_S001 | H21 | Scheme | 2022-05-26 16:04 | FRA_3001260520221554.pdf | doerrd | 3001260520221550 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | m8ur1lh21bml3n4ywpq | Medium Risk closed | Risk Closed | 44729.4285 | Obs15 | Management Of Fire Safety | 45072 | Medium | Court Manager | Fire folder in the fire box needs to be renewed and organised following clarification of the evac policy | fire box renewed asap colour coded as specified from fire officer for easier reading . all access points clear of where evacuation is to be.
3001 | Sir John Brown Court | SIRJOHNBROW_S001 | H21 | Scheme | 2022-05-26 16:04 | FRA_3001260520221554.pdf | doerrd | 3001260520221550 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | vgiindh9x5l3n4ywot | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45072 | Medium | Surveyor | Roof compartmentation between flats is a single layer of plaster board that has damage in areas. Fire evacuation plan may need to be changed to take this into consideration consult with CFRS. | NULL
3002 | Gloucester Court | GLOUCESTER_S001 | H21 | Scheme | 2022-01-28 13:47 | FRA_3002280120221231.pdf | doerrd | 3002280120221230 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | yuvz2qzbd9kyyeu4t9 | Observation Only | Risk Closed | 44732.6807 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Surveyor | Hot works permits are not currently used. A uniform approach is needed from court maintenance contractors and planned maintenance contracts. | Recommended that housing have s suitable procedure.
3002 | Gloucester Court | GLOUCESTER_S001 | H21 | Scheme | 2022-01-28 13:47 | FRA_3002280120221231.pdf | doerrd | 3002280120221230 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | ktx21w0q3m8kyyf3o9y | Low Risk closed | Risk Closed | 44599.4515 | Obs7 | Fire Protection Measures | 45319 | Low | Court Manager | Plug in air fresheners can cause fire risks as they produce heat, hold oil and are plugged into an electrical socket | CM Walked around court and removed any plug in air fresheners. Information for residents not to use in communal areas has been put in February 2022 newsletter
3002 | Gloucester Court | GLOUCESTER_S001 | H21 | Scheme | 2022-01-28 13:47 | FRA_3002280120221231.pdf | doerrd | 3002280120221230 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | pw06mmz7s7ekyyef1l6 | Observation Only | Risk Closed | 44599.3918 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Meter cupboards will only offer protection if they are closed. Please remind residents to secure these closed keys can be supplied. | CM walked around court and made sure all cupboards are secured. Reminder to all residents also included in February 2022 newsletter
3002 | Gloucester Court | GLOUCESTER_S001 | H21 | Scheme | 2022-01-28 13:47 | FRA_3002280120221231.pdf | doerrd | 3002280120221230 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | 5e3p1c3pxo3kyyf0kj7 | Low Risk closed | Risk Closed | 44614.4579 | Obs7 | Fire Protection Measures | 45319 | Low | Court Manager | Door mats are going to cause a potential trip hazard while evacuating or an obstruction for fire fighters. | All residents with door mats which could cause a trip hazard or obstruction whilst evacuating have been asked to remove the mat
3002 | Gloucester Court | GLOUCESTER_S001 | H21 | Scheme | 2022-01-28 13:47 | FRA_3002280120221231.pdf | doerrd | 3002280120221230 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | 3qmn1hounubkyyfjlx1 | Low Risk closed | Risk Closed | 44732.68 | Obs1 | The Building | 45319 | Low | Surveyor | Compartment walls between roof spaces have cable penetrations. This isn't ideal however the detection in all roof spaces mitigated this risk. These should be sealed appropriately when planned maintenance is carried out next. | During future works there will be filled. The risk us an acceptable one in the meantime.
3003 | Cole Court | COLE_S001 | H21 | Scheme | 2022-11-09 11:23 | FRA_3003091120220957.pdf | AndersonV | 3003091120220950 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | 36u7fmdife9la9ic6kr | Medium Risk Overdue | Risk Open | NULL | Obs1 | The Building | 44874 | Medium | Court Manager | Compartment walls need penetrations sealed in communal roof voids | NULL
3003 | Cole Court | COLE_S001 | H21 | Scheme | 2022-11-09 11:23 | FRA_3003091120220957.pdf | AndersonV | 3003091120220950 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | 2mgg77etthyla9itin5 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45605 | Low | Court Manager | Blocks 21-26 and 27-30 compartmentation fire door requires adjusting to ensure it is closing fully into the frame | NULL
3003 | Cole Court | COLE_S001 | H21 | Scheme | 2022-11-09 11:23 | FRA_3003091120220957.pdf | AndersonV | 3003091120220950 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | 6c0ludv077lla9iinn3 | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45605 | Low | Court Manager | No evidence that Mobility scooters are being PAT tested in the scooter store. Please ensure they are included on the next service visit for PAT testing | NULL
3003 | Cole Court | COLE_S001 | H21 | Scheme | 2022-11-09 11:23 | FRA_3003091120220957.pdf | AndersonV | 3003091120220950 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | ohbz78de2bla9hisra | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45239 | Medium | Court Manager | Laundry room door not closing fully into the frame | NULL
3003 | Cole Court | COLE_S001 | H21 | Scheme | 2022-11-09 11:23 | FRA_3003091120220957.pdf | AndersonV | 3003091120220950 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | u2z5loelqila9jq2u9 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45605 | Low | Court Manager | Flats 2,8 & 29 requires adjustments to their front doors | NULL
3006 | Attley Court | ATTLEY_S001 | H21 | Scheme | 2022-09-07 15:49 | FRA_3006070920221540.pdf | doerrd | 3006070920221540 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | r6x0yyiofs7l7rq9sbm | Low Risk closed | Risk Closed | 44903.4316 | Obs6 | Fire Hazards - Elimination & Control | 45542 | Low | Court Manager | A chest of draws is being stored on the landing by flat 24 | Spoke to tenant and drawers have been removed
3006 | Attley Court | ATTLEY_S001 | H21 | Scheme | 2022-09-07 15:49 | FRA_3006070920221540.pdf | doerrd | 3006070920221540 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | ib0liqhzvhql7rq9sc7 | Low Risk closed | Risk Closed | 44851.3986 | Obs6 | Fire Hazards - Elimination & Control | 45542 | Low | Court Manager | An extension lead is being used on the stairlift socket by F32. There are also items stored on this landing that need clearing. | Extension lead removed and stairlift now plugged into socket on the wall. Items have been cleared from landing
3006 | Attley Court | ATTLEY_S001 | H21 | Scheme | 2022-09-07 15:49 | FRA_3006070920221540.pdf | doerrd | 3006070920221540 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | hsxcmklbmcdl7rqd4qe | Medium Risk closed | Risk Closed | 44865.4635 | Obs7 | Fire Protection Measures | 45176 | Medium | Court Manager | The exit door for block 46-51 doesn't open fully leaving the opening with a restricted opening. | Repair completed. Door now opens fully
3006 | Attley Court | ATTLEY_S001 | H21 | Scheme | 2022-09-07 15:49 | FRA_3006070920221540.pdf | doerrd | 3006070920221540 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | 5z9sn66xr43l7rq9sav | Observation Only | Risk Closed | 44841.5165 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Electrical meter boxes are metal but it isn't certain that they will offer half hour protection. | No action required - As per email from Dean Doerr on 7/10/2022
3006 | Attley Court | ATTLEY_S001 | H21 | Scheme | 2022-09-07 15:49 | FRA_3006070920221540.pdf | doerrd | 3006070920221540 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | fa6dz53hg2l7rq9s9t | Low Risk closed | Risk Closed | 44845.5125 | Obs4 | The Occupant - Information Provided By The Court Manager | 45542 | Low | Court Manager | Evacuation plans for the 5 high risk PCFRA residents needs to be completed. | PCFRA's completed and filed in court private file on sharepoint
3006 | Attley Court | ATTLEY_S001 | H21 | Scheme | 2022-09-07 15:49 | FRA_3006070920221540.pdf | doerrd | 3006070920221540 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | xn2ui9k7d68l7rq9s8w | Low Risk closed | Risk Closed | 44865.4638 | Obs1 | The Building | 45542 | Low | Court Manager | Holes are in the ceiling by F41, these need filling. | Holes have now been filled
3010 | Foxfields | FOXFIELDS_S001 | H21 | Scheme | 2022-03-01 15:27 | FRA_3010280220221425.pdf | AndersonV | 3010280220221420 | Extra Care | Extra Care South | EC South 5 | Central | Central Patch 1 | e52ful43k6l06u9gl3 | Low Risk closed | Risk Closed | 44627.4971 | Obs14 | Access By Emergency Services | 44987 | Low | Court Manager | It was noted on the Type 4 FRA that the initial assembly point should be located within the building. This has been agreed to be located within the cafe, the Assistant Court Manager has arranged for the appropriate signage to be displayed and it is noted within the Fire Action Plan. | Sign are in place
3010 | Foxfields | FOXFIELDS_S001 | H21 | Scheme | 2022-03-01 15:27 | FRA_3010280220221425.pdf | AndersonV | 3010280220221420 | Extra Care | Extra Care South | EC South 5 | Central | Central Patch 1 | 8zwf8i32ljl07xrfwe | Low Risk closed | Risk Closed | 44874.5437 | Obs6 | Fire Hazards - Elimination & Control | 45352 | Low | Court Manager | Stairwells should be kept clear and sterile at all times to prevent the risk of fire spread | Please stations have been removed
3010 | Foxfields | FOXFIELDS_S001 | H21 | Scheme | 2022-03-01 15:27 | FRA_3010280220221425.pdf | AndersonV | 3010280220221420 | Extra Care | Extra Care South | EC South 5 | Central | Central Patch 1 | b6xnqox65ycl07zcdz0 | Medium Risk closed | Risk Closed | 44627.5099 | Obs6 | Fire Hazards - Elimination & Control | 44986 | Medium | Court Manager | Outside flat 62 wax burner is plugged into the communal supply. This needs removing and the socket locking to prevent it from being used by residents | Resident spoken to and asked to remove
3010 | Foxfields | FOXFIELDS_S001 | H21 | Scheme | 2022-03-01 15:27 | FRA_3010280220221425.pdf | AndersonV | 3010280220221420 | Extra Care | Extra Care South | EC South 5 | Central | Central Patch 1 | agjjoo1x4gl07zzx7y | Observation Only | Risk Closed | 44637.4565 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Court Manager | AOV's currently screwed shut due to a fault with the rain sensors and mechanisms. This is being investigated by the developers and H21 service contractor. | Reported and meeting arranged with builders
3010 | Foxfields | FOXFIELDS_S001 | H21 | Scheme | 2022-03-01 15:27 | FRA_3010280220221425.pdf | AndersonV | 3010280220221420 | Extra Care | Extra Care South | EC South 5 | Central | Central Patch 1 | h216i4kv0hfl07wscu9 | Observation Only | Risk Closed | 44627.4964 | Obs5 | Evacuation Strategy And Training | NULL | N/A | Court Manager | Staff that have not completed fire safety training are either on maternity leave or long term sick. | Staff information they need to complete training on their return
3010 | Foxfields | FOXFIELDS_S001 | H21 | Scheme | 2022-03-01 15:27 | FRA_3010280220221425.pdf | AndersonV | 3010280220221420 | Extra Care | Extra Care South | EC South 5 | Central | Central Patch 1 | k210kouh5lbl08093vf | Low Risk closed | Risk Closed | 44873.6439 | Obs7 | Fire Protection Measures | 45352 | Low | Court Manager | Compartmentation door beading is damaged and requires replacing adjacent to flaf 27 | Beading have been repast
3010 | Foxfields | FOXFIELDS_S001 | H21 | Scheme | 2022-03-01 15:27 | FRA_3010280220221425.pdf | AndersonV | 3010280220221420 | Extra Care | Extra Care South | EC South 5 | Central | Central Patch 1 | r3ac6kvxtlrl082k042 | Low Risk closed | Risk Closed | 44627.4947 | Obs11 | Fire Fighting Equipment | 44987 | Low | Court Manager | Fire blanket requires fixing to the wall in the commercial kitchen | Blanket back up
3010 | Foxfields | FOXFIELDS_S001 | H21 | Scheme | 2022-03-01 15:27 | FRA_3010280220221425.pdf | AndersonV | 3010280220221420 | Extra Care | Extra Care South | EC South 5 | Central | Central Patch 1 | tapbzqqsgxhl06ucccy | Low Risk closed | Risk Closed | 44701.4507 | Obs14 | Access By Emergency Services | 44987 | Low | Court Manager | External fire assembly point sign needs to be displayed. It has been agreed to relocate the fire assembly point to the rear car park. This needs to be updated in the Fire Action Plan. | Completed
3010 | Foxfields | FOXFIELDS_S001 | H21 | Scheme | 2022-03-01 15:27 | FRA_3010280220221425.pdf | AndersonV | 3010280220221420 | Extra Care | Extra Care South | EC South 5 | Central | Central Patch 1 | ny9sinopyml07xuzae | Low Risk closed | Risk Closed | 44874.544 | Obs8 | Measures To Limit Fire Spread And Development | 45352 | Low | Court Manager | Flats 2, 9 & 7 , 40, 71 excessive gaps to the closing jamb | Being completed as a part of the defects
3010 | Foxfields | FOXFIELDS_S001 | H21 | Scheme | 2022-03-01 15:27 | FRA_3010280220221425.pdf | AndersonV | 3010280220221420 | Extra Care | Extra Care South | EC South 5 | Central | Central Patch 1 | pxudxoqaphql0822oii | Low Risk closed | Risk Closed | 44701.4511 | Obs10 | Fire Safety And Notices | 45352 | Low | Court Manager | Fire Assembly Point sign needs replacing | Completed
3010 | Foxfields | FOXFIELDS_S001 | H21 | Scheme | 2022-03-01 15:27 | FRA_3010280220221425.pdf | AndersonV | 3010280220221420 | Extra Care | Extra Care South | EC South 5 | Central | Central Patch 1 | q0q54cyanbgl0806c5b | Low Risk closed | Risk Closed | 44627.4987 | Obs10 | Fire Safety And Notices | 44987 | Low | Court Manager | Old type fire action notices require removing and replacing with the correct version | Sign removed and New signs put in their place.
3106 | Percy Court | PERCY_S001 | H21 | Scheme | 2022-02-01 16:35 | FRA_3106310120221637.pdf | taylors1 | 3106310120221630 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 1 | nqd832vv4bskz48gunq | Low Risk closed | Risk Closed | 44603.5297 | Obs5 | Evacuation Strategy And Training | 45323 | Low | Court Manager | Copy of fire plan to drop identified folder | The fire plan and risk assessment have been placed into the red fire box at Percy Court.
3106 | Percy Court | PERCY_S001 | H21 | Scheme | 2022-02-01 16:35 | FRA_3106310120221637.pdf | taylors1 | 3106310120221630 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 1 | grd8l57b9t7kz47ks9p | Low Risk closed | Risk Closed | 44614.3689 | Obs8 | Measures To Limit Fire Spread And Development | 45323 | Low | Court Manager | Flat 16 Replace missing smoke seal below hinge | Smoke Seal has been replaced.
3106 | Percy Court | PERCY_S001 | H21 | Scheme | 2022-02-01 16:35 | FRA_3106310120221637.pdf | taylors1 | 3106310120221630 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 1 | idkafsyyw1nkz3tt45p | Low Risk closed | Risk Closed | 44629.6609 | Obs7 | Fire Protection Measures | 44979 | Low | Surveyor | Laundry fire exit door opens inwards however given the number of people and the size of the laundry the risk is mitigated and reduced however this door will be replaced by an outward opening door when the scheme windows are replaced 2022.23 | Door is due for replacement in SIP 22.23 site measured 7.3.22 worksduefor completion July 2022
3107 | Henderson Court | HENDERSON_S001 | H21 | Scheme | 2021-08-23 10:41 | FRA_3107230820211037.pdf | taylors1 | 3107230820211030 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 1 | jahr9fxw9o8ksog3u4o | Low Risk closed | Risk Closed | 44445.4281 | Obs16 | Testing And Maintenance | 45161 | Low | Court Manager | No record of guardian ad-hoc carrying out emergency light testing | Ad hoc carry out monthly emergency lighting checks. See email
3107 | Henderson Court | HENDERSON_S001 | H21 | Scheme | 2021-08-23 10:41 | FRA_3107230820211037.pdf | taylors1 | 3107230820211030 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 1 | m7j2z9u66xhksog3u2r | Medium Risk closed | Risk Closed | 44440.7267 | Obs11 | Fire Fighting Equipment | 44796 | Medium | Court Manager | No fire detection in external laundry building 2no washing machine/driers 1no electric downflow heater extract fan risk medium to high | Openview to quote for works.
3107 | Henderson Court | HENDERSON_S001 | H21 | Scheme | 2021-08-23 10:41 | FRA_3107230820211037.pdf | taylors1 | 3107230820211030 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 1 | eaap9mjibm9ksog3u12 | Observation Only | Risk Closed | 44431.6884 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Court Manager | Refrain from wedging open fire door wedge removed and put into locked understair cupboard | Surveyor removed means of wedding.
3107 | Henderson Court | HENDERSON_S001 | H21 | Scheme | 2021-08-23 10:41 | FRA_3107230820211037.pdf | taylors1 | 3107230820211030 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 1 | dyv8k8u3c1bksog3u3i | Low Risk closed | Risk Closed | 44440.7222 | Obs16 | Testing And Maintenance | 45161 | Low | Court Manager | Fire alarm record book advises of last test by contractor of 29.5.20 or 26.5.20 check records typo | Records show last testing by Openview was 26 05 2021. Typo.0
3107 | Henderson Court | HENDERSON_S001 | H21 | Scheme | 2021-08-23 10:41 | FRA_3107230820211037.pdf | taylors1 | 3107230820211030 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 1 | dluyo13ke9kksog3u44 | Low Risk closed | Risk Closed | 44440.7177 | Obs16 | Testing And Maintenance | 45161 | Low | Court Manager | Contents of red fire box out of date copy of recent FRA to be added and none relevant info removed | AD HOC RUNNING THE BUILDING. No details enclosed from H21 within the fire box. H21 does not have details of residents as under Ad hoc remit.
3107 | Henderson Court | HENDERSON_S001 | H21 | Scheme | 2021-08-23 10:41 | FRA_3107230820211037.pdf | taylors1 | 3107230820211030 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 1 | 49ewg7s877jksog3u1t | Medium Risk closed | Risk Closed | 44440.7201 | Obs9 | Escape Lighting | 44796 | Medium | Court Manager | Check testing has been carried out by managing agent | See email ref ADHOC guardian carrying out weekly checks. Appello has a record.
3201 | Campbell Court | CAMPBELL_S001 | H21 | Scheme | 2022-04-12 11:17 | FRA_3201120420221111.pdf | lofthousei | 3201120420221110 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 4 | 9g6gmfx2xihl1vzhhdi | Observation Only | Risk Closed | 44663.4937 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Court Manager | Detection in flats only linked to Warden Call, not fire panel | No further action required
3201 | Campbell Court | CAMPBELL_S001 | H21 | Scheme | 2022-04-12 11:17 | FRA_3201120420221111.pdf | lofthousei | 3201120420221110 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 4 | sr00wjx973ml1vzm2ck | Observation Only | Risk Closed | 44663.494 | Obs7 | Fire Protection Measures | NULL | N/A | Court Manager | Communal lounge has 2 Fire Exits, plus door to Laundry. 12 First Floor Flats are accessed via 6 stairs (2 flats per stair) | No further action required
3203 | Sycamore Hall | SYCAMOREHALL_S001 | H21 | Scheme | 2022-08-19 14:01 | FRA_3203190820221400.pdf | lofthousei | 3203190820221400 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | 9k0ls9x5y5dl70hbv4d | Low Risk closed | Risk Closed | 44795.3898 | Obs8 | Measures To Limit Fire Spread And Development | 45523 | Low | Court Manager | Cross corridor compartment doors, many are shrinking/warping leading to gaps exceeding 3mm. Adjust door blades to ensure smoke seals are tight on lead edges | works order put in place
3203 | Sycamore Hall | SYCAMOREHALL_S001 | H21 | Scheme | 2022-08-19 14:01 | FRA_3203190820221400.pdf | lofthousei | 3203190820221400 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | e93exmt3oujl70hbv2m | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45523 | Low | Surveyor | Flat entrance doors, letter plate aperture oversized which may compromise integrity of fire resistance. | NULL
3203 | Sycamore Hall | SYCAMOREHALL_S001 | H21 | Scheme | 2022-08-19 14:01 | FRA_3203190820221400.pdf | lofthousei | 3203190820221400 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | 612qijpyphhl70hbv6t | Observation Only | Risk Closed | 44795.3885 | Obs16 | Testing And Maintenance | NULL | N/A | Court Manager | Both AOV control panels have flashing amber warning light. Recent repairs carried out to AOVs have restored working order but cannot resolve warning light! | awaiting feed back on resolution
3203 | Sycamore Hall | SYCAMOREHALL_S001 | H21 | Scheme | 2022-08-19 14:01 | FRA_3203190820221400.pdf | lofthousei | 3203190820221400 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | 5dgvnh6looul70hbv3q | Low Risk closed | Risk Closed | 44795.3874 | Obs8 | Measures To Limit Fire Spread And Development | 45523 | Low | Court Manager | Cross corridor compartment door adjacent to flat 43, main leaf catching on floor - too slow to close. Ease door along bottom edge | works order put in to take off bottom edge of door
3203 | Sycamore Hall | SYCAMOREHALL_S001 | H21 | Scheme | 2022-08-19 14:01 | FRA_3203190820221400.pdf | lofthousei | 3203190820221400 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | 583wxxtmrlnl70hbv52 | Observation Only | Risk Open | NULL | Obs9 | Escape Lighting | NULL | N/A | Surveyor | High number of failed fittings, due to be replaced in 2022 | NULL
3203 | Sycamore Hall | SYCAMOREHALL_S001 | H21 | Scheme | 2022-08-19 14:01 | FRA_3203190820221400.pdf | lofthousei | 3203190820221400 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | wmw1mo0zhgll70hbv5w | Low Risk closed | Risk Closed | 44795.3887 | Obs15 | Management Of Fire Safety | 45523 | Low | Court Manager | Fire Responsibilities Matrix with NYCC to be reviewed and recorded in Fire Safety Management Folder | completed
3204 | Springhill Court | SPRINGHILL_S001 | H21 | Scheme | 2022-06-29 14:57 | FRA_3204290620221456.pdf | lofthousei | 3204290620221450 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | zikccpaz2fl4znvm91 | Low Risk closed | Risk Closed | 44742.7051 | Obs8 | Measures To Limit Fire Spread And Development | 45472 | Low | Court Manager | External letter plate missing to flat 12 | WO raised with Redfern's to supply and fit appropriate letter box.
3204 | Springhill Court | SPRINGHILL_S001 | H21 | Scheme | 2022-06-29 14:57 | FRA_3204290620221456.pdf | lofthousei | 3204290620221450 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | zmfzbuem89l4znvm9z | Low Risk closed | Risk Closed | 44742.705 | Obs8 | Measures To Limit Fire Spread And Development | 45472 | Low | Court Manager | External letter plate broken to flat 22 | WO raised with Redfern's to supply and fit appropriate letter box.
3204 | Springhill Court | SPRINGHILL_S001 | H21 | Scheme | 2022-06-29 14:57 | FRA_3204290620221456.pdf | lofthousei | 3204290620221450 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | 6dsle5tr8dl4znvm8g | Low Risk closed | Risk Closed | 44742.7049 | Obs8 | Measures To Limit Fire Spread And Development | 45472 | Low | Court Manager | External letter plate missing to flat 8 | WO raised with Redfern's to supply and fit appropriate letter box.
3204 | Springhill Court | SPRINGHILL_S001 | H21 | Scheme | 2022-06-29 14:57 | FRA_3204290620221456.pdf | lofthousei | 3204290620221450 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | 6fzj0846my7l4znvmcg | Low Risk closed | Risk Closed | 44742.7102 | Obs8 | Measures To Limit Fire Spread And Development | 45472 | Low | Court Manager | Cross corridor Fire Door adjacent to flat 4, gap along lead edge exceeds 3mm at bottom, adjust doors to ensure tight seal to smoke seal. | WO raised to ease and adjust doors.
3204 | Springhill Court | SPRINGHILL_S001 | H21 | Scheme | 2022-06-29 14:57 | FRA_3204290620221456.pdf | lofthousei | 3204290620221450 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | 34zts93h1kwl4znvmd6 | Low Risk closed | Risk Closed | 44742.7163 | Obs12 | Automatic Fire Systems i.e. Suppression System | 45472 | Low | Court Manager | Remove automatic extinguishers from refuse rooms 3 no. | W O to be raised
3204 | Springhill Court | SPRINGHILL_S001 | H21 | Scheme | 2022-06-29 14:57 | FRA_3204290620221456.pdf | lofthousei | 3204290620221450 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | 03fvcc0j06hel4znvmbb | Low Risk closed | Risk Closed | 44742.7054 | Obs8 | Measures To Limit Fire Spread And Development | 45472 | Low | Court Manager | External letter plate missing to flat 38 | WO raised with Redfern's to supply and fit appropriate letter box.
3204 | Springhill Court | SPRINGHILL_S001 | H21 | Scheme | 2022-06-29 14:57 | FRA_3204290620221456.pdf | lofthousei | 3204290620221450 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | b2nzntuhr7rl4znvm75 | Low Risk closed | Risk Closed | 44742.7038 | Obs6 | Fire Hazards - Elimination & Control | 45472 | Low | Court Manager | No records for scooters, either PAT test or annual service. | WO has been raised with Redfern's to supply and fit appropriate letter box.
3204 | Springhill Court | SPRINGHILL_S001 | H21 | Scheme | 2022-06-29 14:57 | FRA_3204290620221456.pdf | lofthousei | 3204290620221450 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | tsp2y3bh0yl4znvmby | Low Risk closed | Risk Closed | 44742.7098 | Obs8 | Measures To Limit Fire Spread And Development | 45472 | Low | Court Manager | Cross corridor Fire Door adjacent to first floor refuse room, gap on leading edge >4mm, adjust doors to ensure tight seal to smoke seal brush | WO raised with Redfern's to ease and adjust fire doors.
3204 | Springhill Court | SPRINGHILL_S001 | H21 | Scheme | 2022-06-29 14:57 | FRA_3204290620221456.pdf | lofthousei | 3204290620221450 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | r1qweoo6t9l4znvmah | Medium Risk closed | Risk Closed | 44742.7056 | Obs8 | Measures To Limit Fire Spread And Development | 45106 | Medium | Court Manager | Fire rated letter box missing to flat 29 | WO raised with Redfern's to supply and fit appropriate letter box.
3204 | Springhill Court | SPRINGHILL_S001 | H21 | Scheme | 2022-06-29 14:57 | FRA_3204290620221456.pdf | lofthousei | 3204290620221450 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | q8n4tlg0xcl4znvm9j | Low Risk closed | Risk Closed | 44742.7093 | Obs8 | Measures To Limit Fire Spread And Development | 45472 | Low | Court Manager | External letter plate missing to flat 15 | WO raised with Redfern's to supply and fit appropriate letter box.
3204 | Springhill Court | SPRINGHILL_S001 | H21 | Scheme | 2022-06-29 14:57 | FRA_3204290620221456.pdf | lofthousei | 3204290620221450 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | i7hpsvj9lool4znvmaw | Low Risk closed | Risk Closed | 44742.7057 | Obs8 | Measures To Limit Fire Spread And Development | 45472 | Low | Court Manager | External letter plate missing to flat 23 | WO raised with Redfern's to supply and fit appropriate letter box.
3205 | Greyfriars | GREYFRIARS_S001 | H21 | Scheme | 2022-03-08 15:58 | FRA_3205080320221557.pdf | lofthousei | 3205080320221550 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | jk8ssyj24gl0ibgabi | Low Risk closed | Risk Closed | 44698.5308 | Obs15 | Management Of Fire Safety | 45359 | Low | Court Manager | Court Fire Plan requires updating to incorporate staff changes. | updated the file.
3205 | Greyfriars | GREYFRIARS_S001 | H21 | Scheme | 2022-03-08 15:58 | FRA_3205080320221557.pdf | lofthousei | 3205080320221550 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | ptmdjmrj59bl0ibga7j | Observation Only | Risk Closed | 44671.6278 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | 3 high risk persons identified, all located on lower ground floor. None require special measures other than physical assistance. | this information is in the PCFR, stating assistance is required.
3205 | Greyfriars | GREYFRIARS_S001 | H21 | Scheme | 2022-03-08 15:58 | FRA_3205080320221557.pdf | lofthousei | 3205080320221550 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | 2lfa4wyhbqxl0ibgaa7 | Low Risk closed | Risk Closed | 44671.6286 | Obs10 | Fire Safety And Notices | 45001 | Low | Court Manager | Details of assembly point to be inserted on all Fire Action Notices | Have inserted assembly point info on fire notices.
3205 | Greyfriars | GREYFRIARS_S001 | H21 | Scheme | 2022-03-08 15:58 | FRA_3205080320221557.pdf | lofthousei | 3205080320221550 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | 77lz8o6b152l0ibga8c | Low Risk closed | Risk Closed | 44671.6294 | Obs9 | Escape Lighting | 45001 | Low | Court Manager | High frequency of light fittings failing, requiring frequent replacement. | I call redferns and openview to replace lights.
3205 | Greyfriars | GREYFRIARS_S001 | H21 | Scheme | 2022-03-08 15:58 | FRA_3205080320221557.pdf | lofthousei | 3205080320221550 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | ztri6sztpcl0ibgace | Low Risk closed | Risk Closed | 44698.5315 | Obs15 | Management Of Fire Safety | 45359 | Low | Court Manager | Update and maintain training records for NYCC care staff. | records were removed whilst on sick leave, but have started again.
3206 | Limestone View | LIMESTONEVIE_S001 | H21 | Scheme | 2022-09-27 11:08 | FRA_3206270920221104.pdf | PriestleyC | 3206270920221100 | Extra Care | Extra Care North | EC North 4 | North | North Patch 2 | yzfumg2bo0al8k17v6y | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45196 | Medium | Court Manager | Corridor Doors need adjusting adjacent to flat7. Gap too large | NULL
3206 | Limestone View | LIMESTONEVIE_S001 | H21 | Scheme | 2022-09-27 11:08 | FRA_3206270920221104.pdf | PriestleyC | 3206270920221100 | Extra Care | Extra Care North | EC North 4 | North | North Patch 2 | e67866nsz6gl8k1a374 | Medium Risk closed | Risk Closed | 44852.5814 | Obs8 | Measures To Limit Fire Spread And Development | 45196 | Medium | Court Manager | Door closer not operating properly on flat 33. Currently working as hold open instead of free swing | New closer in situ.
3207 | Meadowfields | MEADOWFIELDS_S001 | H21 | Scheme | 2022-03-10 14:27 | FRA_3207100320220959.pdf | lofthousei | 3207100320220950 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | 62rkmlmo2g7l0kunk1g | Low Risk closed | Risk Closed | 44725.4475 | Obs8 | Measures To Limit Fire Spread And Development | 45361 | Low | Court Manager | Fire door to kitchen swing action, unable to confirm adequate fire resistance. Cold smoke seals shearing off. Door requires overhaul & replacement smoke seals. | The smoke strips have been renewed. Job complete
3207 | Meadowfields | MEADOWFIELDS_S001 | H21 | Scheme | 2022-03-10 14:27 | FRA_3207100320220959.pdf | lofthousei | 3207100320220950 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | 16m1o4orn4uil0l2veva | Low Risk closed | Risk Closed | 44679.5602 | Obs8 | Measures To Limit Fire Spread And Development | 45361 | Low | Court Manager | Entrance door to Flat 44: self closer is not set with adequate latching speed, adjust latching speed to ensure consistent full closure. NB, plug to swing-free control is snagging on frame. | Redfern attended door adjusted.
3221 | Bransdale View | BRANSDALEVIEW_S001 | H21 | Scheme | 2022-03-24 10:29 | FRA_3221240320221028.pdf | lofthousei | 3221240320221020 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | 1032tq7jglpnl14uqu3r | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45375 | Low | Other | Recirculation fan to main oven requires regular cleaning of filters | NULL
3221 | Bransdale View | BRANSDALEVIEW_S001 | H21 | Scheme | 2022-03-24 10:29 | FRA_3221240320221028.pdf | lofthousei | 3221240320221020 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | 2tw1ce5mh7ul14uqu63 | Medium Risk to be actioned | Risk Open | NULL | Obs12 | Automatic Fire Systems i.e. Suppression System | 45009 | Medium | Development | Due to major leaks, mist system is currently drained down and decommissioned awaiting repairs under DLP | NULL
3221 | Bransdale View | BRANSDALEVIEW_S001 | H21 | Scheme | 2022-03-24 10:29 | FRA_3221240320221028.pdf | lofthousei | 3221240320221020 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | f0sgvh77m7l14uqu4j | Low Risk closed | Risk Closed | 44701.4108 | Obs8 | Measures To Limit Fire Spread And Development | 45375 | Low | Court Manager | Flat 29 entrance door, gap on lead edge exceeds 3mm - adjust door to even out gaps. Door not closing tight against smoke seal - adjust lockplates to pull door tight. | Tighteeed door
3221 | Bransdale View | BRANSDALEVIEW_S001 | H21 | Scheme | 2022-03-24 10:29 | FRA_3221240320221028.pdf | lofthousei | 3221240320221020 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | nmscn5ygmfrl14uqu1v | Observation Only | Risk Closed | 44655.7095 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | Currently 2 residents using oxygen. Appropriate signs and procedures in place | oxygen users both have stickers out side their apartments - all risk assessments have been completed, PCFRA
3221 | Bransdale View | BRANSDALEVIEW_S001 | H21 | Scheme | 2022-03-24 10:29 | FRA_3221240320221028.pdf | lofthousei | 3221240320221020 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | mljjcdi65il14uqu5b | Low Risk closed | Risk Closed | 44655.71 | Obs10 | Fire Safety And Notices | 45375 | Low | Court Manager | Fire Exit sign required above door from communal kitchen (on kitchen side) | order in place with safelincs 04.04.2022
3221 | Bransdale View | BRANSDALEVIEW_S001 | H21 | Scheme | 2022-03-24 10:29 | FRA_3221240320221028.pdf | lofthousei | 3221240320221020 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | izo99yuv0fl14uqu2s | Low Risk closed | Risk Closed | 44655.6971 | Obs6 | Fire Hazards - Elimination & Control | 45375 | Low | Court Manager | Small fryer supplied by caterer requires fire blanket, located close to fryer. | completed works order 04.04.2022 to safelincs for provision of fire blanket - requested urgent 7day
3222 | Bowland View | BOWLANDVIEW_S001 | H21 | Scheme | 2022-06-28 15:18 | FRA_3222280620221210.pdf | PriestleyC | 3222280620221210 | Extra Care | Extra Care North | EC North 4 | North | North Patch 2 | gjk0g90lohil4y2i6ou | Low Risk closed | Risk Closed | 44763.6995 | Obs10 | Fire Safety And Notices | 45471 | Low | Court Manager | Fie action notices required at MCP'S | notices put up
3222 | Bowland View | BOWLANDVIEW_S001 | H21 | Scheme | 2022-06-28 15:18 | FRA_3222280620221210.pdf | PriestleyC | 3222280620221210 | Extra Care | Extra Care North | EC North 4 | North | North Patch 2 | ljzynb7n4yl4y8zx4f | Low Risk closed | Risk Closed | 44760.3972 | Obs5 | Evacuation Strategy And Training | 45471 | Low | Court Manager | Check Court Manager has carried out relevant FRA training | Fire training done on site 21st april plus all staff have done e learning training
3222 | Bowland View | BOWLANDVIEW_S001 | H21 | Scheme | 2022-06-28 15:18 | FRA_3222280620221210.pdf | PriestleyC | 3222280620221210 | Extra Care | Extra Care North | EC North 4 | North | North Patch 2 | pwqdhgxdq07l4y93hrp | Low Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45471 | Low | M&E Team | Folders required on "G" drive for Bowland view court certificates and inspection docs | NULL
3222 | Bowland View | BOWLANDVIEW_S001 | H21 | Scheme | 2022-06-28 15:18 | FRA_3222280620221210.pdf | PriestleyC | 3222280620221210 | Extra Care | Extra Care North | EC North 4 | North | North Patch 2 | p2uid9lx37l4y2i6pe | Low Risk closed | Risk Closed | 44760.3825 | Obs10 | Fire Safety And Notices | 45471 | Low | Court Manager | Do not use lift in case fire notice required on each level outside lift doors | SIGNS PUT UP ON EACH FLOOR OUTSIDE OF LIFT
3223 | Eller Beck Court | ELLERBECKCOURT_S001 | H21 | Scheme | 2022-10-20 16:09 | FRA_3223201020221546.pdf | PriestleyC | 3223201020221540 | Extra Care | Extra Care North | EC North 4 | North | North Patch 4 | o7eb59uxprl9h7439d | Observation Only | Risk Closed | 44908.6864 | Obs7 | Fire Protection Measures | NULL | N/A | Court Manager | All final exit doors have thumb turn and lever handles. This has been accepted as a managed risk with Cambridge Fire and Rescue service | it was agreed that the final exit doors would remain unlocked but alarmed so that in the event of a fire residents and staff would only need to open the door to get out and not have to manage the thumb turns.
3224 | Fry Court | FRYCOURT_S001 | H21 | Scheme | 2022-07-13 08:58 | FRA_3224120720220946.pdf | whitek2 | 3224120720220940 | Extra Care | Extra Care North | EC North 3 | North | North Patch 8 | ngbqupb9dyl5i5b6nv | High Risk Closed | Risk Closed | 44841.3848 | Obs7 | Fire Protection Measures | 44846 | High | Court Manager | Ground floor laundry door closer not connected requires refixing as a matter of urgency | contractor has fitted a door closure
3224 | Fry Court | FRYCOURT_S001 | H21 | Scheme | 2022-07-13 08:58 | FRA_3224120720220946.pdf | whitek2 | 3224120720220940 | Extra Care | Extra Care North | EC North 3 | North | North Patch 8 | rdoihakan5dl5i5rawf | Medium Risk closed | Risk Closed | 44841.3836 | Obs6 | Fire Hazards - Elimination & Control | 45119 | Medium | Court Manager | Ground floor refuse remove surplus/redundant materials and store refuse trolley in the inner room | Decommissioned to use as store room
3224 | Fry Court | FRYCOURT_S001 | H21 | Scheme | 2022-07-13 08:58 | FRA_3224120720220946.pdf | whitek2 | 3224120720220940 | Extra Care | Extra Care North | EC North 3 | North | North Patch 8 | mfyf488b3esl5i4rigo | Medium Risk closed | Risk Closed | 44909.5581 | Obs7 | Fire Protection Measures | 45119 | Medium | Court Manager | Ajacent to flat 25 Corridor main leaf not closing to make a seal | closes and sealed
3224 | Fry Court | FRYCOURT_S001 | H21 | Scheme | 2022-07-13 08:58 | FRA_3224120720220946.pdf | whitek2 | 3224120720220940 | Extra Care | Extra Care North | EC North 3 | North | North Patch 8 | mqlqpz7zvwnl5i5i6l8 | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45119 | Medium | Court Manager | Remove surplus carpet from service store 5 adjacent to flat 5 | NULL
3224 | Fry Court | FRYCOURT_S001 | H21 | Scheme | 2022-07-13 08:58 | FRA_3224120720220946.pdf | whitek2 | 3224120720220940 | Extra Care | Extra Care North | EC North 3 | North | North Patch 8 | jpmenhsiwtl5i4v14j | Medium Risk closed | Risk Closed | 44909.5577 | Obs7 | Fire Protection Measures | 45119 | Medium | Court Manager | Door leading to staircase floor 1 between flats 25 and 24 require adjustment catching on frame | Frame adjusted
3224 | Fry Court | FRYCOURT_S001 | H21 | Scheme | 2022-07-13 08:58 | FRA_3224120720220946.pdf | whitek2 | 3224120720220940 | Extra Care | Extra Care North | EC North 3 | North | North Patch 8 | alvegugamuvl5i455m7 | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45119 | Medium | Court Manager | Refuse adjacent to flat 45 Ensure surplus / redundant items are disposed of and refuse bin kept in the inner store | NULL
3224 | Fry Court | FRYCOURT_S001 | H21 | Scheme | 2022-07-13 08:58 | FRA_3224120720220946.pdf | whitek2 | 3224120720220940 | Extra Care | Extra Care North | EC North 3 | North | North Patch 8 | 5fxkqfzsv1ll5i5zvcv | Observation Only | Risk Closed | 44756.58 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Observation the temperature in kitchen due to poor ventilation was reported by the staff to have reached 42 degrees yesterday | Advised to open windows and use the air con
3224 | Fry Court | FRYCOURT_S001 | H21 | Scheme | 2022-07-13 08:58 | FRA_3224120720220946.pdf | whitek2 | 3224120720220940 | Extra Care | Extra Care North | EC North 3 | North | North Patch 8 | w69s57qkngl5i5lj6u | Low Risk closed | Risk Closed | 44841.3823 | Obs6 | Fire Hazards - Elimination & Control | 45485 | Low | Court Manager | Repair floor buttons on main lift control | Contractor fitted new buttons
3224 | Fry Court | FRYCOURT_S001 | H21 | Scheme | 2022-07-13 08:58 | FRA_3224120720220946.pdf | whitek2 | 3224120720220940 | Extra Care | Extra Care North | EC North 3 | North | North Patch 8 | vdko5nd309cl5i5enof | Medium Risk closed | Risk Closed | 44756.5854 | Obs6 | Fire Hazards - Elimination & Control | 45119 | Medium | Court Manager | Ensure laundry room dryer fillers are cleaned regularly | All staff have been prompted to check filters as all residents do not know how to do this.
3224 | Fry Court | FRYCOURT_S001 | H21 | Scheme | 2022-07-13 08:58 | FRA_3224120720220946.pdf | whitek2 | 3224120720220940 | Extra Care | Extra Care North | EC North 3 | North | North Patch 8 | xn4fhy00asl5jazrnx | Low Risk closed | Risk Closed | 44783.4371 | Obs10 | Fire Safety And Notices | 45486 | Low | Court Manager | Re-fix fire assembly point sign in carpark | Had the sign re-fitted
3225 | Filey Fields | FILEYFIELDS_S001 | H21 | Scheme | 2022-11-08 13:41 | FRA_3225081120221340.pdf | lofthousei | 3225081120221340 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | xssw37fwqgla89fr32 | Observation Only | Risk Open | NULL | Obs10 | Fire Safety And Notices | NULL | N/A | Development | Mixture of BS type signs used on site. | NULL
3225 | Filey Fields | FILEYFIELDS_S001 | H21 | Scheme | 2022-11-08 13:41 | FRA_3225081120221340.pdf | lofthousei | 3225081120221340 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | 57b0ffoe3mala89fr21 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45604 | Low | Court Manager | Flat 38 not self closing, adjust door or self closer to ensure fully self closing | NULL
3225 | Filey Fields | FILEYFIELDS_S001 | H21 | Scheme | 2022-11-08 13:41 | FRA_3225081120221340.pdf | lofthousei | 3225081120221340 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | 08g09y6qeooala89fr2i | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45604 | Low | Court Manager | Flat 39 door not self closing properly, adjust door or self closer to ensure proper closing via self closer | NULL
3225 | Filey Fields | FILEYFIELDS_S001 | H21 | Scheme | 2022-11-08 13:41 | FRA_3225081120221340.pdf | lofthousei | 3225081120221340 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | df27mb6duyla89fr11 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45604 | Low | Court Manager | Flat 13 Entrance door gaps exceed 3mm adjust door to ensure all gaps 3mm or less. | NULL
3225 | Filey Fields | FILEYFIELDS_S001 | H21 | Scheme | 2022-11-08 13:41 | FRA_3225081120221340.pdf | lofthousei | 3225081120221340 | Extra Care | Extra Care North | EC North 3 | North | North Patch 4 | qd4bzq1ox7la89fr3y | Observation Only | Risk Open | NULL | Obs10 | Fire Safety And Notices | NULL | N/A | Development | Incorrect fire exit signs used at FED's | NULL
3302 | Herbert Buzzard Court | HERBERTBUZZ_S001 | H21 | Scheme | 2022-08-10 16:42 | FRA_3302100820221437.pdf | BatesT | 3302100820221430 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | b43p21en9pdl6ns453e | Medium Risk closed | Risk Closed | 44803.6622 | Obs7 | Fire Protection Measures | 44814 | Medium | Court Manager | Library has no detection | Detection was fitted to the library 30/08/22
3302 | Herbert Buzzard Court | HERBERTBUZZ_S001 | H21 | Scheme | 2022-08-10 16:42 | FRA_3302100820221437.pdf | BatesT | 3302100820221430 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | 28jvkps2odul6np17fv | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45514 | Low | Court Manager | Office has been fitted with battery hold open device - these are not ideal. Recommend that this be replaced with hardwired hold open or free swing closer directly connected to the fire alarm. | NULL
3302 | Herbert Buzzard Court | HERBERTBUZZ_S001 | H21 | Scheme | 2022-08-10 16:42 | FRA_3302100820221437.pdf | BatesT | 3302100820221430 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | 775toji8k59l6npbhwt | Low Risk closed | Risk Closed | 44785.3822 | Obs15 | Management Of Fire Safety | 45514 | Low | Court Manager | Fire safety training not detailed in red book | Printed off new record and completed and filed in red book.
3303 | Lynam Court | LYNAM_S001 | H21 | Scheme | 2022-11-10 13:32 | FRA_3303101120221128.pdf | BatesT | 3303101120221120 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | cqy32lgn6i3lab3l1kb | Low Risk closed | Risk Closed | 44876.398 | Obs8 | Measures To Limit Fire Spread And Development | 45606 | Low | Court Manager | Flat 19 missing smoke seal at top | Seal Fitted by CM on 11/11/2022
3303 | Lynam Court | LYNAM_S001 | H21 | Scheme | 2022-11-10 13:32 | FRA_3303101120221128.pdf | BatesT | 3303101120221120 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | u1yzcm60jp7lab0b9fe | Medium Risk closed | Risk Closed | 44875.6042 | Obs6 | Fire Hazards - Elimination & Control | 45240 | Medium | Court Manager | F9 Has been identified as hoarder and has halogen heater. Has been advised either not to use or to turn off when leaving the room. Fire service referral has been completed. On going discussions with fire service and court manager to aid resident to reduce risk. | Resident has had court manager explain the risks posed by leaving Halogen heater running whilst not in the room, this has been also been disused by the Fire Service during a safe and well visit alongside not allowing cooking to be left unattended. Resident has assured both CM and fire service that she will switch off heater and cooking when not in the room.
3303 | Lynam Court | LYNAM_S001 | H21 | Scheme | 2022-11-10 13:32 | FRA_3303101120221128.pdf | BatesT | 3303101120221120 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | kyrlhfr9sf6lab3lp8o | Low Risk closed | Risk Closed | 44875.6442 | Obs8 | Measures To Limit Fire Spread And Development | 45606 | Low | Court Manager | Flats 20,9 and 7 not pulling to | Flats 7,9,20 all adjusted b CM now fully closing
3303 | Lynam Court | LYNAM_S001 | H21 | Scheme | 2022-11-10 13:32 | FRA_3303101120221128.pdf | BatesT | 3303101120221120 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | l06e5aka2b5lab0wb8z | Low Risk closed | Risk Closed | 44875.5994 | Obs6 | Fire Hazards - Elimination & Control | 45606 | Low | Court Manager | Ideally cleaning staff would check tumble filters weekly, not currently in place. | Introduced a weekly checklist which will document and ensure the filters are checked and cleaned on a weekly basis by CM and cleaner.
3303 | Lynam Court | LYNAM_S001 | H21 | Scheme | 2022-11-10 13:32 | FRA_3303101120221128.pdf | BatesT | 3303101120221120 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | l91wa93l3g5lab3offd | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45606 | Low | Surveyor | Uninterrupted power supply wiring on first floor over communal area could be neater and has spare sockets on wall mounted extension. To be moved to switched fused spurs when site is converted to digital warden call. | NULL
3303 | Lynam Court | LYNAM_S001 | H21 | Scheme | 2022-11-10 13:32 | FRA_3303101120221128.pdf | BatesT | 3303101120221120 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | xl26qzn3edklab3n3oc | Low Risk closed | Risk Closed | 44897.3689 | Obs2 | Means Of Giving Warning In Case Of Fire | 45606 | Low | Court Manager | No detector head in cleaners cupboard in laundry. - recommend one is installed. | New detector fitted by TIS in the cleaning cupboard on 01/12/2022
3304 | Heathcote Court | HEATHCOTE_S001 | H21 | Scheme | 2022-09-05 13:28 | FRA_3304050920221309.pdf | BatesT | 3304050920221300 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | jnr9nx4ytyol7oqmraf | Low Risk closed | Risk Closed | 44819.6461 | Obs7 | Fire Protection Measures | 45540 | Low | Court Manager | No keep shut signage on guest room. | New signs installed on inside and outside of the Guest Room Door.
3304 | Heathcote Court | HEATHCOTE_S001 | H21 | Scheme | 2022-09-05 13:28 | FRA_3304050920221309.pdf | BatesT | 3304050920221300 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | i5t027nsxyql7opzxsj | Low Risk closed | Risk Closed | 44826.6059 | Obs5 | Evacuation Strategy And Training | 45540 | Low | Court Manager | Wardens assigned but not doing regular refresher. | Nominated Persons refresher training on a regular basis.
3304 | Heathcote Court | HEATHCOTE_S001 | H21 | Scheme | 2022-09-05 13:28 | FRA_3304050920221309.pdf | BatesT | 3304050920221300 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | dn1n7ueidcll7opzxti | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45540 | Low | Surveyor | Waste bins all lined up against building. Consider separate storage area. | NULL
3304 | Heathcote Court | HEATHCOTE_S001 | H21 | Scheme | 2022-09-05 13:28 | FRA_3304050920221309.pdf | BatesT | 3304050920221300 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | 96g2cczxwu8l7oqcmk5 | Low Risk closed | Risk Closed | 44845.4159 | Obs8 | Measures To Limit Fire Spread And Development | 45540 | Low | Court Manager | Couple of issues with flat doors to be adjusted | Flat doors adjusted.
3304 | Heathcote Court | HEATHCOTE_S001 | H21 | Scheme | 2022-09-05 13:28 | FRA_3304050920221309.pdf | BatesT | 3304050920221300 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 9 | 3gyny52m877l7opzxup | Low Risk closed | Risk Closed | 44812.517 | Obs7 | Fire Protection Measures | 45540 | Low | Court Manager | Storage cupboards marked keep shut not shut | All storage cupboards now shut - to monitor on a weekly basis.
3305 | George Shooter Court | GEORGESHOO_S001 | H21 | Scheme | 2022-07-26 12:06 | FRA_3305260720221040.pdf | BatesT | 3305260720221040 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | 2kne91rizutl622mk6n | Medium Risk closed | Risk Closed | 44769.6066 | Obs8 | Measures To Limit Fire Spread And Development | 45133 | Medium | Court Manager | Store opposite laundry not pulling to fully on closer. | raised repair job completed today
3305 | George Shooter Court | GEORGESHOO_S001 | H21 | Scheme | 2022-07-26 12:06 | FRA_3305260720221040.pdf | BatesT | 3305260720221040 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | 9gbxs8x9ztwl622hx0j | Low Risk closed | Risk Closed | 44775.3741 | Obs8 | Measures To Limit Fire Spread And Development | 45499 | Low | Court Manager | Office door not pulling fully closed on closer. | magnet fitted to door and closing now
3305 | George Shooter Court | GEORGESHOO_S001 | H21 | Scheme | 2022-07-26 12:06 | FRA_3305260720221040.pdf | BatesT | 3305260720221040 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | esi4lkenhp7l622gtjh | Low Risk closed | Risk Closed | 44769.6028 | Obs10 | Fire Safety And Notices | 45499 | Low | Court Manager | Recommend and action in event of fire sign be added to rear of guest room door. | Notice is now in place
3305 | George Shooter Court | GEORGESHOO_S001 | H21 | Scheme | 2022-07-26 12:06 | FRA_3305260720221040.pdf | BatesT | 3305260720221040 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | ftucrmxmxb8l622e3kb | Low Risk closed | Risk Closed | 44769.6031 | Obs8 | Measures To Limit Fire Spread And Development | 45499 | Low | Court Manager | Some flat doors still have Perco style closers. These can not be adjusted, so should any issues arise recommend replacement with newer style adjustable closers. | I will replace them when they are faulty
3305 | George Shooter Court | GEORGESHOO_S001 | H21 | Scheme | 2022-07-26 12:06 | FRA_3305260720221040.pdf | BatesT | 3305260720221040 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | kal1c069lull622di35 | Low Risk closed | Risk Closed | 44775.3773 | Obs8 | Measures To Limit Fire Spread And Development | 45499 | Low | Court Manager | F26 Drop down to be replaced | raised repair work completed
3305 | George Shooter Court | GEORGESHOO_S001 | H21 | Scheme | 2022-07-26 12:06 | FRA_3305260720221040.pdf | BatesT | 3305260720221040 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | sw1zvqwac74l6206tzs | Low Risk closed | Risk Closed | 44775.5914 | Obs6 | Fire Hazards - Elimination & Control | 45499 | Low | Court Manager | Pat testing for buggies booked in for 27/7/22 | tested today 2/8/22
3305 | George Shooter Court | GEORGESHOO_S001 | H21 | Scheme | 2022-07-26 12:06 | FRA_3305260720221040.pdf | BatesT | 3305260720221040 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | wuieyy76b9bl6203ie2 | Observation Only | Risk Closed | 44778.7513 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Other | No high risk residents at present. arrangements in place and regularly reviewed. | n/a observation only
3305 | George Shooter Court | GEORGESHOO_S001 | H21 | Scheme | 2022-07-26 12:06 | FRA_3305260720221040.pdf | BatesT | 3305260720221040 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | y2ergq8ui6jl622inje | Low Risk closed | Risk Closed | 44775.3847 | Obs8 | Measures To Limit Fire Spread And Development | 45499 | Low | Court Manager | Office door propped open with wedge. Recommend fitting magnet. | Magnet fitted all ok
3306 | Seagrave Court | SEAGRAVE_S001 | H21 | Scheme | 2022-10-06 10:34 | FRA_3306061020220942.pdf | BatesT | 3306061020220940 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 6 | qxu607inm0ul8wtz29c | Observation Only | Risk Open | NULL | Obs9 | Escape Lighting | NULL | N/A | Surveyor | Note Only - lighting changed throughout residential corridors, still to be changed in communal spaces. | NULL
3306 | Seagrave Court | SEAGRAVE_S001 | H21 | Scheme | 2022-10-06 10:34 | FRA_3306061020220942.pdf | BatesT | 3306061020220940 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 6 | f8v9lzk28hkl8wuzrdd | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45205 | Medium | Surveyor | Recommend a full FRA be completed again once makeover works are offsite, within maximum of 6 months. Currently extensive upgrades in place making the it very difficult to review the day to day operation of the site. Currently "keep locked" riser doors are open, but heating engineers are onsite, door furniture from flats missing but joiners onsite, some slight snagging with communal doors but floor layers are onsite. | NULL
3306 | Seagrave Court | SEAGRAVE_S001 | H21 | Scheme | 2022-10-06 10:34 | FRA_3306061020220942.pdf | BatesT | 3306061020220940 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 6 | 9hbkexq6om3l8wu88xw | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45218 | Low | Surveyor | Limited running man signage in communal area. To be reviewed on makeover currently onsite. | NULL
3309 | Colin Broughton Court | COLINBROU_S001 | H21 | Scheme | 2022-10-05 14:27 | FRA_3309051020221306.pdf | BatesT | 3309051020221300 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | anjflzvy659l8vmyi1y | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45204 | Medium | Surveyor | Confirm all fire doors replaced and signed off with FIRAS certification. | NULL
3312 | John Quinn Court | JOHNQUIN_S001 | H21 | Scheme | 2022-11-18 14:21 | FRA_3312181120221350.pdf | BatesT | 3312181120221350 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | r5cdgbf7j3laml4szi | Medium Risk closed | Risk Closed | 44900.6622 | Obs6 | Fire Hazards - Elimination & Control | 45248 | Medium | Court Manager | Cm reports issues with storage in communal areas 31-36. Communal areas to be kept clear as escape routes | Spoke with Resident also in the newsletter
3312 | John Quinn Court | JOHNQUIN_S001 | H21 | Scheme | 2022-11-18 14:21 | FRA_3312181120221350.pdf | BatesT | 3312181120221350 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | s8i8tja8ol9lamkxpvj | Low Risk closed | Risk Closed | 44900.6618 | Obs8 | Measures To Limit Fire Spread And Development | 45614 | Low | Court Manager | Internal door by 27 not pulling to | Door now closing 05/12/22
3312 | John Quinn Court | JOHNQUIN_S001 | H21 | Scheme | 2022-11-18 14:21 | FRA_3312181120221350.pdf | BatesT | 3312181120221350 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | q2qzrc65swjlamka4lk | Low Risk closed | Risk Closed | 44900.6612 | Obs10 | Fire Safety And Notices | 45614 | Low | Court Manager | No running man signage from conservatory | Signs now up in conservatory
3312 | John Quinn Court | JOHNQUIN_S001 | H21 | Scheme | 2022-11-18 14:21 | FRA_3312181120221350.pdf | BatesT | 3312181120221350 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | pbkhmvzps2rlaml1tsq | Low Risk closed | Risk Closed | 44900.6616 | Obs8 | Measures To Limit Fire Spread And Development | 45614 | Low | Court Manager | 31 flat door not pulling to | ADC fixed the door closing properly now 05/12/2022
3312 | John Quinn Court | JOHNQUIN_S001 | H21 | Scheme | 2022-11-18 14:21 | FRA_3312181120221350.pdf | BatesT | 3312181120221350 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | zhvhubjh5tlamk69xi | Observation Only | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Other | Consideration should be given to installing a p6 system alongside the original which would / should reduce unwanted signals should they become an issue. | NULL
3313 | Marian Murdoch Court | MARIANMURD_S001 | H21 | Scheme | 2022-09-28 14:01 | FRA_3313280920221318.pdf | BatesT | 3313280920221310 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | 58dljill2pzl8lmr8vi | Medium Risk closed | Risk Closed | 44897.3417 | Obs8 | Measures To Limit Fire Spread And Development | 45197 | Medium | Court Manager | Office and lounge doors regularly being propped open. Recommend fitting free swing or hold open door closers. | requested TIS to install door closers
3315 | Carroll Gardens | CARROLLGARD_S001 | H21 | Scheme | 2022-10-21 14:17 | FRA_3315211020221402.pdf | BatesT | 3315211020221400 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | 8em7it8it16l9ii551s | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45220 | Medium | Court Manager | BBQ stored in binstore | NULL
3315 | Carroll Gardens | CARROLLGARD_S001 | H21 | Scheme | 2022-10-21 14:17 | FRA_3315211020221402.pdf | BatesT | 3315211020221400 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | ee4ftihn0lsl9ii550o | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45586 | Low | Court Manager | Charger in communal buggy store not pat tested. | NULL
3315 | Carroll Gardens | CARROLLGARD_S001 | H21 | Scheme | 2022-10-21 14:17 | FRA_3315211020221402.pdf | BatesT | 3315211020221400 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | bx577v7y9bdl9ii556e | Low Risk closed | Risk Closed | 44889.5753 | Obs7 | Fire Protection Measures | 45586 | Low | Court Manager | Hairdresser door not closing fully | 109DW015 Dayworks £27.00 To chop hinges in a little as proud. To chop in latch a little as proud. Adjusted the door closer as required. 15/11/2022
3315 | Carroll Gardens | CARROLLGARD_S001 | H21 | Scheme | 2022-10-21 14:17 | FRA_3315211020221402.pdf | BatesT | 3315211020221400 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | rla38j3ugz7l9ii5548 | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45220 | Medium | Court Manager | Paper storage in with pa system and water heater | NULL
3315 | Carroll Gardens | CARROLLGARD_S001 | H21 | Scheme | 2022-10-21 14:17 | FRA_3315211020221402.pdf | BatesT | 3315211020221400 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | rk73t1k14ffl9ii555j | Low Risk closed | Risk Closed | 44876.3719 | Obs7 | Fire Protection Measures | 45226 | Low | Court Manager | Keep locked switch door, unlocked. Only on triangle key, could be converted to normal key. | Door locked. Still on triangle key
3315 | Carroll Gardens | CARROLLGARD_S001 | H21 | Scheme | 2022-10-21 14:17 | FRA_3315211020221402.pdf | BatesT | 3315211020221400 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | thguk18408hl9ii5580 | High Risk Closed | Risk Closed | 44880.6798 | Obs8 | Measures To Limit Fire Spread And Development | 44947 | High | Court Manager | No closer, needs to be fitted asap. | Door closure fitted to exterior of door. 15/11/2022
3315 | Carroll Gardens | CARROLLGARD_S001 | H21 | Scheme | 2022-10-21 14:17 | FRA_3315211020221402.pdf | BatesT | 3315211020221400 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | kfyneul5399l9ii54zk | Low Risk to be actioned | Risk Open | NULL | Obs3 | Details Of Fire Loss | 45586 | Low | Surveyor | Isolate bin shutes from loft spaces. | NULL
3315 | Carroll Gardens | CARROLLGARD_S001 | H21 | Scheme | 2022-10-21 14:17 | FRA_3315211020221402.pdf | BatesT | 3315211020221400 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | mrmqakxr6ol9ii553a | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45220 | Medium | Court Manager | Paper storage with Pac switches. Can't be a storage space. | NULL
3315 | Carroll Gardens | CARROLLGARD_S001 | H21 | Scheme | 2022-10-21 14:17 | FRA_3315211020221402.pdf | BatesT | 3315211020221400 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | hhpuy741vbgl9ii552l | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45586 | Low | Court Manager | Fire door in bin store not pulling to. 1st floor by lift. | NULL
3315 | Carroll Gardens | CARROLLGARD_S001 | H21 | Scheme | 2022-10-21 14:17 | FRA_3315211020221402.pdf | BatesT | 3315211020221400 | Retirement Housing | Mid East | Derbyshire and Nottinghamshire | Central | Central Patch 6 | ve17novz2rcl9ii5570 | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45220 | Medium | Court Manager | Fire detector loose | NULL
3401 | Amos Court | AMOS_S001 | H21 | Scheme | 2022-07-12 11:48 | FRA_3401120720220844.pdf | AndersonV | 3401120720220840 | Retirement Housing | Mid South | Glos Oxford and South Bucks | Central | Central Patch 7 | oxfc8ncnm1el5i0njrd | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45119 | Medium | Court Manager | Flat 3 stores a scooter in the communal area (open to fresh air) Suitable means of storing and charging the unit need to be made. It also needs to be ensured that the scooter is PAT tested on the next service in November | NULL
3401 | Amos Court | AMOS_S001 | H21 | Scheme | 2022-07-12 11:48 | FRA_3401120720220844.pdf | AndersonV | 3401120720220840 | Retirement Housing | Mid South | Glos Oxford and South Bucks | Central | Central Patch 7 | d1nf0m6g686l5i06ant | Observation Only | Risk Closed | 44824.3812 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Surveyor | All flat doors open onto fresh air and therefore do not require FD30 fire doors. | No further action was required
3401 | Amos Court | AMOS_S001 | H21 | Scheme | 2022-07-12 11:48 | FRA_3401120720220844.pdf | AndersonV | 3401120720220840 | Retirement Housing | Mid South | Glos Oxford and South Bucks | Central | Central Patch 7 | echbn3pvvy5l5hzu7n3 | Observation Only | Risk Closed | 44824.3816 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Surveyor | Evidence of UV / weather damage to external fire alarm cables | To monitor the situation as there are currently no faults with the system
3402 | Stanbridge House | STANBRIDGEHOUS_S001 | H21 | Scheme | 2022-05-12 15:28 | FRA_3402110520221548.pdf | AndersonV | 3402110520221540 | Extra Care | Extra Care South | EC South 3 | Central | Central Patch 7 | d7mfdvly64il333p8ol | Medium Risk closed | Risk Closed | 44797.7558 | Obs8 | Measures To Limit Fire Spread And Development | 45058 | Medium | Court Manager | Flat fire doors need to be checked on a regular basis to ensure they are compliant. Please refer to the list of random doors that were selected today for inspection and action the repairs as necessary. | All repairs completed 19/08/2022
3402 | Stanbridge House | STANBRIDGEHOUS_S001 | H21 | Scheme | 2022-05-12 15:28 | FRA_3402110520221548.pdf | AndersonV | 3402110520221540 | Extra Care | Extra Care South | EC South 3 | Central | Central Patch 7 | b8daxtod0edl3325wzc | Observation Only | Risk Closed | 44818.6767 | Obs1 | The Building | NULL | N/A | Court Manager | It is noted that the exit staircase leading to the old day care centre is currently out of use due to construction works. Residents are aware that this is not currently a means of escape from the building and have been advised to use the nearest alternative in the event that an evacuation may be required. The staircase is due to be reopened and accessible within the next few weeks. | This is now open 9th September 2022
3402 | Stanbridge House | STANBRIDGEHOUS_S001 | H21 | Scheme | 2022-05-12 15:28 | FRA_3402110520221548.pdf | AndersonV | 3402110520221540 | Extra Care | Extra Care South | EC South 3 | Central | Central Patch 7 | 28hxwsvlabjil32v0aet | Medium Risk closed | Risk Closed | 44824.381 | Obs6 | Fire Hazards - Elimination & Control | 45058 | Medium | Surveyor | 1st Floor comms cupboard. Excessive heat from warden call server, ventilation needs to be provided in this area. | Air con unit has now been fitted
3402 | Stanbridge House | STANBRIDGEHOUS_S001 | H21 | Scheme | 2022-05-12 15:28 | FRA_3402110520221548.pdf | AndersonV | 3402110520221540 | Extra Care | Extra Care South | EC South 3 | Central | Central Patch 7 | jtms2t5yoml3334l6t | Low Risk to be actioned | Risk Open | NULL | Obs14 | Access By Emergency Services | 45424 | Low | Court Manager | An initial assembly point should be located within the building. The location of this needs to be agreed with the Court Manager with the appropriate signage being displayed. This will also need to be noted in the Fire Action Plan. | NULL
3402 | Stanbridge House | STANBRIDGEHOUS_S001 | H21 | Scheme | 2022-05-12 15:28 | FRA_3402110520221548.pdf | AndersonV | 3402110520221540 | Extra Care | Extra Care South | EC South 3 | Central | Central Patch 7 | w8byw2dityl32vcwr9 | Medium Risk closed | Risk Closed | 44824.3807 | Obs7 | Fire Protection Measures | 45058 | Medium | Surveyor | 1st Floor meter room check fire stopping is adequate to mains cable and service pipes | The floor is fire stopped from the ceiling above. No further action required
3402 | Stanbridge House | STANBRIDGEHOUS_S001 | H21 | Scheme | 2022-05-12 15:28 | FRA_3402110520221548.pdf | AndersonV | 3402110520221540 | Extra Care | Extra Care South | EC South 3 | Central | Central Patch 7 | xp0c53plxbil32smhfb | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45058 | Medium | Court Manager | The designated smoking area needs to be located away from the bin store | NULL
3406 | Frank Cook Court | FRANKCOOK_S001 | H21 | Scheme | 2022-08-12 11:11 | FRA_3406120820220935.pdf | pickfordj | 3406120820220930 | Retirement Housing | Mid South | Glos Oxford and South Bucks | South | South Patch 4 | naw322i3zb8l6qadsld | Observation Only | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Other | Windows | NULL
3406 | Frank Cook Court | FRANKCOOK_S001 | H21 | Scheme | 2022-08-12 11:11 | FRA_3406120820220935.pdf | pickfordj | 3406120820220930 | Retirement Housing | Mid South | Glos Oxford and South Bucks | South | South Patch 4 | p7h4yek66tkl6qb0qej | Medium Risk closed | Risk Closed | 44791.4891 | Obs6 | Fire Hazards - Elimination & Control | 45150 | Medium | Court Manager | One set of refuse bins stored against the building. These need to be removed away from building due to lack of arson adequate security | Bins removed from against the building.
3406 | Frank Cook Court | FRANKCOOK_S001 | H21 | Scheme | 2022-08-12 11:11 | FRA_3406120820220935.pdf | pickfordj | 3406120820220930 | Retirement Housing | Mid South | Glos Oxford and South Bucks | South | South Patch 4 | qf9dy969qcl6qa81k2 | Medium Risk closed | Risk Closed | 44791.5346 | Obs15 | Management Of Fire Safety | 45150 | Medium | Court Manager | Cm to put up details on communal board regards stay put/early warning procedure for visitors | Signs put up for visitors on noticeboard and in guest room.
3406 | Frank Cook Court | FRANKCOOK_S001 | H21 | Scheme | 2022-08-12 11:11 | FRA_3406120820220935.pdf | pickfordj | 3406120820220930 | Retirement Housing | Mid South | Glos Oxford and South Bucks | South | South Patch 4 | re5abpqsnil6qaxu6n | Medium Risk closed | Risk Closed | 44845.6494 | Obs8 | Measures To Limit Fire Spread And Development | 45150 | Medium | Court Manager | 14 and 12 missing cold smoke seal | New smoke seals fitted.
3407 | Brooks-Taylor Court | BROOKSTAYL_S001 | H21 | Scheme | 2022-02-16 10:26 | FRA_3407150220221626.pdf | AhmadW | 3407150220221620 | Retirement Housing | Mid South | Glos Oxford and South Bucks | South | South Patch 4 | x28vsnhyzgikzpen7h5 | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 44973 | Medium | Court Manager | Various door repairs to be carried out, as per separate report sent to the CM. | NULL
3411 | Erdington House | ERDINGTONHOUS_S001 | H21 | Scheme | 2022-03-08 11:13 | FRA_3411080320221011.pdf | AhmadW | 3411080320221010 | Extra Care | Extra Care South | EC South 3 | South | South Patch 4 | 7n7x1hcv41tl0hzitis | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45359 | Low | Court Manager | Adjust following doors Slave door by lift (office side), not closing. | NULL
3413 | Willow Gardens | WILLOWGARDENS_S001 | H21 | Scheme | 2022-04-28 15:31 | FRA_3413280420220946.pdf | AndersonV | 3413280420220940 | Extra Care | Extra Care South | EC South 3 | South | South Patch 1 | ec0cwiz9grpl2irl5xs | Observation Only | Risk Closed | 44691.4692 | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | Flat 2 had issue with faulty detector which activated the fire alarm, the issue has now been resolved | Appello contacted and unit has been replaced
3413 | Willow Gardens | WILLOWGARDENS_S001 | H21 | Scheme | 2022-04-28 15:31 | FRA_3413280420220946.pdf | AndersonV | 3413280420220940 | Extra Care | Extra Care South | EC South 3 | South | South Patch 1 | rdu35lowgrjl2is54a9 | Medium Risk closed | Risk Closed | 44691.4696 | Obs7 | Fire Protection Measures | 45044 | Medium | Court Manager | Carpet remnant at bottom of staircase outside lift lobby requires removing as this causes a trip hazard along the escape route | carpet has now been removed
3413 | Willow Gardens | WILLOWGARDENS_S001 | H21 | Scheme | 2022-04-28 15:31 | FRA_3413280420220946.pdf | AndersonV | 3413280420220940 | Extra Care | Extra Care South | EC South 3 | South | South Patch 1 | rcd2b3a5btnl2iuigou | Medium Risk closed | Risk Closed | 44691.4694 | Obs7 | Fire Protection Measures | 45044 | Medium | Court Manager | The Scooter store should be kept clear and sterile at all times to prevent the risk of fire spread | scooter room has now been cleared
3413 | Willow Gardens | WILLOWGARDENS_S001 | H21 | Scheme | 2022-04-28 15:31 | FRA_3413280420220946.pdf | AndersonV | 3413280420220940 | Extra Care | Extra Care South | EC South 3 | South | South Patch 1 | thobuf2acaal2it0hx3 | Low Risk closed | Risk Closed | 44732.6671 | Obs7 | Fire Protection Measures | 45410 | Low | Court Manager | Top floor refuse room requires clearing of combustible materials and should be kept clear and sterile at all times | Room cleared, shelving fitted and room tidied
3413 | Willow Gardens | WILLOWGARDENS_S001 | H21 | Scheme | 2022-04-28 15:31 | FRA_3413280420220946.pdf | AndersonV | 3413280420220940 | Extra Care | Extra Care South | EC South 3 | South | South Patch 1 | qo1ip0hcodbl2j317ns | Medium Risk closed | Risk Closed | 44791.377 | Obs8 | Measures To Limit Fire Spread And Development | 44957 | Medium | Development | Following the fire stopping survey that was carried out 31.1.2022, it was identified that some areas required further works. Namely Fire Barrier boarding, breaches to sprinkler pipes within a compartment, and joints that require resealiing to thermal boarding. Clarification has been sought from Development in relation to the status of these defects with Deeley's. | Complete - Lisa Ord confirmed via email on 15th August 2022
3413 | Willow Gardens | WILLOWGARDENS_S001 | H21 | Scheme | 2022-04-28 15:31 | FRA_3413280420220946.pdf | AndersonV | 3413280420220940 | Extra Care | Extra Care South | EC South 3 | South | South Patch 1 | gifjczcdflwl2ivbnnk | Low Risk closed | Risk Closed | 44691.4717 | Obs10 | Fire Safety And Notices | 45410 | Low | Court Manager | No smoking signage should be displayed at each common entrance | signs have now been displayed at every entrance
3501 | Richard Onslow Court | RICHARDONSL_S001 | H21 | Scheme | 2022-09-06 23:59 | FRA_3501060920221221.pdf | HallS | 3501060920221220 | Retirement Housing | Mid West | Staffordshire | Central | Central Patch 4 | iaftevuj2zsl7qqb2e2 | Medium Risk closed | Risk Closed | 44897.4065 | Obs6 | Fire Hazards - Elimination & Control | 45175 | Medium | Court Manager | There are currently several trailing leads and extension cables being utilised within the Court Managrrs office. I recommend that the Court Manager raise an order for dado trunking to be installed within the office with a sufficient amount of sockets to accomodate the necessary office equipment. | dado trunking now fitted.
3501 | Richard Onslow Court | RICHARDONSL_S001 | H21 | Scheme | 2022-09-06 23:59 | FRA_3501060920221221.pdf | HallS | 3501060920221220 | Retirement Housing | Mid West | Staffordshire | Central | Central Patch 4 | sjk15tqr48l7q7wzm8 | Medium Risk to be actioned | Risk Open | NULL | Obs9 | Escape Lighting | 45175 | Medium | Court Manager | There are 5 high level emergency lights located above each stairwell within each residential block and one has failed and requiring repair / replacement. Due to their location and height, access towers will be required and therefore the initial repair quotation is high. The court manager has been advised to approach alternative contractors for additional and hopefully more cost effective quotations. As the failed light illuminates a change in levels, I have asked the Court Manager to arrange rectification within the next month. | NULL
3501 | Richard Onslow Court | RICHARDONSL_S001 | H21 | Scheme | 2022-09-06 23:59 | FRA_3501060920221221.pdf | HallS | 3501060920221220 | Retirement Housing | Mid West | Staffordshire | Central | Central Patch 4 | 9kcnpbk4ciul7qsbyv4 | Low Risk closed | Risk Closed | 44830.4535 | Obs6 | Fire Hazards - Elimination & Control | 45541 | Low | Court Manager | There is a scooter stored and charged within the communal garage. The garage is equipped with detection for early warning. However, the scooter has not been PAT tested, in part due to the pandemic. I have advised the Court Manager to ensure that the scooter is included within the next scheduled PAT test. | PAT tester on site Friday 23rd, owner of scooter advised that the charger is kept in his garage and the scooter is only ever charged in his garage. PAT tester advised they only pat test the chargers so as it is not stored in the communal garage it would not need testing.
3501 | Richard Onslow Court | RICHARDONSL_S001 | H21 | Scheme | 2022-09-06 23:59 | FRA_3501060920221221.pdf | HallS | 3501060920221220 | Retirement Housing | Mid West | Staffordshire | Central | Central Patch 4 | 0ela0s10f2ocl7q66v4q | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45541 | Low | Court Manager | One resident and their visitors have continually breached the no smoking policy with the communal area. This is being addressed as part of a wider issue. Court Manager to confirm once this issue has been resolved. | NULL
3505 | Guy Thornycroft Court | GUYTHOR_S001 | H21 | Scheme | 2022-01-19 12:38 | FRA_3505190120221042.pdf | HallS | 3505190120221040 | Retirement Housing | Mid West | Staffordshire | Central | Central Patch 4 | 6pgpedud79mkylidhs4 | Observation Only | Risk Closed | 44629.4924 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Court Manager | There is no part 6 detection linked to the warden call. I therefore reccomend that when the fire alarm system is upgraded that pt 6 devices linked to warden call are included. This comment is advisory only. | Pt 6 devices will be linked to call system when fire alarm system is upgraded
3505 | Guy Thornycroft Court | GUYTHOR_S001 | H21 | Scheme | 2022-01-19 12:38 | FRA_3505190120221042.pdf | HallS | 3505190120221040 | Retirement Housing | Mid West | Staffordshire | Central | Central Patch 4 | wz4zfcwqkekyli369q | Low Risk closed | Risk Closed | 44634.6522 | Obs2 | Means Of Giving Warning In Case Of Fire | 45310 | Low | Court Manager | Since the last fire alarm system test by the service contractor openview, the fire zones have been accidentally deleted from the fire panel. So now when testing or on activation, the entire court is alerted. This requires reinstatement even though there is not a fault displayed on the fire panel. | TIS have attended site and carried out a full reprogram of the fire panel and reinstated the correct zoning on work order 1524443
3601 | Leonard Houlden Court | LEONARDHOUL_S001 | H21 | Scheme | 2022-01-17 13:00 | FRA_3601170120221146.pdf | BoardP | 3601170120221140 | Retirement Housing | South West | Devon Cornwall and South West Somerset | South | South Patch 9 | sq3k63412tpkyin9zik | Low Risk closed | Risk Closed | 44761.364 | Obs10 | Fire Safety And Notices | 45308 | Low | Court Manager | Install new fire assembly point sign | Installed new fire assembly point sign
3604 | Douglas Yates Court | DOUGLASYATE_S001 | H21 | Scheme | 2022-10-04 12:26 | FRA_3604041020221129.pdf | fowlerb1 | 3604041020221120 | Retirement Housing | South West | North East Somerset Wilts and Avon | South | South Patch 2 | qvkjg5k4nyl8u2ur9c | Observation Only | Risk Closed | 44852.3447 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Surveyor | FFE for information only | For information only
3604 | Douglas Yates Court | DOUGLASYATE_S001 | H21 | Scheme | 2022-10-04 12:26 | FRA_3604041020221129.pdf | fowlerb1 | 3604041020221120 | Retirement Housing | South West | North East Somerset Wilts and Avon | South | South Patch 2 | hh07rj482ynl8u40sjf | Observation Only | Risk Closed | 44852.3449 | Obs10 | Fire Safety And Notices | NULL | N/A | Surveyor | Fire action notices for information only | For information only
3604 | Douglas Yates Court | DOUGLASYATE_S001 | H21 | Scheme | 2022-10-04 12:26 | FRA_3604041020221129.pdf | fowlerb1 | 3604041020221120 | Retirement Housing | South West | North East Somerset Wilts and Avon | South | South Patch 2 | 1xl3eq6wx8pl8u2fark | Observation Only | Risk Closed | 44852.345 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel for information only | For information only
3605 | Clifford Ashman Court | CLIFFORDASHM_S001 | H21 | Scheme | 2022-01-25 12:11 | FRA_3605250120221031.pdf | BoardP | 3605250120221030 | Retirement Housing | South West | Devon Cornwall and South West Somerset | South | South Patch 9 | 5wtpgqt7a8lkytzop75 | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | No high risk residents identified at the scheme. | NULL
3608 | Treasure Court | TREASURE_S001 | H21 | Scheme | 2022-01-12 12:09 | FRA_3608120120221036.pdf | BoardP | 3608120120221030 | Retirement Housing | South West | North East Somerset Wilts and Avon | South | South Patch 9 | 9jajwkd3wo5kybgh9ku | Low Risk closed | Risk Closed | 44746.3777 | Obs14 | Access By Emergency Services | 45303 | Low | Court Manager | Install new assembly point sign | new sign installed
3608 | Treasure Court | TREASURE_S001 | H21 | Scheme | 2022-01-12 12:09 | FRA_3608120120221036.pdf | BoardP | 3608120120221030 | Retirement Housing | South West | North East Somerset Wilts and Avon | South | South Patch 9 | 9jajwkd3wo5kybgh9ku | Low Risk closed | Risk Closed | 44818.6814 | Obs14 | Access By Emergency Services | 45303 | Low | Court Manager | Install new assembly point sign | Sign replaced
3608 | Treasure Court | TREASURE_S001 | H21 | Scheme | 2022-01-12 12:09 | FRA_3608120120221036.pdf | BoardP | 3608120120221030 | Retirement Housing | South West | North East Somerset Wilts and Avon | South | South Patch 9 | 9jajwkd3wo5kybgh9ku | Low Risk closed | Risk Closed | 44790.693 | Obs14 | Access By Emergency Services | 45303 | Low | Court Manager | Install new assembly point sign | Sign replaced
3617 | Diamond Court | DIAMOND_S001 | H21 | Scheme | 2022-01-25 11:06 | FRA_3617250120221013.pdf | fowlerb1 | 3617250120221010 | Extra Care | Extra Care Central | EC Central 1 | South | South Patch 2 | 8mni1uwvbygkyu01q9q | Observation Only | Risk Closed | 44649.3675 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Surveyor | Staircase window | This is information only
3617 | Diamond Court | DIAMOND_S001 | H21 | Scheme | 2022-01-25 11:06 | FRA_3617250120221013.pdf | fowlerb1 | 3617250120221010 | Extra Care | Extra Care Central | EC Central 1 | South | South Patch 2 | amivkdoy7wvkytyouex | Observation Only | Risk Closed | 44649.3677 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel for info only | This is information only
3617 | Diamond Court | DIAMOND_S001 | H21 | Scheme | 2022-01-25 11:06 | FRA_3617250120221013.pdf | fowlerb1 | 3617250120221010 | Extra Care | Extra Care Central | EC Central 1 | South | South Patch 2 | c9f4139kdwckytz2skr | Medium Risk closed | Risk Closed | 44593.4108 | Obs6 | Fire Hazards - Elimination & Control | 44951 | Medium | Court Manager | Fire risk assessment to be supplied by the catering contractor | Discussion with contractor and fire risk assessment updated
3617 | Diamond Court | DIAMOND_S001 | H21 | Scheme | 2022-01-25 11:06 | FRA_3617250120221013.pdf | fowlerb1 | 3617250120221010 | Extra Care | Extra Care Central | EC Central 1 | South | South Patch 2 | 61468a0oxv8kyu043wa | Observation Only | Risk Closed | 44649.3681 | Obs10 | Fire Safety And Notices | NULL | N/A | Surveyor | Fire action notices | This is information only
3617 | Diamond Court | DIAMOND_S001 | H21 | Scheme | 2022-01-25 11:06 | FRA_3617250120221013.pdf | fowlerb1 | 3617250120221010 | Extra Care | Extra Care Central | EC Central 1 | South | South Patch 2 | 26nqzeaahckyu06psz | Observation Only | Risk Closed | 44649.3679 | Obs11 | Fire Fighting Equipment | NULL | N/A | Surveyor | P50 | This is information only
3617 | Diamond Court | DIAMOND_S001 | H21 | Scheme | 2022-01-25 11:06 | FRA_3617250120221013.pdf | fowlerb1 | 3617250120221010 | Extra Care | Extra Care Central | EC Central 1 | South | South Patch 2 | 3ql1i4my6imkytyn9gu | Observation Only | Risk Closed | 44649.3684 | Obs1 | The Building | NULL | N/A | Surveyor | Cedar cladding | This is information only
3617 | Diamond Court | DIAMOND_S001 | H21 | Scheme | 2022-01-25 11:06 | FRA_3617250120221013.pdf | fowlerb1 | 3617250120221010 | Extra Care | Extra Care Central | EC Central 1 | South | South Patch 2 | 0awfz5rohtnikyu09km1 | Observation Only | Risk Closed | 44832.4421 | Obs14 | Access By Emergency Services | NULL | N/A | Surveyor | Fire assembly point to be relocated upon completion of extension | Information only
3617 | Diamond Court | DIAMOND_S001 | H21 | Scheme | 2022-01-25 11:06 | FRA_3617250120221013.pdf | fowlerb1 | 3617250120221010 | Extra Care | Extra Care Central | EC Central 1 | South | South Patch 2 | ifxtr2ioojlkytyvkc5 | Observation Only | Risk Closed | 44649.3682 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Surveyor | GF electric meters | This is information only
3618 | Strawberry Gardens | STRAWBERRYGARD_S001 | H21 | Scheme | 2022-09-12 12:04 | FRA_3618120920221152.pdf | fowlerb1 | 3618120920221150 | Extra Care | Extra Care Central | EC Central 1 | South | South Patch 2 | 7f1nen54afl7ynbzo5 | Observation Only | Risk Closed | 44832.449 | Obs11 | Fire Fighting Equipment | NULL | N/A | Surveyor | FFE for information only | Information only
3618 | Strawberry Gardens | STRAWBERRYGARD_S001 | H21 | Scheme | 2022-09-12 12:04 | FRA_3618120920221152.pdf | fowlerb1 | 3618120920221150 | Extra Care | Extra Care Central | EC Central 1 | South | South Patch 2 | cl2a83simf5l7ynbzn0 | Observation Only | Risk Closed | 44832.4492 | Obs10 | Fire Safety And Notices | NULL | N/A | Surveyor | Fire action notices for information only | Information only
3618 | Strawberry Gardens | STRAWBERRYGARD_S001 | H21 | Scheme | 2022-09-12 12:04 | FRA_3618120920221152.pdf | fowlerb1 | 3618120920221150 | Extra Care | Extra Care Central | EC Central 1 | South | South Patch 2 | 9g4229umzkel7ynbzlh | Observation Only | Risk Closed | 44832.4493 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel for information only | Information only
3701 | Brigadier Hargreaves Court | BRIGHARG_S001 | H21 | Scheme | 2022-07-01 13:52 | FRA_3701010720221310.pdf | BrigdenN | 3701010720221310 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 6 | 0cjjnmxev23ul52ffok9 | Observation Only | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | NULL | N/A | Other | High Risk Flats - Flat 4 - Oxygen. Flats 9,25,29 need assistance. | NULL
3701 | Brigadier Hargreaves Court | BRIGHARG_S001 | H21 | Scheme | 2022-07-01 13:52 | FRA_3701010720221310.pdf | BrigdenN | 3701010720221310 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 6 | p65b9xeoyil52fzg2t | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45108 | Medium | Court Manager | Communal Fire escape door requires chairs clearing from the patio area so that a safe route out of the building can be maintained. | NULL
3701 | Brigadier Hargreaves Court | BRIGHARG_S001 | H21 | Scheme | 2022-07-01 13:52 | FRA_3701010720221310.pdf | BrigdenN | 3701010720221310 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 6 | p4lh8q6pr5ml52g2zk3 | Medium Risk to be actioned | Risk Open | NULL | Obs14 | Access By Emergency Services | 45108 | Medium | Court Manager | Assembly point sign in car park missing. | NULL
3701 | Brigadier Hargreaves Court | BRIGHARG_S001 | H21 | Scheme | 2022-07-01 13:52 | FRA_3701010720221310.pdf | BrigdenN | 3701010720221310 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 6 | yynkqeouxql52fosin | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45108 | Medium | Court Manager | Walking frame is causing an obstruction on the fire escape route. Please ask tenant to remove. | NULL
3702 | Rokeby Gardens | ROKEBYGARD_S001 | H21 | Scheme | 2022-11-03 18:06 | FRA_3702031120221511.pdf | BrigdenN | 3702031120221510 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | wed6teugj8la17u4hi | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Other | Flat No's 10,11,12,15,17, 23, 24, 28,36, 46 &48 are all classed as high risk tenants. | NULL
3702 | Rokeby Gardens | ROKEBYGARD_S001 | H21 | Scheme | 2022-11-03 18:06 | FRA_3702031120221511.pdf | BrigdenN | 3702031120221510 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | i2u7quvhx5la17zo7a | High Risk Closed | Risk Closed | 44872.3856 | Obs6 | Fire Hazards - Elimination & Control | 44595 | High | Court Manager | Mobility scooter needs to be removed from fire escape route outside flat 16 | Discussed with resident, scooter now being kept in scooter room.
3702 | Rokeby Gardens | ROKEBYGARD_S001 | H21 | Scheme | 2022-11-03 18:06 | FRA_3702031120221511.pdf | BrigdenN | 3702031120221510 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | jypbmzs6yolla181b2y | High Risk Closed | Risk Closed | 44872.3866 | Obs6 | Fire Hazards - Elimination & Control | 44595 | High | Court Manager | Combustible items need to be removed from the fire escape routes. | Tables removed from under shelfs from flat 36, 37
3702 | Rokeby Gardens | ROKEBYGARD_S001 | H21 | Scheme | 2022-11-03 18:06 | FRA_3702031120221511.pdf | BrigdenN | 3702031120221510 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | 4yttyjmtwojla1dg0dj | Low Risk closed | Risk Closed | 44872.523 | Obs5 | Evacuation Strategy And Training | 45599 | Low | Court Manager | Just one member of staff needs to complete e learning module. | staff member completed e learning.
3702 | Rokeby Gardens | ROKEBYGARD_S001 | H21 | Scheme | 2022-11-03 18:06 | FRA_3702031120221511.pdf | BrigdenN | 3702031120221510 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | blphcyrw9jhla1ct71b | High Risk Closed | Risk Closed | 44872.386 | Obs7 | Fire Protection Measures | 44960 | High | Court Manager | Mobility scooter is still being stored on the fire escape route outside flat 16 | Discussed with resident scooter now being stored in scooter room.
3704 | Blenheim Court 1 | BLENHEIM1_S001 | H21 | Scheme | 2022-05-23 12:25 | FRA_3704230520221215.pdf | BrigdenN | 3704230520221210 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 6 | 170vouyockcl3imu28w | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Other | Flat No s 1,2,4,12, 17, 37, 41, 42, 45, 47, 48, 50 are all high risk as identified on PEEP | NULL
3709 | Blenheim Court 2 | BLENHEIM2_S001 | H21 | Scheme | 2022-05-23 12:31 | FRA_3709230520221224.pdf | BrigdenN | 3709230520221220 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 6 | oqnlnttangnl3in6wsc | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Other | Flats 19 & 65 are classed as high risk. | NULL
3710 | Chindit Court | CHINDIT1_S001 | H21 | Scheme | 2022-07-01 14:16 | FRA_3710010720221353.pdf | BrigdenN | 3710010720221350 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 6 | mhhd0flzjzl52gzqpm | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45108 | Medium | Court Manager | Please can walker be removed from the fire escape route. | NULL
3710 | Chindit Court | CHINDIT1_S001 | H21 | Scheme | 2022-07-01 14:16 | FRA_3710010720221353.pdf | BrigdenN | 3710010720221350 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 6 | 7fbv79zyqlwl52h8akc | Observation Only | Risk Open | NULL | Obs15 | Management Of Fire Safety | NULL | N/A | Other | Covering court manager could not advise of false alarms. | NULL
3710 | Chindit Court | CHINDIT1_S001 | H21 | Scheme | 2022-07-01 14:16 | FRA_3710010720221353.pdf | BrigdenN | 3710010720221350 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 6 | bmxk3u6c3hll52gvm8v | Medium Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45108 | Medium | Court Manager | Tenants information in red fire box needs updating. Last dated Feb 2022. | NULL
3710 | Chindit Court | CHINDIT1_S001 | H21 | Scheme | 2022-07-01 14:16 | FRA_3710010720221353.pdf | BrigdenN | 3710010720221350 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 6 | 8lvopljuj6l52h0zhn | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45108 | Medium | Court Manager | Please can rubber be removed from the frame of the fire exit door next to the court managers office as it is comprising the fire safety. | NULL
3710 | Chindit Court | CHINDIT1_S001 | H21 | Scheme | 2022-07-01 14:16 | FRA_3710010720221353.pdf | BrigdenN | 3710010720221350 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 6 | yldyxqgcj8l52gujr2 | Observation Only | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | NULL | N/A | Other | Please note temporary court manager at time of inspection. | NULL
3710 | Chindit Court | CHINDIT1_S001 | H21 | Scheme | 2022-07-01 14:16 | FRA_3710010720221353.pdf | BrigdenN | 3710010720221350 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 6 | ywxzqd2p1h8l52gso5o | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Other | Flats 4, 22,19, 24,25,27 are classed as high risk. | NULL
3711 | Minden Court 1 | MINDEN1_S001 | H21 | Scheme | 2022-08-04 16:07 | FRA_3711040820221532.pdf | BrigdenN | 3711040820221530 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 6 | 6whtzi50ao7l6f5jxgr | Medium Risk closed | Risk Closed | 44781.4626 | Obs6 | Fire Hazards - Elimination & Control | 44785 | Medium | Court Manager | Combustible it's need clearing from electrical cupboard. | Removed 8th August 2022
3711 | Minden Court 1 | MINDEN1_S001 | H21 | Scheme | 2022-08-04 16:07 | FRA_3711040820221532.pdf | BrigdenN | 3711040820221530 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 6 | 02b8hadffllbl6f5geoz | Medium Risk closed | Risk Closed | 44781.4599 | Obs5 | Evacuation Strategy And Training | 44785 | Medium | Court Manager | Court manager needs to update her fire safety training. | Completed 5th August 2022
3711 | Minden Court 1 | MINDEN1_S001 | H21 | Scheme | 2022-08-04 16:07 | FRA_3711040820221532.pdf | BrigdenN | 3711040820221530 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 6 | gs5hsrfijqtl6f5pons | Low Risk closed | Risk Closed | 44781.4604 | Obs6 | Fire Hazards - Elimination & Control | 45150 | Low | Court Manager | Plant stand needs to be moved from fire escape route. | Moved 8th August 2022
3711 | Minden Court 1 | MINDEN1_S001 | H21 | Scheme | 2022-08-04 16:07 | FRA_3711040820221532.pdf | BrigdenN | 3711040820221530 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 6 | fsw1ofz1ifvl6f5dtp1 | Medium Risk closed | Risk Closed | 44873.6401 | Obs4 | The Occupant - Information Provided By The Court Manager | 45142 | Medium | Court Manager | Person centred fire risk assessments need to be completed in New format. | PCFRA completed
3711 | Minden Court 1 | MINDEN1_S001 | H21 | Scheme | 2022-08-04 16:07 | FRA_3711040820221532.pdf | BrigdenN | 3711040820221530 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 6 | ga51ejf8uzl6f5c0vk | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Other | Flat No 29 high risk | NULL
3711 | Minden Court 1 | MINDEN1_S001 | H21 | Scheme | 2022-08-04 16:07 | FRA_3711040820221532.pdf | BrigdenN | 3711040820221530 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 6 | nkpq3pk7dfol6f5n8w9 | Medium Risk closed | Risk Closed | 44785.5762 | Obs6 | Fire Hazards - Elimination & Control | 45142 | Medium | Court Manager | Chairs need to be cleared from fire escape route. | Chairs put inside salon
3711 | Minden Court 1 | MINDEN1_S001 | H21 | Scheme | 2022-08-04 16:07 | FRA_3711040820221532.pdf | BrigdenN | 3711040820221530 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 6 | sicv4nsxjgl6f63lrv | Medium Risk closed | Risk Closed | 44781.4614 | Obs16 | Testing And Maintenance | 45142 | Medium | Court Manager | Door near flat no 69 needs adjusting as it does not close properly | Repair raised 5th August 2022 1554337
3713 | Minden Court 2 | MINDEN2_S001 | H21 | Scheme | 2022-08-04 16:37 | FRA_3713040820221607.pdf | BrigdenN | 3713040820221600 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 6 | tb53ou362uil6f6kro9 | Medium Risk closed | Risk Closed | 44783.6784 | Obs5 | Evacuation Strategy And Training | 44785 | Medium | Court Manager | Fire Safety Managers course needs updating. | Course completed on 3rd August 2022
3713 | Minden Court 2 | MINDEN2_S001 | H21 | Scheme | 2022-08-04 16:37 | FRA_3713040820221607.pdf | BrigdenN | 3713040820221600 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 6 | gnnxy5pw12l6f6luo3 | Medium Risk closed | Risk Closed | 44798.3477 | Obs5 | Evacuation Strategy And Training | 45142 | Medium | Court Manager | High Risk tenants information needs to be added to Red fire box at Minden 1 | Information updated and added to red fire box at Minden 1
3713 | Minden Court 2 | MINDEN2_S001 | H21 | Scheme | 2022-08-04 16:37 | FRA_3713040820221607.pdf | BrigdenN | 3713040820221600 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 6 | dx49os7zzvl6f6hrdd | Low Risk closed | Risk Closed | 44872.3968 | Obs4 | The Occupant - Information Provided By The Court Manager | 45508 | Low | Court Manager | Person centred fire risk assessments need to be updated to new form. | All completed 6 Full Assessments done
3713 | Minden Court 2 | MINDEN2_S001 | H21 | Scheme | 2022-08-04 16:37 | FRA_3713040820221607.pdf | BrigdenN | 3713040820221600 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 6 | y34t2kjxpidl6f6gsg5 | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Other | Flat No 2 is high risk as has piped oxygen. | NULL
3715 | Staveley Court | STAVELEY_S001 | H21 | Scheme | 2022-09-28 08:08 | FRA_3715270920221226.pdf | PriestleyC | 3715270920221220 | Extra Care | Extra Care North | EC North 5 | North | North Patch 2 | tac78fs4zrl8k48s6n | Medium Risk closed | Risk Closed | 44897.4088 | Obs8 | Measures To Limit Fire Spread And Development | 45196 | Medium | Court Manager | Door wedged open flat 25 | Door closer now fixed
3715 | Staveley Court | STAVELEY_S001 | H21 | Scheme | 2022-09-28 08:08 | FRA_3715270920221226.pdf | PriestleyC | 3715270920221220 | Extra Care | Extra Care North | EC North 5 | North | North Patch 2 | t5gdi9ejgkl8k4m0gm | Low Risk closed | Risk Closed | 44897.4095 | Obs10 | Fire Safety And Notices | 45562 | Low | Court Manager | Missing fire action notice at MCP in lounge | Notice now in place
3716 | Charles Court | CHARLES_S001 | H21 | Scheme | 2022-08-05 17:05 | FRA_3716050820221529.pdf | BrigdenN | 3716050820221520 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | sn0xkhifj3jl6gkc572 | Medium Risk closed | Risk Closed | 44832.6227 | Obs6 | Fire Hazards - Elimination & Control | 45143 | Medium | Court Manager | Oil vats are to be removed from fire escape route near kitchen. | Removed vats
3716 | Charles Court | CHARLES_S001 | H21 | Scheme | 2022-08-05 17:05 | FRA_3716050820221529.pdf | BrigdenN | 3716050820221520 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | mbdjhakyzfkl6gkc5ap | Medium Risk closed | Risk Closed | 44832.6195 | Obs7 | Fire Protection Measures | 45143 | Medium | Court Manager | Can all combustible items be cleared from near flat entrance doors | Removed all items from outside if flats
3716 | Charles Court | CHARLES_S001 | H21 | Scheme | 2022-08-05 17:05 | FRA_3716050820221529.pdf | BrigdenN | 3716050820221520 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | lqwvqltqfkal6gkc59z | Medium Risk closed | Risk Closed | 44832.6245 | Obs7 | Fire Protection Measures | 45143 | Medium | Court Manager | Please can outside furniture be moved away from fire escape route from communal lounge. | Removed items
3716 | Charles Court | CHARLES_S001 | H21 | Scheme | 2022-08-05 17:05 | FRA_3716050820221529.pdf | BrigdenN | 3716050820221520 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | k600mrauqvl6gkc563 | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Other | Flat No s 5,6,1, 24, 29, 33, 39 are high risk. | NULL
3716 | Charles Court | CHARLES_S001 | H21 | Scheme | 2022-08-05 17:05 | FRA_3716050820221529.pdf | BrigdenN | 3716050820221520 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | 92rwfv0y924l6gkc581 | Medium Risk closed | Risk Closed | 44832.6215 | Obs6 | Fire Hazards - Elimination & Control | 45143 | Medium | Court Manager | Combustible items need to be cleared out of GF electrical cupboard. | Removed items
3716 | Charles Court | CHARLES_S001 | H21 | Scheme | 2022-08-05 17:05 | FRA_3716050820221529.pdf | BrigdenN | 3716050820221520 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | bb98334dhs6l6gkc58y | Medium Risk closed | Risk Closed | 44832.6208 | Obs7 | Fire Protection Measures | 44784 | Medium | Court Manager | Fire doors in kitchen area are being wedged open | Ensure doors are nit wedged open
3717 | Swallowdale | SWALLOWDALE_S001 | H21 | Scheme | 2022-07-25 11:53 | FRA_3717250720221109.pdf | BrigdenN | 3717250720221100 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | 8oy1mcmboyfl60mevpw | Medium Risk to be actioned | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | 45132 | Medium | Court Manager | New style forms need to filled in for tenants risk assessments | NULL
3717 | Swallowdale | SWALLOWDALE_S001 | H21 | Scheme | 2022-07-25 11:53 | FRA_3717250720221109.pdf | BrigdenN | 3717250720221100 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | cmarhv3xvsjl60mgqgc | Low Risk closed | Risk Closed | 44875.6028 | Obs6 | Fire Hazards - Elimination & Control | 45498 | Low | Court Manager | Record of cleaning of filters to laundry needs to be put in place. | Paperwork set up and being completed by staff
3717 | Swallowdale | SWALLOWDALE_S001 | H21 | Scheme | 2022-07-25 11:53 | FRA_3717250720221109.pdf | BrigdenN | 3717250720221100 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | 0u6xuh5w4j6ql60lbgy0 | Medium Risk closed | Risk Closed | 44875.6026 | Obs6 | Fire Hazards - Elimination & Control | 45132 | Medium | Court Manager | Refuse bins need moving away from the external fire escape route. | Moved away from Fire Escape
3717 | Swallowdale | SWALLOWDALE_S001 | H21 | Scheme | 2022-07-25 11:53 | FRA_3717250720221109.pdf | BrigdenN | 3717250720221100 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | 1ny2xoyajjbl60l7igd | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Other | Flat Now's 47, 51 and 62 are classed as high risk. | NULL
3717 | Swallowdale | SWALLOWDALE_S001 | H21 | Scheme | 2022-07-25 11:53 | FRA_3717250720221109.pdf | BrigdenN | 3717250720221100 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | 30ed8y50tttl60l9tmq | Medium Risk closed | Risk Closed | 44875.6024 | Obs6 | Fire Hazards - Elimination & Control | 45132 | Medium | Court Manager | Replacement fire extinguisher is required in kitchen area. | Ordered and delivered
3717 | Swallowdale | SWALLOWDALE_S001 | H21 | Scheme | 2022-07-25 11:53 | FRA_3717250720221109.pdf | BrigdenN | 3717250720221100 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | k0tshvrwybl60l7ii3 | Medium Risk closed | Risk Closed | 44875.6021 | Obs5 | Evacuation Strategy And Training | 45132 | Medium | Court Manager | 6 members of staff need to complete the fire safety e learning training. | Completed on FRED
3717 | Swallowdale | SWALLOWDALE_S001 | H21 | Scheme | 2022-07-25 11:53 | FRA_3717250720221109.pdf | BrigdenN | 3717250720221100 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | lqs5s4pwjol60lkrp6 | Medium Risk Overdue | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44656 | Medium | Development | Additional works identified to spandrel panels in roof space. | NULL
3717 | Swallowdale | SWALLOWDALE_S001 | H21 | Scheme | 2022-07-25 11:53 | FRA_3717250720221109.pdf | BrigdenN | 3717250720221100 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | m7gf5932auil60mbvv9 | Medium Risk to be actioned | Risk Open | NULL | Obs16 | Testing And Maintenance | 45132 | Medium | M&E Team | Outstanding repair required on automatic smoke vent system. | NULL
3717 | Swallowdale | SWALLOWDALE_S001 | H21 | Scheme | 2022-07-25 11:53 | FRA_3717250720221109.pdf | BrigdenN | 3717250720221100 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | fm6ppgeyrlhl60l7ifd | High Risk Overdue | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | 44859 | High | M&E Team | There are faults showing with the fire alarm system and repairs need to be carried out. | NULL
3717 | Swallowdale | SWALLOWDALE_S001 | H21 | Scheme | 2022-07-25 11:53 | FRA_3717250720221109.pdf | BrigdenN | 3717250720221100 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | y733frvgo0pl60lsik2 | Medium Risk to be actioned | Risk Open | NULL | Obs12 | Automatic Fire Systems i.e. Suppression System | 45132 | Medium | Court Manager | There are some outstanding repairs required to the smoke Vents. | NULL
3717 | Swallowdale | SWALLOWDALE_S001 | H21 | Scheme | 2022-07-25 11:53 | FRA_3717250720221109.pdf | BrigdenN | 3717250720221100 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | xfpp0o5syldl60l7ihd | Medium Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45132 | Medium | Court Manager | Court Manager is required to complete the fire safety managers course. | NULL
3718 | Casson Court | CASSON_S001 | H21 | Scheme | 2022-04-20 10:58 | FRA_3718190420221144.pdf | BrigdenN | 3718190420221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | ycmgxymnfjfl260ql82 | Medium Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45035 | Medium | Court Manager | Most have completed but there has been a few new starters. | NULL
3718 | Casson Court | CASSON_S001 | H21 | Scheme | 2022-04-20 10:58 | FRA_3718190420221144.pdf | BrigdenN | 3718190420221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | v1pzuj57nkl261uu0v | Observation Only | Risk Open | NULL | Obs13 | Other Relevant Fixed Systems | NULL | N/A | Other | Contractors attended site also on 13/04/22 to repair leak to sprinkler system. | NULL
3718 | Casson Court | CASSON_S001 | H21 | Scheme | 2022-04-20 10:58 | FRA_3718190420221144.pdf | BrigdenN | 3718190420221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | fyuswnudjpl261bigt | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45035 | Medium | Court Manager | Fire escape route is being blocked by bench. This must be moved. | NULL
3718 | Casson Court | CASSON_S001 | H21 | Scheme | 2022-04-20 10:58 | FRA_3718190420221144.pdf | BrigdenN | 3718190420221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | hkaf9ojmajcl261phpc | Observation Only | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Other | Unable to inspect individual flat doors due to a COVID outbreak on the court at the time of the FRA. | NULL
3718 | Casson Court | CASSON_S001 | H21 | Scheme | 2022-04-20 10:58 | FRA_3718190420221144.pdf | BrigdenN | 3718190420221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | lrg2s2hkwrl26113ru | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45035 | Medium | Court Manager | Not all of the scooter chargers have been PAT tested. | NULL
3718 | Casson Court | CASSON_S001 | H21 | Scheme | 2022-04-20 10:58 | FRA_3718190420221144.pdf | BrigdenN | 3718190420221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | tm6sj90zm7sl27e89pn | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Other | Flat No 6 & 47 are high risk due to oxygen. | NULL
3718 | Casson Court | CASSON_S001 | H21 | Scheme | 2022-04-20 10:58 | FRA_3718190420221144.pdf | BrigdenN | 3718190420221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | u4i8k9xul8al261fxep | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45035 | Medium | Court Manager | Fire door to laundry not closing due to digi lock locked in the closed position. Please ensure the door is fully closed to ensure compartmentation is not comprised. | NULL
3718 | Casson Court | CASSON_S001 | H21 | Scheme | 2022-04-20 10:58 | FRA_3718190420221144.pdf | BrigdenN | 3718190420221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | qj1jx204nyl2612pc2 | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45035 | Medium | Court Manager | Communal Fire Doors in corridor areas outside flats 40, 38, 31, 60, 68 require adjusting as the gaps between leafs are non compliant. | NULL
3718 | Casson Court | CASSON_S001 | H21 | Scheme | 2022-04-20 10:58 | FRA_3718190420221144.pdf | BrigdenN | 3718190420221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | 2mkb7bctro4l27e9mdy | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Other | 27 No High Risk, 13 No Medium Risk and 24 No Low Risk identified on PEEPS. | NULL
3718 | Casson Court | CASSON_S001 | H21 | Scheme | 2022-04-20 10:58 | FRA_3718190420221144.pdf | BrigdenN | 3718190420221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | d4t16wkaufgl2615edw | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45035 | Medium | Court Manager | Room within plant room with electrical equipment in it, requires all combustible materials clearing from it. | NULL
3718 | Casson Court | CASSON_S001 | H21 | Scheme | 2022-04-20 10:58 | FRA_3718190420221144.pdf | BrigdenN | 3718190420221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | 8efujec7x9ql260ua8r | Observation Only | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | NULL | N/A | Other | Graham Green attended the FRA and carried out inspection and provided a report on the stay put policy to confirm the building supports this, as long as the sprinkler system is fully operational. | NULL
3718 | Casson Court | CASSON_S001 | H21 | Scheme | 2022-04-20 10:58 | FRA_3718190420221144.pdf | BrigdenN | 3718190420221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 6 | b7jcmky30jpl27edaei | Medium Risk to be actioned | Risk Open | NULL | Obs16 | Testing And Maintenance | 45036 | Medium | Court Manager | No evidence of the lightning protection system being serviced. Raised this with the compliance team and court manager. | NULL
3801 | Oliver Leese Court | OLIVERLEES_S001 | H21 | Scheme | 2022-11-03 09:09 | FRA_3801021120221208.pdf | CrosdaleS | 3801021120221200 | Retirement Housing | Mid West | Staffordshire | Central | Central Patch 5 | 90djynaqg6hl9zmmtwp | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45598 | Low | Court Manager | Recommend to supply and fit a few hard wire double sockets on the wall to minimise socket overload | NULL
3801 | Oliver Leese Court | OLIVERLEES_S001 | H21 | Scheme | 2022-11-03 09:09 | FRA_3801021120221208.pdf | CrosdaleS | 3801021120221200 | Retirement Housing | Mid West | Staffordshire | Central | Central Patch 5 | s9x2kln3i1l9zli118 | Observation Only | Risk Open | NULL | Obs7 | Fire Protection Measures | NULL | N/A | Other | Escape routes are all external. There is only one escape route on the first floor walkway due tovthe original construction design | NULL
3802 | Lord Cromwell Court | LORDCROM_S001 | H21 | Scheme | 2022-02-09 09:21 | FRA_3802080220220907.pdf | CrosdaleS | 3802080220220900 | Retirement Housing | Mid West | Staffordshire | Central | Central Patch 5 | 98botbx9q2nkze44j1b | Medium Risk closed | Risk Closed | 44603.4251 | Obs6 | Fire Hazards - Elimination & Control | 44965 | Medium | Court Manager | Refuse bins to Flats14-26; 52-56 & 60-72 located in close proximuty to the building. There are 2 small external bin areas. The majority of the bins can fit. There are 3 residents with severe mobility issues who are unable to walk to the bin area. | Resident's bins that can safely be put in the bin areas will be as soon as possible.
3802 | Lord Cromwell Court | LORDCROM_S001 | H21 | Scheme | 2022-02-09 09:21 | FRA_3802080220220907.pdf | CrosdaleS | 3802080220220900 | Retirement Housing | Mid West | Staffordshire | Central | Central Patch 5 | dmcn51fn1x9kze4neer | Observation Only | Risk Closed | 44603.4258 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Dryer filters are the residents responsibility to clean after use. Filters are also cleaned 3x per week by the cleaner | Completed
3803 | Curtis Court | CURTIS_S001 | H21 | Scheme | 2022-01-25 16:23 | FRA_3803250120221250.pdf | CrosdaleS | 3803250120221250 | Retirement Housing | Mid West | Staffordshire | Central | Central Patch 5 | taex29mdjinkyu49jbk | Low Risk closed | Risk Closed | 44594.462 | Obs7 | Fire Protection Measures | 45316 | Low | Court Manager | Table and plant on the escape route by Flat 30 | Plant has been removed
3803 | Curtis Court | CURTIS_S001 | H21 | Scheme | 2022-01-25 16:23 | FRA_3803250120221250.pdf | CrosdaleS | 3803250120221250 | Retirement Housing | Mid West | Staffordshire | Central | Central Patch 5 | pvc35ry10ukyu49jc7 | Low Risk closed | Risk Closed | 44594.4623 | Obs7 | Fire Protection Measures | 45316 | Low | Court Manager | Door mats in all blocks | Asked the residents to remove all mats etc
3804 | Pearce Court | PEARCE_S001 | H21 | Scheme | 2022-01-26 16:25 | FRA_3804260120221204.pdf | CrosdaleS | 3804260120221200 | Retirement Housing | Mid West | Staffordshire | Central | Central Patch 5 | 9x7gvdi4yfhkyvi73c7 | Low Risk closed | Risk Closed | 44628.6071 | Obs7 | Fire Protection Measures | 45317 | Low | Court Manager | The placing of door mats needs to be removed from the communal areas | Put request in newsletter. Had to give a couple of residents formal letters to remove their mats. All mats now removed
3806 | William Birch Court | WILLIAMBIRC_S001 | H21 | Scheme | 2022-01-14 08:33 | FRA_3806130120220923.pdf | CrosdaleS | 3806130120220920 | Retirement Housing | Mid West | Cheshire and Lancashire | Central | Central Patch 5 | zyi7ahc9igqkycz67e7 | Observation Only | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Other | Resident's are responsible for clearing the tumble driers after use | NULL
3807 | George Hill Court | GEORGEHILL_S001 | H21 | Scheme | 2022-01-20 09:51 | FRA_3807190120221302.pdf | CrosdaleS | 3807190120221300 | Retirement Housing | Mid West | Staffordshire | Central | Central Patch 5 | wse9gd51bcikyll0s7g | Low Risk closed | Risk Closed | 44589.6094 | Obs10 | Fire Safety And Notices | 45310 | Low | Court Manager | Fire Exit Door in Lounge to have sign affix externally 'Fire Exit Keep Clear. | COMPLETED by handyperson 28/01/2022
3807 | George Hill Court | GEORGEHILL_S001 | H21 | Scheme | 2022-01-20 09:51 | FRA_3807190120221302.pdf | CrosdaleS | 3807190120221300 | Retirement Housing | Mid West | Staffordshire | Central | Central Patch 5 | bs7whm6k7rikylkigy6 | Low Risk closed | Risk Closed | 44587.4368 | Obs6 | Fire Hazards - Elimination & Control | 45310 | Low | Court Manager | Court Manager to confirm if reasonable measures are taken to prevent fire as a result of cooking taking place in the communal kitchen | No residents cook in the communal kitchen.
3807 | George Hill Court | GEORGEHILL_S001 | H21 | Scheme | 2022-01-20 09:51 | FRA_3807190120221302.pdf | CrosdaleS | 3807190120221300 | Retirement Housing | Mid West | Staffordshire | Central | Central Patch 5 | ptywgv3te3kylkdbvz | Low Risk closed | Risk Closed | 44589.6127 | Obs5 | Evacuation Strategy And Training | 45310 | Low | Court Manager | Court Manager to confirm Training is up to date | Yes. All e-learning up to date. Fire Safety Manager 24/03/2021
3807 | George Hill Court | GEORGEHILL_S001 | H21 | Scheme | 2022-01-20 09:51 | FRA_3807190120221302.pdf | CrosdaleS | 3807190120221300 | Retirement Housing | Mid West | Staffordshire | Central | Central Patch 5 | loyuqb5sx5kylklcot | Low Risk closed | Risk Closed | 44587.4383 | Obs6 | Fire Hazards - Elimination & Control | 45310 | Low | Court Manager | Court Manager to confirm resident's on Oxygen and have scooters | No oxygen on court. Flat 1 has a scooter which is in scooter store outside block 5 Flat 5 has a scooter in scooter store outside block 1
3807 | George Hill Court | GEORGEHILL_S001 | H21 | Scheme | 2022-01-20 09:51 | FRA_3807190120221302.pdf | CrosdaleS | 3807190120221300 | Retirement Housing | Mid West | Staffordshire | Central | Central Patch 5 | hck4wb9d3wkyll53ih | Low Risk closed | Risk Closed | 44587.4406 | Obs14 | Access By Emergency Services | 45310 | Low | Court Manager | The court and its surroundings is small/compact. | No action as to size of court can't be changed.
3809 | Lea Court | LEA_S001 | H21 | Scheme | 2022-06-15 17:11 | FRA_3809150620221358.pdf | CrosdaleS | 3809150620221350 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 5 | gz99pkjoh2pl4fln6fx | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45092 | Medium | Court Manager | Scooter outside flat | NULL
3809 | Lea Court | LEA_S001 | H21 | Scheme | 2022-06-15 17:11 | FRA_3809150620221358.pdf | CrosdaleS | 3809150620221350 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 5 | m44a9jxoerpl4fln6fa | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45458 | Low | Court Manager | Items outside flat door | NULL
3809 | Lea Court | LEA_S001 | H21 | Scheme | 2022-06-15 17:11 | FRA_3809150620221358.pdf | CrosdaleS | 3809150620221350 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 5 | c4o8cf9z2xil4fln6ek | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45458 | Low | Court Manager | Items directly outside Flat door | NULL
3809 | Lea Court | LEA_S001 | H21 | Scheme | 2022-06-15 17:11 | FRA_3809150620221358.pdf | CrosdaleS | 3809150620221350 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 5 | ewcucr1mdjl4fln6dr | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45458 | Low | Court Manager | Trolley parked on the escape route | NULL
3812 | Smalley Court | SMALLEY_S001 | H21 | Scheme | 2022-10-04 16:16 | FRA_3812041020221320.pdf | CrosdaleS | 3812041020221320 | Retirement Housing | Mid West | Staffordshire | Central | Central Patch 5 | 45n2xdjklnbl8u6hleg | Observation Only | Risk Open | NULL | Obs14 | Access By Emergency Services | NULL | N/A | Court Manager | Assembly point on the grass verge outside the communal lounge | NULL
3812 | Smalley Court | SMALLEY_S001 | H21 | Scheme | 2022-10-04 16:16 | FRA_3812041020221320.pdf | CrosdaleS | 3812041020221320 | Retirement Housing | Mid West | Staffordshire | Central | Central Patch 5 | tel30u3smhol8u65ep1 | Observation Only | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Responsibilities are with the residents on each use as well as cleaned out weekly by domestic and a resident | NULL
3812 | Smalley Court | SMALLEY_S001 | H21 | Scheme | 2022-10-04 16:16 | FRA_3812041020221320.pdf | CrosdaleS | 3812041020221320 | Retirement Housing | Mid West | Staffordshire | Central | Central Patch 5 | wsgrq79mr2l8u65eqb | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45203 | Medium | Court Manager | Fire seals are missing | NULL
3812 | Smalley Court | SMALLEY_S001 | H21 | Scheme | 2022-10-04 16:16 | FRA_3812041020221320.pdf | CrosdaleS | 3812041020221320 | Retirement Housing | Mid West | Staffordshire | Central | Central Patch 5 | xf953407jel8u65eru | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45203 | Medium | Court Manager | Electric meter cupboard door opposite Flat 36 has no fire strips | NULL
3812 | Smalley Court | SMALLEY_S001 | H21 | Scheme | 2022-10-04 16:16 | FRA_3812041020221320.pdf | CrosdaleS | 3812041020221320 | Retirement Housing | Mid West | Staffordshire | Central | Central Patch 5 | wz11hxfg8hl8u65er7 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45569 | Low | Court Manager | Cross corridor doors adjust door closers adj to Flat 18, Flat 15, Flat 34 | NULL
3818 | Summerfield Court | SUMMERFIELD_B001 | H21 | Unknown | 2022-01-27 15:13 | FRA_3818270120221512.pdf | CrosdaleS | 3818270120221510 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 5 | yyihz7hpbkqkyx48fjd | Low Risk closed | Risk Closed | 44909.3652 | Obs7 | Fire Protection Measures | 45318 | Low | Court Manager | Front door mats needs to be removed | informed residents to remove mats outside front doors
3818 | Summerfield Court | SUMMERFIELD_B001 | H21 | Unknown | 2022-01-27 15:13 | FRA_3818270120221512.pdf | CrosdaleS | 3818270120221510 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 5 | tk9f856pi6kyx48flc | Medium Risk closed | Risk Closed | 44627.479 | Obs10 | Fire Safety And Notices | 44588 | Medium | Court Manager | 'Fire Action Notice needs to be displayed by each break glass device | Fire action notice displayed. Action completed
3818 | Summerfield Court | SUMMERFIELD_B001 | H21 | Unknown | 2022-01-27 15:13 | FRA_3818270120221512.pdf | CrosdaleS | 3818270120221510 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 5 | n8dok39c4xskyx48fjz | Low Risk closed | Risk Closed | 44627.4802 | Obs7 | Fire Protection Measures | 45318 | Low | Court Manager | Clutter on the escape route | Clutter removed
3818 | Summerfield Court | ALTONAHOUS_B001 | H21 | Unknown | 2022-10-20 13:02 | FRA_3818201020221245.pdf | CrosdaleS | 3818201020221240 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 5 | g2q4xe4j8gnl9gzyeja | Observation Only | Risk Closed | 44860.4346 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Surveyor | The emergency call system unit is placed near to the bin area. The unit is in a fire metal surround, the area is solid brick leading into open space and has fire detection. | The bin area is brick built with smoke detection and leads out into external space. Considered as a low risk area
3818 | Summerfield Court | ALTONAHOUS_B001 | H21 | Unknown | 2022-10-20 13:02 | FRA_3818201020221245.pdf | CrosdaleS | 3818201020221240 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 5 | 7bbn0kurrhl9gzyekk | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45254 | Low | Court Manager | There are no Fire Action Notices in the block, which should be placed by or close to the red break glasses. At least 3 notices are required. | NULL
3818 | Summerfield Court | SUMMERFIELD_B001 | H21 | Unknown | 2022-01-27 15:13 | FRA_3818270120221512.pdf | CrosdaleS | 3818270120221510 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 5 | 7mdend2og46kyx48fm6 | Medium Risk closed | Risk Closed | 44627.4806 | Obs10 | Fire Safety And Notices | 44588 | Medium | Court Manager | Each final fire exits should display on the external glass side 'Fire Exit Keep Clear' signs | Signs displayed
3818 | Summerfield Court | SUMMERFIELD_B001 | H21 | Unknown | 2022-01-27 15:13 | FRA_3818270120221512.pdf | CrosdaleS | 3818270120221510 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 5 | 0umswdnfseickyx48fkm | Medium Risk closed | Risk Closed | 44627.4794 | Obs7 | Fire Protection Measures | 44588 | Medium | Court Manager | Scooter parked on the escape route. Needs to be within the flats or scooter store | Scooter stored in flat
3818 | Summerfield Court | SUMMERFIELD_B001 | H21 | Unknown | 2022-01-27 15:13 | FRA_3818270120221512.pdf | CrosdaleS | 3818270120221510 | Extra Care | Extra Care Central | EC Central 3 | Central | Central Patch 5 | c39bpoqunqakyx48fij | Observation Only | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | M&E Team | For Information: 2nd fire alarm panel outside the care office should be set as a repeater as original set up. | NULL
3880 | Lisbon Place | LISBONPLAC_S001 | H21 | Scheme | 2022-02-03 09:03 | FRA_3880030220220902.pdf | CrosdaleS | 3880030220220900 | Retirement Housing | Mid West | Staffordshire | Central | Central Patch 5 | xp4130enu2nkz6r2o65 | Observation Only | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Other | 16 Flats with Shared Entrances to the 1st floor do not have detection as recommended. Area consists mainly a staircase and compartmentation is of brick structure. | NULL
3881 | Copperfields | COPPERFIELDS_S001 | H21 | Scheme | 2022-02-09 16:13 | FRA_3881090220221039.pdf | CrosdaleS | 3881090220221030 | Retirement Housing | Mid West | Staffordshire | Central | Central Patch 5 | t56aye8uwjakzflo104 | Observation Only | Risk Closed | 44601.7832 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Allcresidents are responsible for cleaning the filters after use. The Court Manager also checks | Signage on all tumble dryers to remind every user to clean the filters after every use. Reminder also published in newsletter
3901 | Stradbroke Court | STRADBROKE_B001 | H21 | Unknown | 2020-05-19 15:11 | FRA_390119052020.pdf | hallr | 390119052020 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 3 | fk6mj1h3998zkadyt6kj | Observation Only | Risk Closed | 44426.7583 | Obs1 | The Building | NULL | N/A | Surveyor | The fire compartmentation within the pitched roof areas is not to a good standard, although this risk has been mitigated by the location and zoning of additional detection. | No action required at this time.
3901 | Stradbroke Court | STRADBROKE_S001 | H21 | Scheme | 2022-05-19 09:02 | FRA_3901190520220859.pdf | colej | 3901190520220850 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 3 | ky99utbwcqbl3cq302l | Observation Only | Risk Closed | 44754.6024 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Court Manager | Both systems are automatically connected to the warden call system and local fire service. | No action required.
3901 | Stradbroke Court | STRADBROKE_B001 | H21 | Unknown | 2020-05-19 15:11 | FRA_390119052020.pdf | hallr | 390119052020 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 3 | ks794ldilehzkadz6xzg | Low Risk closed | Risk Closed | 44335.6598 | Obs5 | Evacuation Strategy And Training | 44700 | Low | Court Manager | Agreed with CM that this needs some updating as earlier comment. | All training complete.
3901 | Stradbroke Court | STRADBROKE_B001 | H21 | Unknown | 2020-05-19 15:11 | FRA_390119052020.pdf | hallr | 390119052020 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 3 | 8xd5dc4efj5gkadzmzgh | Observation Only | Risk Closed | 44335.6595 | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | Third part carers are employed directly by the residents and are informed of the necessary fire actions via the Fire Action Notices as any visitor. | Fire instruction notice given to residents.
3901 | Stradbroke Court | STRADBROKE_B001 | H21 | Unknown | 2020-05-19 15:11 | FRA_390119052020.pdf | hallr | 390119052020 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 3 | b79509roz7s0kadz2h97 | Low Risk closed | Risk Closed | 44335.66 | Obs4 | The Occupant - Information Provided By The Court Manager | 44700 | Low | Court Manager | Due to the on going Corona virus pandemic some of the occupant information has not been updated in the fire folder. It was agreed with the CM that this will be attended to ASAP. | All information updated.
3901 | Stradbroke Court | STRADBROKE_S001 | H21 | Scheme | 2022-05-19 09:02 | FRA_3901190520220859.pdf | colej | 3901190520220850 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 3 | 32jhllhwd2il3cq3018 | Low Risk closed | Risk Closed | 44747.594 | Obs1 | The Building | 45065 | Low | Surveyor | This is an observational note and a record of information previously identified. The loft compartmentation is very limited with some fire curtains that are in poor condition. This has been mitigated by the installation of detection in the loft and a zoned evacuation policy. | This is for noting purposes only. No further action required due to the roof space detection added.
3901 | Stradbroke Court | STRADBROKE_S001 | H21 | Scheme | 2022-05-19 09:02 | FRA_3901190520220859.pdf | colej | 3901190520220850 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 3 | 4ytdc5w6ba5l3cq303b | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45431 | Low | Court Manager | The displayed fire action notices require the assembly point information to be added. | NULL
3901 | Stradbroke Court | STRADBROKE_B001 | H21 | Unknown | 2020-05-19 15:11 | FRA_390119052020.pdf | hallr | 390119052020 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 3 | wgdjppcvhjd0kadziym6 | Low Risk closed | Risk Closed | 44335.6591 | Obs10 | Fire Safety And Notices | 44700 | Low | Court Manager | No Fire Action Notice on inside of guest room door. NB - Guest room not in use during Coronavirus restrictions | Fire instruction poster put on inside of the door.
3902 | Vinnicombe Court | VINNICOMBE_S001 | H21 | Scheme | 2022-02-17 14:54 | FRA_3902170220221404.pdf | HallR | 3902170220221400 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | 7sle6glq9cmkzr2udw8 | Observation Only | Risk Open | NULL | Obs14 | Access By Emergency Services | NULL | N/A | Other | Fire fighter access to rear of building is not ideal. | NULL
3902 | Vinnicombe Court | VINNICOMBE_S001 | H21 | Scheme | 2022-02-17 14:54 | FRA_3902170220221404.pdf | HallR | 3902170220221400 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | 1cvnu7j1hx3kzr2qn17 | Observation Only | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Other | No automatic ventilation but windows can be opened. | NULL
3902 | Vinnicombe Court | VINNICOMBE_S001 | H21 | Scheme | 2022-02-17 14:54 | FRA_3902170220221404.pdf | HallR | 3902170220221400 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | b4y0v6c6twckzr2smy6 | Observation Only | Risk Open | NULL | Obs11 | Fire Fighting Equipment | NULL | N/A | Other | Fire fighting equipment adequate for building and occupants. | NULL
3902 | Vinnicombe Court | VINNICOMBE_S001 | H21 | Scheme | 2022-02-17 14:54 | FRA_3902170220221404.pdf | HallR | 3902170220221400 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | a14ytlnx4t5kzr3owlx | Low Risk closed | Risk Closed | 44617.486 | Obs8 | Measures To Limit Fire Spread And Development | 45339 | Low | Court Manager | Door closers need adjustment to flats 33 & 27. | Got them adjusted.
3902 | Vinnicombe Court | VINNICOMBE_S001 | H21 | Scheme | 2022-02-17 14:54 | FRA_3902170220221404.pdf | HallR | 3902170220221400 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | a5gj2k80cj5kzr2ihus | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45339 | Low | Other | Management of hot works by contractors is limited especially the repair contractors. | NULL
3902 | Vinnicombe Court | VINNICOMBE_S001 | H21 | Scheme | 2022-02-17 14:54 | FRA_3902170220221404.pdf | HallR | 3902170220221400 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | a33n0k1bt2kzr3du19 | Observation Only | Risk Open | NULL | Obs1 | The Building | NULL | N/A | Other | No access available to loft space via communal areas but zoned evacuation policy is not relying on integrity of compartmentation in roof space. | NULL
3903 | Mays Court | MAYS_S001 | H21 | Scheme | 2022-07-19 18:29 | FRA_3903190720221552.pdf | CooneyE | 3903190720221550 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | b60hh34po8jl5sg0bvv | Low Risk closed | Risk Closed | 44777.6972 | Obs8 | Measures To Limit Fire Spread And Development | 45492 | Low | Court Manager | Adjust F49 door closer to shut less quickly | Bluestar adjusted all done
3903 | Mays Court | MAYS_S001 | H21 | Scheme | 2022-07-19 18:29 | FRA_3903190720221552.pdf | CooneyE | 3903190720221550 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | 0crqn6m5d7zrl5sfoj2v | Low Risk closed | Risk Closed | 44846.6586 | Obs11 | Fire Fighting Equipment | 45492 | Low | Court Manager | Change Co2 fire extinguisher beside lift to P50 type | duplicate
3903 | Mays Court | MAYS_S001 | H21 | Scheme | 2022-07-19 18:29 | FRA_3903190720221552.pdf | CooneyE | 3903190720221550 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | 3e0hotgvid9l5sfm5pj | Medium Risk closed | Risk Closed | 44777.6978 | Obs8 | Measures To Limit Fire Spread And Development | 45126 | Medium | Court Manager | Communal kitchen door doesn't fully close | Door Closer needed moving all done
3903 | Mays Court | MAYS_S001 | H21 | Scheme | 2022-07-19 18:29 | FRA_3903190720221552.pdf | CooneyE | 3903190720221550 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | 3p68qqxbsmol5sflggg | Low Risk closed | Risk Closed | 44796.5295 | Obs8 | Measures To Limit Fire Spread And Development | 45492 | Low | Court Manager | S/f door closer to laundry door | Door closer has been fitted
3903 | Mays Court | MAYS_S001 | H21 | Scheme | 2022-07-19 18:29 | FRA_3903190720221552.pdf | CooneyE | 3903190720221550 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | 6t9pj9cz84l5sfjhq8 | Medium Risk closed | Risk Closed | 44796.5293 | Obs9 | Escape Lighting | 45126 | Medium | Court Manager | Emergency light on 3rd floor staircase 44-51 not working | Quote received and works to be carried with other emergency lights not working
3903 | Mays Court | MAYS_S001 | H21 | Scheme | 2022-07-19 18:29 | FRA_3903190720221552.pdf | CooneyE | 3903190720221550 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | mqhsj53g6el5sfnhav | Low Risk closed | Risk Closed | 44846.654 | Obs11 | Fire Fighting Equipment | 45492 | Low | Court Manager | Laundry room fire extinguisher to be hung on wall bracket | Duplicate
3903 | Mays Court | MAYS_S001 | H21 | Scheme | 2022-07-19 18:29 | FRA_3903190720221552.pdf | CooneyE | 3903190720221550 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | gaak2xipc5ll5sfy93m | Low Risk closed | Risk Closed | 44810.5169 | Obs8 | Measures To Limit Fire Spread And Development | 45492 | Low | Court Manager | S/f external bar type intumescent strip to F28 front entrance door. | Bluestar has fitted this
3903 | Mays Court | MAYS_S001 | H21 | Scheme | 2022-07-19 18:29 | FRA_3903190720221552.pdf | CooneyE | 3903190720221550 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | hog932daif9l5say2wx | Observation Only | Risk Closed | 44846.6539 | Obs1 | The Building | NULL | N/A | Surveyor | Unable to carry out loft inspection | N/A
3903 | Mays Court | MAYS_S001 | H21 | Scheme | 2022-07-19 18:29 | FRA_3903190720221552.pdf | CooneyE | 3903190720221550 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | hog932daif9l5say2wx | Observation Only | Risk Closed | 44846.6541 | Obs1 | The Building | NULL | N/A | Surveyor | Unable to carry out loft inspection | N/A
3903 | Mays Court | MAYS_S001 | H21 | Scheme | 2022-07-19 18:29 | FRA_3903190720221552.pdf | CooneyE | 3903190720221550 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | tq8v2lz2fl5sfsd6l | Observation Only | Risk Closed | 44778.7474 | Obs15 | Management Of Fire Safety | NULL | N/A | Other | Testing records digitally recorded via 'Pebbles' in house system. | n/a observation only
3903 | Mays Court | MAYS_S001 | H21 | Scheme | 2022-07-19 18:29 | FRA_3903190720221552.pdf | CooneyE | 3903190720221550 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | r4ve155k68l5sb2ic6 | Medium Risk closed | Risk Closed | 44846.6584 | Obs2 | Means Of Giving Warning In Case Of Fire | 44783 | Medium | Court Manager | Linked smoke detector required to new office area | duplicate
3903 | Mays Court | MAYS_S001 | H21 | Scheme | 2022-07-19 18:29 | FRA_3903190720221552.pdf | CooneyE | 3903190720221550 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | pppbjetos6l5sfdjvu | Low Risk closed | Risk Closed | 44796.4601 | Obs7 | Fire Protection Measures | 45492 | Low | Court Manager | 2no fridges by fire assembly point to be removed | These have been removed
3903 | Mays Court | MAYS_S001 | H21 | Scheme | 2022-07-19 18:29 | FRA_3903190720221552.pdf | CooneyE | 3903190720221550 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | q0qr3f1d8l5sb91iv | Low Risk closed | Risk Closed | 44796.458 | Obs7 | Fire Protection Measures | 45148 | Low | Court Manager | Materials stored on exit routes to be removed | Materials have been removed
3903 | Mays Court | MAYS_S001 | H21 | Scheme | 2022-07-19 18:29 | FRA_3903190720221552.pdf | CooneyE | 3903190720221550 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | yuxwcv5ywoml5sfx1ft | Medium Risk closed | Risk Closed | 44777.6969 | Obs8 | Measures To Limit Fire Spread And Development | 45126 | Medium | Court Manager | Adjust F36 Front entrance door to fully close | Bluestar adjusted all done
3904 | Hildesley Court | HILDESLEY_S001 | H21 | Scheme | 2022-02-02 14:09 | FRA_3904020220221108.pdf | HallR | 3904020220221100 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | yb2ice3u64hkz5l8s3e | Low Risk closed | Risk Closed | 44824.4397 | Obs11 | Fire Fighting Equipment | 45324 | Low | Court Manager | Fire fighting equipment adequate for building and occupants, although there is not a fire blanket in the kitchen. | new fire blanket in kitchen
3904 | Hildesley Court | HILDESLEY_S001 | H21 | Scheme | 2022-02-02 14:09 | FRA_3904020220221108.pdf | HallR | 3904020220221100 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | gvsi6yh3w6fkz5l6o0o | Low Risk closed | Risk Closed | 44678.6092 | Obs10 | Fire Safety And Notices | 45324 | Low | Court Manager | Fire zone chart needs fixing to wall. | Fire zone chart now on wall
3904 | Hildesley Court | HILDESLEY_S001 | H21 | Scheme | 2022-02-02 14:09 | FRA_3904020220221108.pdf | HallR | 3904020220221100 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | 6f10r65r70dkz5l03io | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45324 | Low | Other | Control of hot works by contractors is limited especially the repair contractors. | NULL
3904 | Hildesley Court | HILDESLEY_S001 | H21 | Scheme | 2022-02-02 14:09 | FRA_3904020220221108.pdf | HallR | 3904020220221100 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | 933ffjul1obkz5hca2c | Observation Only | Risk Closed | 44678.609 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | Three high risk residents due to poor mobility. Court Manager has assessed and reviews their risk and method of escape. | Regular assessment as conditions change
3904 | Hildesley Court | HILDESLEY_S001 | H21 | Scheme | 2022-02-02 14:09 | FRA_3904020220221108.pdf | HallR | 3904020220221100 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | chk8n85jakwkz5hny1p | Observation Only | Risk Open | NULL | Obs14 | Access By Emergency Services | NULL | N/A | Other | As zoned evacuation policy and independant living a fire assembly point is of limited value. | NULL
3905 | Charles Miller Court | CHARLESMILL_S001 | H21 | Scheme | 2022-02-15 17:08 | FRA_3905150220221524.pdf | HallR | 3905150220221520 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | czcx3c0iq0vkzodfmc9 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45337 | Low | Other | There are extractor fans / ducts into the escape corridors by flats 1 & 18. However as these sections of the corridors are separated via fire doors, the risk of compromising the escape route of other flats is very low. These may already have suitable fire dampers in place. | NULL
3905 | Charles Miller Court | CHARLESMILL_S001 | H21 | Scheme | 2022-02-15 17:08 | FRA_3905150220221524.pdf | HallR | 3905150220221520 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | hua19na7nojkzoamqqf | Observation Only | Risk Open | NULL | Obs14 | Access By Emergency Services | NULL | N/A | Other | With zoned evacuation policy the fire assembly point is of limited value. | NULL
3905 | Charles Miller Court | CHARLESMILL_S001 | H21 | Scheme | 2022-02-15 17:08 | FRA_3905150220221524.pdf | HallR | 3905150220221520 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | syp1tgoynxbkzod8scg | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45337 | Low | Other | Management of hot works by contractors is limited especially the repair contractors. | NULL
3907 | Wilding Court | WILDING_S001 | H21 | Scheme | 2022-10-05 17:28 | FRA_3907051020221022.pdf | macpheem | 3907051020221020 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | ahreg4aha48l8vf8wz4 | Low Risk to be actioned | Risk Open | NULL | Obs3 | Details Of Fire Loss | 45570 | Low | Surveyor | A number of call outs due to way apello system does not communicate with fire alarm system. Fire alarm system requires upgrade. MM yo confirm when fire alarm upgrade is planned. | NULL
3908 | Thompson Court | THOMPSON_S001 | H21 | Scheme | 2022-10-13 16:20 | FRA_3908131020221555.pdf | macpheem | 3908131020221550 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | kzcre9ko7qml976vu7q | Low Risk to be actioned | Risk Open | NULL | Obs3 | Details Of Fire Loss | 45578 | Low | Court Manager | Approximately 10 Nr false alarm calls due to faulty detectors. This should be resolved as part of upgrade planned to be done shortly. | NULL
3908 | Thompson Court | THOMPSON_S001 | H21 | Scheme | 2022-10-13 16:20 | FRA_3908131020221555.pdf | macpheem | 3908131020221550 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | jdongyjc1jjl97729bq | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45578 | Low | Court Manager | Excess material stored in understairs cupboards adjacent to escape routes. | NULL
3908 | Thompson Court | THOMPSON_S001 | H21 | Scheme | 2022-10-13 16:20 | FRA_3908131020221555.pdf | macpheem | 3908131020221550 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 2 | zpv9j99a8vel977fh79 | Low Risk closed | Risk Closed | 44865.6625 | Obs15 | Management Of Fire Safety | 45578 | Low | Court Manager | Only partial record of false alarms due to out of hours calls. | Report any false alarms which I am aware of
3909 | Rukba (Felixstowe) | RUKBA_B13C | H21 | Unknown | 2022-05-24 13:33 | FRA_3909240520221304.pdf | CooneyE | 3909240520221300 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | yuexl12svqfl3k4hzui | Low Risk closed | Risk Closed | 44846.6559 | Obs6 | Fire Hazards - Elimination & Control | 45436 | Low | Court Manager | Basement fire doors x 2 held open with fire extinguishers, which should be fixed to wall. | Duplicate
3909 | Rukba (Felixstowe) | RUKBA_B45G | H21 | Unknown | 2022-05-26 08:04 | FRA_3909260520220742.pdf | CooneyE | 3909260520220740 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | zgsrbgr3ssl3mnu9jl | Observation Only | Risk Closed | 44778.7491 | Obs14 | Access By Emergency Services | NULL | N/A | Other | Street property with no designated fire fighting vehicle space | n/a observation only
3909 | Rukba (Felixstowe) | RUKBA_B13C | H21 | Unknown | 2022-05-24 13:33 | FRA_3909240520221304.pdf | CooneyE | 3909240520221300 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | mwhs4cn0dxbl3k4jvub | Low Risk closed | Risk Closed | 44796.4596 | Obs6 | Fire Hazards - Elimination & Control | 45436 | Low | Court Manager | Debris on staircase including xmas tree & roofrack bars to be removed | These have been removed
3909 | Rukba (Felixstowe) | RUKBA_B39H | H21 | Unknown | 2022-05-26 08:21 | FRA_3909260520220805.pdf | CooneyE | 3909260520220800 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | hsnxah43u6vl3mol37u | Observation Only | Risk Closed | 44778.7492 | Obs14 | Access By Emergency Services | NULL | N/A | Other | Street property with no designated fire fighting vehicle space | n/a observation only
3909 | Rukba (Felixstowe) | RUKBA_B26H | H21 | Unknown | 2022-05-26 08:51 | FRA_3909260520220834.pdf | CooneyE | 3909260520220830 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | tsrwybmh27ol3mps98l | Low Risk closed | Risk Closed | 44846.6577 | Obs9 | Escape Lighting | 45438 | Low | Court Manager | Emergency light and smoke detector to communal area to be tested in line with H21 policy | duplicate
3909 | Rukba (Felixstowe) | RUKBA_B26H | H21 | Unknown | 2022-05-26 08:51 | FRA_3909260520220834.pdf | CooneyE | 3909260520220830 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | tsrwybmh27ol3mps98l | Low Risk closed | Risk Closed | 44851.5656 | Obs9 | Escape Lighting | 45438 | Low | Court Manager | Emergency light and smoke detector to communal area to be tested in line with H21 policy | Tested weekly
3909 | Rukba (Felixstowe) | RUKBA_B45G | H21 | Unknown | 2022-05-26 08:04 | FRA_3909260520220742.pdf | CooneyE | 3909260520220740 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | ty9ayqga41l3mo2d84 | Low Risk closed | Risk Closed | 44846.6568 | Obs15 | Management Of Fire Safety | 45438 | Low | Court Manager | Linked detectors between flats to be tested regularly | duplicate
3909 | Rukba (Felixstowe) | RUKBA_B45G | H21 | Unknown | 2022-05-26 08:04 | FRA_3909260520220742.pdf | CooneyE | 3909260520220740 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | ty9ayqga41l3mo2d84 | Low Risk closed | Risk Closed | 44854.6519 | Obs15 | Management Of Fire Safety | 45438 | Low | Court Manager | Linked detectors between flats to be tested regularly | Tenants Been informed by letter to test alarms within own flat the forst week of every month. Any one unbale to will contact CM to carry out the test. CM to undertake own test every 6 months.
3909 | Rukba (Felixstowe) | RUKBA_B13C | H21 | Unknown | 2022-05-24 13:33 | FRA_3909240520221304.pdf | CooneyE | 3909240520221300 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | r2wtl506pghl3k4xmv4 | Observation Only | Risk Closed | 44778.749 | Obs15 | Management Of Fire Safety | NULL | N/A | Other | Testing recorded digitally with in house system ( Pebbles). | n/a observation only
3909 | Rukba (Felixstowe) | RUKBA_B13C | H21 | Unknown | 2022-05-24 13:33 | FRA_3909240520221304.pdf | CooneyE | 3909240520221300 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | rdhyjzlgw7l3k4vxl0 | Observation Only | Risk Closed | 44778.749 | Obs14 | Access By Emergency Services | NULL | N/A | Other | Street property with no designated fire fighting vehicle space | n/a observation only
3909 | Rukba (Felixstowe) | RUKBA_B28H | H21 | Unknown | 2022-05-26 09:07 | FRA_3909260520220853.pdf | CooneyE | 3909260520220850 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | ac3wnltr1ghl3mqaz3k | Low Risk closed | Risk Closed | 44875.5451 | Obs15 | Management Of Fire Safety | 45438 | Low | Court Manager | Emergency light and linked smoke detectors to be tested in line with H21 policy | EMERGANCY LIGHTS TESTED MONTHLY BY CM. weekly fire tests by CM 6th monthly fire tests by openview letter been given to all tenants advising them to test own smoke alarms monthly.
3909 | Rukba (Felixstowe) | RUKBA_B28H | H21 | Unknown | 2022-05-26 09:07 | FRA_3909260520220853.pdf | CooneyE | 3909260520220850 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | ac3wnltr1ghl3mqaz3k | Low Risk closed | Risk Closed | 44846.6579 | Obs15 | Management Of Fire Safety | 45438 | Low | Court Manager | Emergency light and linked smoke detectors to be tested in line with H21 policy | duplicate
3909 | Rukba (Felixstowe) | RUKBA_B11Y | H21 | Unknown | 2022-05-24 13:02 | FRA_3909240520221242.pdf | CooneyE | 3909240520221240 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | aj4alxptf9sl3k3t0ny | Observation Only | Risk Closed | 44778.7488 | Obs16 | Testing And Maintenance | NULL | N/A | Other | Testing records inputted to in house digital system (Pebbles) | n/a observation only
3909 | Rukba (Felixstowe) | RUKBA_B03H | H21 | Unknown | 2022-05-24 12:42 | FRA_3909240520221208.pdf | CooneyE | 3909240520221200 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | as11gm2sc9pl3k3018y | Observation Only | Risk Closed | 44778.7487 | Obs15 | Management Of Fire Safety | NULL | N/A | Other | Emergency lighting testing recorded via in house digital system ( Pebbles). | n/a observation only
3909 | Rukba (Felixstowe) | RUKBA_B03H | H21 | Unknown | 2022-05-24 12:42 | FRA_3909240520221208.pdf | CooneyE | 3909240520221200 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | bkp6chrgvmkl3k2o5li | Medium Risk closed | Risk Closed | 44846.6514 | Obs6 | Fire Hazards - Elimination & Control | 45070 | Medium | Court Manager | Emergency light fitting to be checked, as unable to confirm working order at time of visit | duplicate
3909 | Rukba (Felixstowe) | RUKBA_B03H | H21 | Unknown | 2022-05-24 12:42 | FRA_3909240520221208.pdf | CooneyE | 3909240520221200 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | bkp6chrgvmkl3k2o5li | Medium Risk closed | Risk Closed | 44846.6518 | Obs6 | Fire Hazards - Elimination & Control | 45070 | Medium | Court Manager | Emergency light fitting to be checked, as unable to confirm working order at time of visit | duplicate
3909 | Rukba (Felixstowe) | RUKBA_B13C | H21 | Unknown | 2022-05-24 13:33 | FRA_3909240520221304.pdf | CooneyE | 3909240520221300 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | 99nu7lrqarl3k4m04y | Low Risk closed | Risk Closed | 44846.6533 | Obs6 | Fire Hazards - Elimination & Control | 45436 | Low | Court Manager | Ignition source material stored within basement area to be removed | duplicate
3909 | Rukba (Felixstowe) | RUKBA_B13C | H21 | Unknown | 2022-05-24 13:33 | FRA_3909240520221304.pdf | CooneyE | 3909240520221300 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | 99nu7lrqarl3k4m04y | Low Risk closed | Risk Closed | 44851.5637 | Obs6 | Fire Hazards - Elimination & Control | 45436 | Low | Court Manager | Ignition source material stored within basement area to be removed | all items removed and disposed of on Friday 14th October 2022
3909 | Rukba (Felixstowe) | RUKBA_B13C | H21 | Unknown | 2022-05-24 13:33 | FRA_3909240520221304.pdf | CooneyE | 3909240520221300 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | 9jc0wqskmksl3k4emwt | Low Risk closed | Risk Closed | 44846.6556 | Obs6 | Fire Hazards - Elimination & Control | 45436 | Low | Court Manager | Old water type fire extinguisher within basement to be removed and replaced with P50 type, secured to wall. | duplicate
3909 | Rukba (Felixstowe) | RUKBA_B26H | H21 | Unknown | 2022-05-26 08:51 | FRA_3909260520220834.pdf | CooneyE | 3909260520220830 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | bt03snnbp75l3mpld7c | Observation Only | Risk Closed | 44778.7493 | Obs14 | Access By Emergency Services | NULL | N/A | Other | Street property with no designated space for fire fighting vehicle | n/a observation only
3909 | Rukba (Felixstowe) | RUKBA_B39H | H21 | Unknown | 2022-05-26 08:21 | FRA_3909260520220805.pdf | CooneyE | 3909260520220800 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | elfazblkt1l3moongv | Low Risk closed | Risk Closed | 44854.6513 | Obs16 | Testing And Maintenance | 45438 | Low | Court Manager | Emergency light and linked detectors to be tested regularly and in line with H21 policy | tenants informed to check fire alarms first week of every month,or contact CM to carry out test. CM to carry out own test every 6 months.
3909 | Rukba (Felixstowe) | RUKBA_B39H | H21 | Unknown | 2022-05-26 08:21 | FRA_3909260520220805.pdf | CooneyE | 3909260520220800 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | elfazblkt1l3moongv | Low Risk closed | Risk Closed | 44846.6574 | Obs16 | Testing And Maintenance | 45438 | Low | Court Manager | Emergency light and linked detectors to be tested regularly and in line with H21 policy | duplicate
3909 | Rukba (Felixstowe) | RUKBA_B26H | H21 | Unknown | 2022-05-26 08:51 | FRA_3909260520220834.pdf | CooneyE | 3909260520220830 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | eg3vdr4sw68l3mpqmdn | Observation Only | Risk Closed | 44778.7493 | Obs13 | Other Relevant Fixed Systems | NULL | N/A | Other | Rear fire exit. Metal staircase from ground - 1st floor. | n/a observation only
3909 | Rukba (Felixstowe) | RUKBA_B03H | H21 | Unknown | 2022-05-24 12:42 | FRA_3909240520221208.pdf | CooneyE | 3909240520221200 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | 7tghb0b5hp4l3k2wm2k | Observation Only | Risk Closed | 44778.7487 | Obs14 | Access By Emergency Services | NULL | N/A | Other | Street property with no designated fire fighting parking | n/a observation only
3909 | Rukba (Felixstowe) | RUKBA_B28H | H21 | Unknown | 2022-05-26 09:07 | FRA_3909260520220853.pdf | CooneyE | 3909260520220850 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | 49kivvv2xxl3mq93ds | Observation Only | Risk Closed | 44778.7494 | Obs14 | Access By Emergency Services | NULL | N/A | Other | Street property with no designated fire fighting vehicle space | n/a observation only
3909 | Rukba (Felixstowe) | RUKBA_B11Y | H21 | Unknown | 2022-05-24 13:02 | FRA_3909240520221242.pdf | CooneyE | 3909240520221240 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | 01ghw1k4ktspl3k3prze | Observation Only | Risk Closed | 44778.7489 | Obs14 | Access By Emergency Services | NULL | N/A | Other | Street property with no designated fire fighting vehicle space | n/a observation only
3909 | Rukba (Felixstowe) | RUKBA_B03H | H21 | Unknown | 2022-05-24 12:42 | FRA_3909240520221208.pdf | CooneyE | 3909240520221200 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | 0sllyfpgdjul3k2rdo1 | Low Risk closed | Risk Closed | 44846.6521 | Obs7 | Fire Protection Measures | 45436 | Low | Court Manager | MED has yale lock and knob latch, leading to 2 handed opening in the event of a fire. Latch to be disabled | duplicate
3909 | Rukba (Felixstowe) | RUKBA_B03H | H21 | Unknown | 2022-05-24 12:42 | FRA_3909240520221208.pdf | CooneyE | 3909240520221200 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | 0sllyfpgdjul3k2rdo1 | Low Risk closed | Risk Closed | 44882.6639 | Obs7 | Fire Protection Measures | 45436 | Low | Court Manager | MED has yale lock and knob latch, leading to 2 handed opening in the event of a fire. Latch to be disabled | now removed by handyman
3909 | Rukba (Felixstowe) | RUKBA_B45G | H21 | Unknown | 2022-05-26 08:04 | FRA_3909260520220742.pdf | CooneyE | 3909260520220740 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | 1p7qn036wwul3mnyt0o | Low Risk closed | Risk Closed | 44887.6074 | Obs13 | Other Relevant Fixed Systems | 45438 | Low | Court Manager | MED has yale and knob latch preventing one handed door opening. Knob latch to be removed. | latch removed by handyman
3909 | Rukba (Felixstowe) | RUKBA_B45G | H21 | Unknown | 2022-05-26 08:04 | FRA_3909260520220742.pdf | CooneyE | 3909260520220740 | Retirement Housing | East Anglia | Suffolk | Central | Central Patch 7 | 1p7qn036wwul3mnyt0o | Low Risk closed | Risk Closed | 44882.6643 | Obs13 | Other Relevant Fixed Systems | 45438 | Low | Court Manager | MED has yale and knob latch preventing one handed door opening. Knob latch to be removed. | now removed by handyman
3910 | Mere View Court | MEREVIEW_S001 | H21 | Scheme | 2022-02-11 09:50 | FRA_3910110220220934.pdf | HallR | 3910110220220930 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 2 | 6vrvy9du6zhkzi7r783 | Observation Only | Risk Open | NULL | Obs11 | Fire Fighting Equipment | NULL | N/A | Other | Fire fighting equipment adequate for building and occupants. | NULL
3910 | Mere View Court | MEREVIEW_S001 | H21 | Scheme | 2022-02-11 09:50 | FRA_3910110220220934.pdf | HallR | 3910110220220930 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 2 | qq9zpfwgjokzi7r76x | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45333 | Low | Other | Control of hot works by contractors is limited especially the repair contractors. | NULL
3910 | Mere View Court | MEREVIEW_S001 | H21 | Scheme | 2022-02-11 09:50 | FRA_3910110220220934.pdf | HallR | 3910110220220930 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 2 | ot3gwagkqokzi899wg | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45333 | Low | Surveyor | Some enhancement of the fire stopping above the first floor flat entrance doors is being arranged to ensure the the long term viability of the escape routes. As agreed with Cambridge F&R Service. | NULL
3917 | Shearman Court | SHEARMAN_S001 | H21 | Scheme | 2022-06-06 17:01 | FRA_3917060620220751.pdf | colej | 3917060620220750 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 3 | pcqnu7du0gl42wr8md | High Risk Closed | Risk Closed | 44819.4349 | Obs8 | Measures To Limit Fire Spread And Development | 44810 | High | Court Manager | Flat 18. Door closer missing. Requires replacing. | Door closure fitted
3917 | Shearman Court | SHEARMAN_S001 | H21 | Scheme | 2022-06-06 17:01 | FRA_3917060620220751.pdf | colej | 3917060620220750 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 3 | 7ovzvkgt29pl42ldp9j | Observation Only | Risk Closed | 44778.7495 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Other | No hot works permits are issued to contractors. All contractors are to work within their provided RAMS and inline with H21 accepted practices. | n/a observation only
3917 | Shearman Court | SHEARMAN_S001 | H21 | Scheme | 2022-06-06 17:01 | FRA_3917060620220751.pdf | colej | 3917060620220750 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 3 | 3a9afudaa7nl42wvf5k | Medium Risk closed | Risk Closed | 44907.4789 | Obs8 | Measures To Limit Fire Spread And Development | 45083 | Medium | Court Manager | Flat 13. The free swing closer requires adjustment on the last 15 degree closing action. | door closure adjusted
3917 | Shearman Court | SHEARMAN_S001 | H21 | Scheme | 2022-06-06 17:01 | FRA_3917060620220751.pdf | colej | 3917060620220750 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 3 | x02tioi5lshl42wsi7p | Medium Risk closed | Risk Closed | 44907.4785 | Obs8 | Measures To Limit Fire Spread And Development | 45083 | Medium | Court Manager | Flat16. Free swing closer requires adjustment on the final 15 degree closing action. | new door closure fitted
3917 | Shearman Court | SHEARMAN_S001 | H21 | Scheme | 2022-06-06 17:01 | FRA_3917060620220751.pdf | colej | 3917060620220750 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 3 | ups3c62098ol42mhvb0 | Observation Only | Risk Closed | 44778.7496 | Obs15 | Management Of Fire Safety | NULL | N/A | Other | Comment only. All false alarms have been either cooking or test triggers. No areas of concern raised as a result of false alarms. | n/a observation only
3917 | Shearman Court | SHEARMAN_S001 | H21 | Scheme | 2022-06-06 17:01 | FRA_3917060620220751.pdf | colej | 3917060620220750 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 3 | v3go8if9roel42wuajz | High Risk Closed | Risk Closed | 44819.4351 | Obs8 | Measures To Limit Fire Spread And Development | 44810 | High | Court Manager | Flat 12. Door closer missing and requires replacing. | Door closure fitted
3925 | Holm Court | HOLM_S001 | H21 | Scheme | 2022-02-16 16:48 | FRA_3925160220221624.pdf | HallR | 3925160220221620 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 2 | wq9tmeqi73lkzprlv35 | Medium Risk to be actioned | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | 44973 | Medium | Court Manager | There is no detection in the first floor office, which has inner welfare rooms leading from it. | NULL
3925 | Holm Court | HOLM_S001 | H21 | Scheme | 2022-02-16 16:48 | FRA_3925160220221624.pdf | HallR | 3925160220221620 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 2 | wqk715yh1vdkzprlv7k | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45338 | Low | Court Manager | Fire door to commercial kitchen is held open with door wedge. Although not directly onto the escape routes consideration should be given to a hold open device connected to the the fire detection system. Or the door kept shut. | NULL
3925 | Holm Court | HOLM_S001 | H21 | Scheme | 2022-02-16 16:48 | FRA_3925160220221624.pdf | HallR | 3925160220221620 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 2 | 3660tmgnnxykzprlv6e | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45338 | Low | Other | Management of hot work controls on contractors is limited especially the repair contractors. | NULL
3925 | Holm Court | HOLM_S001 | H21 | Scheme | 2022-02-16 16:48 | FRA_3925160220221624.pdf | HallR | 3925160220221620 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 2 | nne4vb1d50kkzprlv6v | Observation Only | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | The large commercial wheelie bins are not enclosed or locked and are adjacent to the public footpath. Although without any history of arson or antisocial behaviour the risk is minimal. | NULL
3925 | Holm Court | HOLM_S001 | H21 | Scheme | 2022-02-16 16:48 | FRA_3925160220221624.pdf | HallR | 3925160220221620 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 2 | swwuzcdgbuokzprlv5w | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45338 | Low | Court Manager | Unecessary storage of wooden pallets by external fence. | NULL
3925 | Holm Court | HOLM_S001 | H21 | Scheme | 2022-02-16 16:48 | FRA_3925160220221624.pdf | HallR | 3925160220221620 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 2 | gura4481uinkzps4i0k | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45338 | Low | Court Manager | Doors / closers need adjusting to flats 13, 24 & 26 | NULL
3925 | Holm Court | HOLM_S001 | H21 | Scheme | 2022-02-16 16:48 | FRA_3925160220221624.pdf | HallR | 3925160220221620 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 2 | gkwgoxy4c8ckzprlv8a | Observation Only | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Other | There are suitable Windows that can be opened. | NULL
3925 | Holm Court | HOLM_S001 | H21 | Scheme | 2022-02-16 16:48 | FRA_3925160220221624.pdf | HallR | 3925160220221620 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 2 | mdp29ctjwigkzprlv93 | Observation Only | Risk Open | NULL | Obs10 | Fire Safety And Notices | NULL | N/A | Other | Signage adequate for building and occupants. | NULL
3925 | Holm Court | HOLM_S001 | H21 | Scheme | 2022-02-16 16:48 | FRA_3925160220221624.pdf | HallR | 3925160220221620 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 2 | m6ax9hp6skzprnlvt | Observation Only | Risk Open | NULL | Obs1 | The Building | NULL | N/A | Other | Compartmentation in lofts is horizontal with additional fire curtains above cross corridor fire doors. Additinal fire stopped to the ceiling forming the horizontal fire break was being improved at time of F R A. | NULL
3925 | Holm Court | HOLM_S001 | H21 | Scheme | 2022-02-16 16:48 | FRA_3925160220221624.pdf | HallR | 3925160220221620 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 2 | lb6o23vy3ckzprlv9z | Observation Only | Risk Open | NULL | Obs14 | Access By Emergency Services | NULL | N/A | Other | Due to the stay put policy and the occupants an external fire assembly point is of limited value. | NULL
3925 | Holm Court | HOLM_S001 | H21 | Scheme | 2022-02-16 16:48 | FRA_3925160220221624.pdf | HallR | 3925160220221620 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 2 | joh70j3nyppkzprlv4x | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | There are three high risk residents, who would need assistance to leave their flat / building. | NULL
3926 | Oakhouse Court,Oakhouse Day Centre | OAKHOUS_S001 | H21 | Scheme | 2022-04-20 18:29 | FRA_3926200420221120.pdf | CooneyE | 3926200420221120 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 7 | uh3hqcy734ml27uj3xv | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45402 | Low | Court Manager | Buggy within store has no PAT test to battery visual | NULL
3926 | Oakhouse Court,Oakhouse Day Centre | OAKHOUS_S001 | H21 | Scheme | 2022-04-20 18:29 | FRA_3926200420221120.pdf | CooneyE | 3926200420221120 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 7 | o82futkyrol27tyg0q | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45402 | Low | Court Manager | Builders' debris to be removed from plant room | NULL
3926 | Oakhouse Court,Oakhouse Day Centre | OAKHOUS_S001 | H21 | Scheme | 2022-04-20 18:29 | FRA_3926200420221120.pdf | CooneyE | 3926200420221120 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 7 | 2tzp77l5nxql27udm9b | Medium Risk to be actioned | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | 45036 | Medium | Court Manager | New Fire Alarm recently installed, and zone plan requires small adjustment | NULL
3926 | Oakhouse Court,Oakhouse Day Centre | OAKHOUS_S001 | H21 | Scheme | 2022-04-20 18:29 | FRA_3926200420221120.pdf | CooneyE | 3926200420221120 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 7 | 4la5ebjihjjl27uac0a | Observation Only | Risk Open | NULL | Obs16 | Testing And Maintenance | NULL | N/A | Other | Testing recorded digitally and backed up in file | NULL
3927 | Blackbourne View | BLACKBOURNEVIEW_S001 | H21 | Scheme | 2022-07-12 15:40 | FRA_3927110720221250.pdf | colej | 3927110720221250 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 1 | 4ravfxh3u3nl5i18lp4 | Low Risk closed | Risk Closed | 44757.4757 | Obs2 | Means Of Giving Warning In Case Of Fire | 45485 | Low | Court Manager | It was noted at the time of inspection the alarm panel was showing a fault. The court manager is aware and an order is with Openview to rectify. | Parts on order
3927 | Blackbourne View | BLACKBOURNEVIEW_S001 | H21 | Scheme | 2022-07-12 15:40 | FRA_3927110720221250.pdf | colej | 3927110720221250 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 1 | 3xaie0a996ll5hz1feq | Low Risk closed | Risk Closed | 44757.4741 | Obs10 | Fire Safety And Notices | 45485 | Low | Court Manager | It was noted at the time of the fire risk assessment that not all of the escape signage and fire action notices were in place. This is being completed by CLC as part of the makeover works and is due to be completed shortly. The court manager is to follow this up to a conclusion asap and liaise with the surveyor if required for support. | These signs are on order with clc
3927 | Blackbourne View | BLACKBOURNEVIEW_S001 | H21 | Scheme | 2022-07-12 15:40 | FRA_3927110720221250.pdf | colej | 3927110720221250 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 1 | 0a2bvf8lexknl5i00hfk | Observation Only | Risk Closed | 44757.4763 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Court Manager | It was pointed out that the closer to the cross corridor doors by flat 17 has an intermittent fault and is due to be replaced. It was functioning at the time of inspection. | These are being replaced today
3927 | Blackbourne View | BLACKBOURNEVIEW_S001 | H21 | Scheme | 2022-07-12 15:40 | FRA_3927110720221250.pdf | colej | 3927110720221250 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 1 | d5pl6s1okkdl5hzib8q | Medium Risk closed | Risk Closed | 44757.4754 | Obs8 | Measures To Limit Fire Spread And Development | 45119 | Medium | Court Manager | It was noted that the communal lounge doors have self closing devices that are not linked to the fire alarm to operate when the alarm sounds. Doors are being held open by a manual latch on the arm of the closer. It is recommended that these are replaced if the doors are required to be held open. The doors need to automatically close upon the sound of the fire alarm. | Will arrange open view to come in and quote the works to have the closures changed
3927 | Blackbourne View | BLACKBOURNEVIEW_S001 | H21 | Scheme | 2022-07-12 15:40 | FRA_3927110720221250.pdf | colej | 3927110720221250 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 1 | mgvs57lx59ml5gp3vvj | Observation Only | Risk Closed | 44757.476 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | 16 number of high risk residents have been identified on the court. PCFRA's/PEEPs have been completed for all and consideration has been given to mobility, mental health capacity, hearing and vision. | No action needed
3927 | Blackbourne View | BLACKBOURNEVIEW_S001 | H21 | Scheme | 2022-07-12 15:40 | FRA_3927110720221250.pdf | colej | 3927110720221250 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 1 | gfqo5mxcg7l5gox740 | Observation Only | Risk Closed | 44757.4745 | Obs1 | The Building | NULL | N/A | Court Manager | Purely observational comment. Compartmentation in the roof space is very good with masonry walls taken to the underside of the roof. | No action needed
3927 | Blackbourne View | BLACKBOURNEVIEW_S001 | H21 | Scheme | 2022-07-12 15:40 | FRA_3927110720221250.pdf | colej | 3927110720221250 | Extra Care | Extra Care South | EC South 1 | Central | Central Patch 1 | ysi8usxggal5hzqdsl | Low Risk closed | Risk Closed | 44757.4737 | Obs8 | Measures To Limit Fire Spread And Development | 45485 | Low | Court Manager | It was noted that there are a number of Dorguard units throughout the court. Although these are considered acceptable, It is recommended for these to be upgraded to fire alarm linked units when replacement is required. | These will upgraded once they fail
4003 | The Elms | JBTHEELMS_S001 | H21 | Scheme | 2022-10-27 12:14 | FRA_4003271020221200.pdf | GerrishR | 4003271020221200 | Retirement Housing | Mid South | Berks and Hampshire North | South | South Patch 7 | 75fczm1wx97l9qyfbh4 | High Risk to be actioned | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | 44953 | High | Court Manager | New court manager in the process of doing it. | NULL
4004 | Anvil Court | ANVIL_S001 | H21 | Scheme | 2021-01-22 16:52 | FRA_4004220120211648.pdf | mayesd | 4004220120211640 | Extra Care | Extra Care South | EC South 3 | South | South Patch 7 | 5sj6s8fmcy7kk8iphan | Low Risk closed | Risk Closed | 44292.4482 | Obs8 | Measures To Limit Fire Spread And Development | 44948 | Low | Court Manager | Flat 8 requires a drop down bar | CLC VISITED ON 1ST APRIL P.M., ENGINEER STUART ANDREWS (CONTRACTS MANAGER) AND COMPLETED JOB FOR DROP DOWN BAR
4004 | Anvil Court | ANVIL_S001 | H21 | Scheme | 2021-01-22 16:52 | FRA_4004220120211648.pdf | mayesd | 4004220120211640 | Extra Care | Extra Care South | EC South 3 | South | South Patch 7 | 37p1w9a1jmqkk8iph8z | Medium Risk closed | Risk Closed | 44497.5799 | Obs7 | Fire Protection Measures | 44583 | Medium | Surveyor | The automatic opener adjacent to the lift requires repairing. An order has been placed | Works complete
4004 | Anvil Court | ANVIL_S001 | H21 | Scheme | 2021-01-22 16:52 | FRA_4004220120211648.pdf | mayesd | 4004220120211640 | Extra Care | Extra Care South | EC South 3 | South | South Patch 7 | m22d8jo1dsmkk8iphcc | Medium Risk closed | Risk Closed | 44260.6633 | Obs16 | Testing And Maintenance | 44583 | Medium | M&E Team | Smoke shaft doors and dry risers have no service contract in place. | AOV's serviced in July 2020, due again July 2021. Dry Risers added to contract and service booked for 4/3/21
4101 | Lord Gort Close | LORDGORT_S001 | H21 | Scheme | 2022-06-22 15:51 | FRA_4101210620222327.pdf | taylors1 | 4101210620222320 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 1 | o2lnwh5ctzl4pegr0l | Medium Risk closed | Risk Closed | 44782.3616 | Obs8 | Measures To Limit Fire Spread And Development | 45099 | Medium | Court Manager | Pack hinge side of cross corridor door adjacent to flat 11 to reduce gap on closing edge | Intumescent packed behind hinge , ticket complete on 8/8/22 ticket number 1549089
4101 | Lord Gort Close | LORDGORT_S001 | H21 | Scheme | 2022-06-22 15:51 | FRA_4101210620222327.pdf | taylors1 | 4101210620222320 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 1 | xngvfh7of3l4pekxvo | Medium Risk closed | Risk Closed | 44782.3622 | Obs8 | Measures To Limit Fire Spread And Development | 45099 | Medium | Court Manager | Pack hinge side of store fire door adj to flat 8 to reduce gap on closing edge | Intumescent packed behind hinge on door completed 8/8/22 ticket number 1549089
4101 | Lord Gort Close | LORDGORT_S001 | H21 | Scheme | 2022-06-22 15:51 | FRA_4101210620222327.pdf | taylors1 | 4101210620222320 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 1 | vopvs13l8nl4pottty | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45099 | Medium | M&E Team | Fixed appliance testing date 2018 | NULL
4103 | Robert Allan Court | ROBERTALLA_S001 | H21 | Scheme | 2022-04-29 11:43 | FRA_4103290420221006.pdf | taylors1 | 4103290420221000 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 1 | x6jvnlsj9hel2kb34x3 | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45045 | Medium | Court Manager | Refix overhead door closer to flat 14 | NULL
4103 | Robert Allan Court | ROBERTALLA_S001 | H21 | Scheme | 2022-04-29 11:43 | FRA_4103290420221006.pdf | taylors1 | 4103290420221000 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 1 | qmgd9bsgyosl2kb1kds | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45045 | Medium | Court Manager | Refix overhead door closer to flat 2 | NULL
4103 | Robert Allan Court | ROBERTALLA_S001 | H21 | Scheme | 2022-04-29 11:43 | FRA_4103290420221006.pdf | taylors1 | 4103290420221000 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 1 | ffvxpk88y8el2kb2bzm | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45045 | Medium | Court Manager | Refix overhead door closer to flat 5 | NULL
4103 | Robert Allan Court | ROBERTALLA_S001 | H21 | Scheme | 2022-04-29 11:43 | FRA_4103290420221006.pdf | taylors1 | 4103290420221000 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 1 | fvhgwa4mxcel2kb3j8w | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45045 | Medium | Court Manager | Refix overhead door closer to flat 16 | NULL
4103 | Robert Allan Court | ROBERTALLA_S001 | H21 | Scheme | 2022-04-29 11:43 | FRA_4103290420221006.pdf | taylors1 | 4103290420221000 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 1 | 07moueb547k9l2kb2qrk | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45045 | Medium | Court Manager | Refix overhead door closer to flat 10 | NULL
4110 | Rowan Croft | ROWANCROFT_S001 | H21 | Scheme | 2022-01-28 15:45 | FRA_4110260120221303.pdf | taylors1 | 4110260120221300 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | 6i2cx81ehaikyyahw6z | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45319 | Low | Court Manager | Adjust staircase fire door floor 1 adj flat 21 to close fully | NULL
4110 | Rowan Croft | ROWANCROFT_S001 | H21 | Scheme | 2022-01-28 15:45 | FRA_4110260120221303.pdf | taylors1 | 4110260120221300 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | j71fphgq2mrkyybmano | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44954 | Medium | Court Manager | Ease bottom edge of door leading into catering kitchen | NULL
4111 | Linskill Park | LINSKILLPARK_S001 | H21 | Scheme | 2022-04-19 15:27 | FRA_4111070420220930.pdf | taylors1 | 4111070420220930 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | hrlkpe2jsw7l1ornw72 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45389 | Low | Court Manager | Intumescent pack across hinges to reduce closing edge gap on inner door to refuse room opp flat 21 | NULL
4111 | Linskill Park | LINSKILLPARK_S001 | H21 | Scheme | 2022-04-19 15:27 | FRA_4111070420220930.pdf | taylors1 | 4111070420220930 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | letnyio807pl1qe6qiw | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45024 | Medium | Court Manager | Rehasng refuse room inner door opp flat 29 | NULL
4111 | Linskill Park | LINSKILLPARK_S001 | H21 | Scheme | 2022-04-19 15:27 | FRA_4111070420220930.pdf | taylors1 | 4111070420220930 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | jfzvseu5nyml1orqyhe | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45023 | Medium | Court Manager | Adjust cross corridor door adjacent to flat 17 to close on release of fire alarm | NULL
4111 | Linskill Park | LINSKILLPARK_S001 | H21 | Scheme | 2022-04-19 15:27 | FRA_4111070420220930.pdf | taylors1 | 4111070420220930 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | k8kusdqdx4l1ot1qag | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45023 | Medium | Court Manager | Scheme management advised that no motorised scooters to be parked on corridors | NULL
4111 | Linskill Park | LINSKILLPARK_S001 | H21 | Scheme | 2022-04-19 15:27 | FRA_4111070420220930.pdf | taylors1 | 4111070420220930 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | pipnjhvhq6kl1os3avd | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45023 | Medium | Court Manager | Intumescent pack across bottom hinges to reduce closing edge gap on main door leading into refuse room opp flat 21 | NULL
4111 | Linskill Park | LINSKILLPARK_S001 | H21 | Scheme | 2022-04-19 15:27 | FRA_4111070420220930.pdf | taylors1 | 4111070420220930 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | ul35e2yhdhfl1qf5e5k | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45024 | Medium | Court Manager | Flat 57 ease door to close | NULL
4111 | Linskill Park | LINSKILLPARK_S001 | H21 | Scheme | 2022-04-19 15:27 | FRA_4111070420220930.pdf | taylors1 | 4111070420220930 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | ttk8ajblkbol1qf3yqf | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45024 | Medium | Court Manager | Flat 26 intumescent packers to reduce gap on closing edge | NULL
4111 | Linskill Park | LINSKILLPARK_S001 | H21 | Scheme | 2022-04-19 15:27 | FRA_4111070420220930.pdf | taylors1 | 4111070420220930 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | tihs8wlyovbl1ou4aqq | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45023 | Medium | Court Manager | Ease catering office door to close | NULL
4111 | Linskill Park | LINSKILLPARK_S001 | H21 | Scheme | 2022-04-19 15:27 | FRA_4111070420220930.pdf | taylors1 | 4111070420220930 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | sqe4rtesp5ol1or97vf | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45389 | Low | Court Manager | Intumescent Pack bottom hinge on second floor assisted bathroom door to reduce gap on closing edge | NULL
4111 | Linskill Park | LINSKILLPARK_S001 | H21 | Scheme | 2022-04-19 15:27 | FRA_4111070420220930.pdf | taylors1 | 4111070420220930 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | rvewlzrll1osn8xr | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45023 | Medium | Court Manager | Intumescent pack across hinges to reduce closing edge gap on outer refuse door op flat 7 | NULL
4111 | Linskill Park | LINSKILLPARK_S001 | H21 | Scheme | 2022-04-19 15:27 | FRA_4111070420220930.pdf | taylors1 | 4111070420220930 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | 7gogzhbh4mml1qf29hy | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45024 | Medium | Court Manager | Flat 19 intumescent packers to reduce gap on closing edge | NULL
4111 | Linskill Park | LINSKILLPARK_S001 | H21 | Scheme | 2022-04-19 15:27 | FRA_4111070420220930.pdf | taylors1 | 4111070420220930 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | 63xgo7lzygl1ou4wr1 | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45023 | Medium | Court Manager | Adjust catering kitchen swing door to close to rebate | NULL
4111 | Linskill Park | LINSKILLPARK_S001 | H21 | Scheme | 2022-04-19 15:27 | FRA_4111070420220930.pdf | taylors1 | 4111070420220930 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | 5g5ul2yzcurl1qf4dx6 | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45024 | Medium | Court Manager | Flat 35 intumescent packers to reduce gap on top edge | NULL
4111 | Linskill Park | LINSKILLPARK_S001 | H21 | Scheme | 2022-04-19 15:27 | FRA_4111070420220930.pdf | taylors1 | 4111070420220930 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | 37a2l3n111l1osch7p | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45023 | Medium | Court Manager | Intumescent pack across hinges to reduce closing edge gap on fire door on ground floor staircase adjacent to lift | NULL
4111 | Linskill Park | LINSKILLPARK_S001 | H21 | Scheme | 2022-04-19 15:27 | FRA_4111070420220930.pdf | taylors1 | 4111070420220930 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | a4ak1y924a7l1os18wb | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45389 | Low | Court Manager | Intumescent pack across hinges to reduce closing edge gap on inner door to refuse room opp flat 34 | NULL
4111 | Linskill Park | LINSKILLPARK_S001 | H21 | Scheme | 2022-04-19 15:27 | FRA_4111070420220930.pdf | taylors1 | 4111070420220930 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | x5fvjvf1chsl1qf2ylt | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45024 | Medium | Court Manager | Flat 25 Intumescent pack across hinges to reduce closing gap on closing edge | NULL
4111 | Linskill Park | LINSKILLPARK_S001 | H21 | Scheme | 2022-04-19 15:27 | FRA_4111070420220930.pdf | taylors1 | 4111070420220930 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | xnx8u63cbml1oshq4p | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45023 | Medium | Court Manager | Intumescent pack across hinges to reduce closing edge gap on opening plant room door | NULL
4112 | Lawrence Hill Court | LAWRENCEHILL_S001 | H21 | Scheme | 2022-06-01 10:33 | FRA_4112010620220840.pdf | taylors1 | 4112010620220840 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 1 | a2ens56xx8il3va4h0d | Medium Risk closed | Risk Closed | 44750.7201 | Obs8 | Measures To Limit Fire Spread And Development | 45078 | Medium | Court Manager | Supply and fit combined smoke seals to kitchen door edges | Works completed on 24 July by Robinson Property Maintenance
4112 | Lawrence Hill Court | LAWRENCEHILL_S001 | H21 | Scheme | 2022-06-01 10:33 | FRA_4112010620220840.pdf | taylors1 | 4112010620220840 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 1 | eli5dvufpjil3vdqok9 | Medium Risk closed | Risk Closed | 44733.5361 | Obs8 | Measures To Limit Fire Spread And Development | 45078 | Medium | Court Manager | Flat 26 refix door closer | Robinson's maintenance completed work 14.07.22
4112 | Lawrence Hill Court | LAWRENCEHILL_S001 | H21 | Scheme | 2022-06-01 10:33 | FRA_4112010620220840.pdf | taylors1 | 4112010620220840 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 1 | 501e3wb3fll3vdq04o | Medium Risk closed | Risk Closed | 44733.5374 | Obs8 | Measures To Limit Fire Spread And Development | 45078 | Medium | Court Manager | Flat 18 refix door closer | Robinson's maintenance completed work 14.07.22
4112 | Lawrence Hill Court | LAWRENCEHILL_S001 | H21 | Scheme | 2022-06-01 10:33 | FRA_4112010620220840.pdf | taylors1 | 4112010620220840 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 1 | 4upkkt0onu3l3vdrset | Medium Risk closed | Risk Closed | 44750.7219 | Obs8 | Measures To Limit Fire Spread And Development | 45078 | Medium | Court Manager | Flat 23 pack bottom hinge with intumescent packers to reduce gap on closing edge | Works completed on 24 July by Robinson Property Maintenance
4112 | Lawrence Hill Court | LAWRENCEHILL_S001 | H21 | Scheme | 2022-06-01 10:33 | FRA_4112010620220840.pdf | taylors1 | 4112010620220840 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 1 | rmwrfgpr0kl3vdrdcg | Medium Risk closed | Risk Closed | 44733.5352 | Obs8 | Measures To Limit Fire Spread And Development | 45078 | Medium | Court Manager | Flat 39 refix door closer | Robinson's maintenance completed work 14.07.22
4114 | East Croft Court | EASTCROFT_S001 | H21 | Scheme | 2022-02-02 15:54 | FRA_4114020220221553.pdf | whitek2 | 4114020220221550 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 8 | r0rsqy5yaemkz5qc2f2 | Medium Risk closed | Risk Closed | 44614.4027 | Obs8 | Measures To Limit Fire Spread And Development | 44959 | Medium | Court Manager | Flat 3 Door not latching tight into frame and gap not acceptable closing side Adjust as necessary | Job completed by R&D
4114 | East Croft Court | EASTCROFT_S001 | H21 | Scheme | 2022-02-02 15:54 | FRA_4114020220221553.pdf | whitek2 | 4114020220221550 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 8 | u1vjyne16mbkz5qc2co | Medium Risk closed | Risk Closed | 44614.4029 | Obs7 | Fire Protection Measures | 44959 | Medium | Court Manager | Fire door first floor near cleaners cupboard require slight adjustment to close tight to frame | Job completed by R&D
4114 | East Croft Court | EASTCROFT_S001 | H21 | Scheme | 2022-02-02 15:54 | FRA_4114020220221553.pdf | whitek2 | 4114020220221550 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 8 | qhf2499ucykz5qc2dc | Medium Risk closed | Risk Closed | 44614.4021 | Obs7 | Fire Protection Measures | 44959 | Medium | Court Manager | Door between flats 39 and 29 magnetic restraint loose and not hold side panel door in open position | Job completed by R&D
4114 | East Croft Court | EASTCROFT_S001 | H21 | Scheme | 2022-02-02 15:54 | FRA_4114020220221553.pdf | whitek2 | 4114020220221550 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 8 | otcbmah1jigkz5qc2ed | Medium Risk closed | Risk Closed | 44614.4024 | Obs7 | Fire Protection Measures | 44959 | Medium | Court Manager | Corridor door near scooter store requires slight adjustment to close tight to the frame | Job completed by R&D
4114 | East Croft Court | EASTCROFT_S001 | H21 | Scheme | 2022-02-02 15:54 | FRA_4114020220221553.pdf | whitek2 | 4114020220221550 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 8 | edprt67y0zkz5qc2dy | Medium Risk closed | Risk Closed | 44614.4018 | Obs7 | Fire Protection Measures | 44959 | Medium | Court Manager | Door between flats 14 and 15 requires slight adjustment to ensure it closes tight to frame | Job completed by R & D
4115 | William Roberts Court | WILLIAMROBE_S001 | H21 | Scheme | 2022-04-29 12:06 | FRA_4115290420221144.pdf | taylors1 | 4115290420221140 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 1 | bzkvo7xp9mfl2kbllpr | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45045 | Medium | Court Manager | Flat 5 refix overhead closer | NULL
4115 | William Roberts Court | WILLIAMROBE_S001 | H21 | Scheme | 2022-04-29 12:06 | FRA_4115290420221144.pdf | taylors1 | 4115290420221140 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 1 | 95oo9dd2d3kl2kbs7b0 | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45045 | Medium | Court Manager | S&F fire rated loft hatch within plant roof and fire stop around ceiling penetrations, liaise with surveyor to obtain contractor and costs | NULL
4115 | William Roberts Court | WILLIAMROBE_S001 | H21 | Scheme | 2022-04-29 12:06 | FRA_4115290420221144.pdf | taylors1 | 4115290420221140 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 1 | q13dtme76ql2kbmpoe | Medium Risk closed | Risk Closed | 44680.6775 | Obs8 | Measures To Limit Fire Spread And Development | 45045 | Medium | Surveyor | Flat 21 refix overhead closer | This was referred for action by the CM
4115 | William Roberts Court | WILLIAMROBE_S001 | H21 | Scheme | 2022-04-29 12:06 | FRA_4115290420221144.pdf | taylors1 | 4115290420221140 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 1 | xhicm94h6ul2kbmbdj | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45045 | Medium | Court Manager | Flat 8 refix overhead closer | NULL
4115 | William Roberts Court | WILLIAMROBE_S001 | H21 | Scheme | 2022-04-29 12:06 | FRA_4115290420221144.pdf | taylors1 | 4115290420221140 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 1 | wfx36428esrl2kbqeuj | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45045 | Medium | Court Manager | Check exposed cable within lift motor room isolate safely within junction box or remove back to DB | NULL
4117 | Robert Wheatman Court | ROBERTWHEA_S001 | H21 | Scheme | 2022-04-14 13:19 | FRA_4117130420221042.pdf | whitek2 | 4117130420221040 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 8 | w0sw6ffk0ctl1xfpar7 | Observation Only | Risk Closed | 44757.4272 | Obs9 | Escape Lighting | NULL | N/A | Surveyor | Lighting is adequate however the fittings are aged and illumination levels low. Need to consider changing to LED | Recommend for future SIP
4117 | Robert Wheatman Court | ROBERTWHEA_S001 | H21 | Scheme | 2022-04-14 13:19 | FRA_4117130420221042.pdf | whitek2 | 4117130420221040 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 8 | xj4ghitxidl1xeec75 | Low Risk closed | Risk Closed | 44692.6997 | Obs7 | Fire Protection Measures | 45395 | Low | Court Manager | Door to first floor sitting room adjacent to flat 28 catch defective requires replacing | Works completed on 10.5.22 by Robinson Property Maintenance
4117 | Robert Wheatman Court | ROBERTWHEA_S001 | H21 | Scheme | 2022-04-14 13:19 | FRA_4117130420221042.pdf | whitek2 | 4117130420221040 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 8 | psezjtxlk1ql1xg80ie | Low Risk closed | Risk Closed | 44692.7005 | Obs8 | Measures To Limit Fire Spread And Development | 45395 | Low | Court Manager | Flat 36 require closer adjusting as door slamming | Works completed on 10.5.22 by Robinson Property Maintenance
4117 | Robert Wheatman Court | ROBERTWHEA_S001 | H21 | Scheme | 2022-04-14 13:19 | FRA_4117130420221042.pdf | whitek2 | 4117130420221040 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 8 | o9nlf8p6ril1xek55q | Medium Risk closed | Risk Closed | 44692.6991 | Obs7 | Fire Protection Measures | 45029 | Medium | Court Manager | First floor firedoor leading to stairs next to lift catching carpet needs bottom edge easysing | Works completed 10.05.22 by Robinson Property Maintenance
4117 | Robert Wheatman Court | ROBERTWHEA_S001 | H21 | Scheme | 2022-04-14 13:19 | FRA_4117130420221042.pdf | whitek2 | 4117130420221040 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 8 | i89jsivci3l1xi49kp | Low Risk closed | Risk Closed | 44692.701 | Obs10 | Fire Safety And Notices | 45395 | Low | Court Manager | Running man sign needs fixing above door cor Staircase lobby leading to flats 11-17 | Works completed on 10.5.22 by Robinson Property Maintenance
4117 | Robert Wheatman Court | ROBERTWHEA_S001 | H21 | Scheme | 2022-04-14 13:19 | FRA_4117130420221042.pdf | whitek2 | 4117130420221040 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 8 | 9u90wh6816tl1xe9bi2 | Observation Only | Risk Closed | 44757.4279 | Obs7 | Fire Protection Measures | NULL | N/A | Surveyor | No markings to identify if glazing in first floor sitting room is fire rated or if safety glass require further investigation | Glass complient at time of installation notional fire rating
4117 | Robert Wheatman Court | ROBERTWHEA_S001 | H21 | Scheme | 2022-04-14 13:19 | FRA_4117130420221042.pdf | whitek2 | 4117130420221040 | Retirement Housing | North East | Tyne and Wear and Northumberland | North | North Patch 8 | 09u14ud11ji6l1xeuewl | Medium Risk closed | Risk Closed | 44757.4264 | Obs7 | Fire Protection Measures | 45029 | Medium | Surveyor | Ground floor fire door between guest room and flat 7 requires adjustment to close into leading edge rebate with side door | Works complete
4124 | Priory Court | PRIORY_S001 | H21 | Scheme | 2022-06-10 12:37 | FRA_4124100620221222.pdf | taylors1 | 4124100620221220 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | 17nsuy90enil48d0mj4 | Low Risk closed | Risk Closed | 44746.5035 | Obs8 | Measures To Limit Fire Spread And Development | 45453 | Low | Court Manager | Adjust closing lath to HCM office door | Raised a job with R&D
4124 | Priory Court | PRIORY_S001 | H21 | Scheme | 2022-06-10 12:37 | FRA_4124100620221222.pdf | taylors1 | 4124100620221220 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | 8yie61h1l25l48d0mm5 | Low Risk closed | Risk Closed | 44743.5855 | Obs10 | Fire Safety And Notices | 45453 | Low | Court Manager | Write assembly location on fire action notice adj to progressive security door | This has been completed
4124 | Priory Court | PRIORY_S001 | H21 | Scheme | 2022-06-10 12:37 | FRA_4124100620221222.pdf | taylors1 | 4124100620221220 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | 875ei0s8udql48d0mf7 | Low Risk closed | Risk Closed | 44746.5046 | Obs8 | Measures To Limit Fire Spread And Development | 45453 | Low | Court Manager | Replace intumescent glazing compound to 1f sitting room Fd glass loose | RAISED A JOB WITH R&D
4124 | Priory Court | PRIORY_S001 | H21 | Scheme | 2022-06-10 12:37 | FRA_4124100620221222.pdf | taylors1 | 4124100620221220 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | bcwqtd9p4xel48d0mi8 | Medium Risk closed | Risk Closed | 44746.5038 | Obs8 | Measures To Limit Fire Spread And Development | 45087 | Medium | Court Manager | Fix hardwood flipping to closing edge of salon door to alleviate gap to 3mm | RAISED A JOB WITH R&D
4124 | Priory Court | PRIORY_S001 | H21 | Scheme | 2022-06-10 12:37 | FRA_4124100620221222.pdf | taylors1 | 4124100620221220 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | cxkbxhb41fal48d0mjy | Low Risk closed | Risk Closed | 44746.4745 | Obs8 | Measures To Limit Fire Spread And Development | 45453 | Low | Court Manager | Intumescent packer to bottom hinge to reduce gap at head of door flat 28 | reported the job to R&D awaiting them coming out to fix the door
4124 | Priory Court | PRIORY_S001 | H21 | Scheme | 2022-06-10 12:37 | FRA_4124100620221222.pdf | taylors1 | 4124100620221220 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | i35h67mpw8el48d0mmt | Low Risk closed | Risk Closed | 44743.5512 | Obs10 | Fire Safety And Notices | 45453 | Low | Court Manager | Write assembly location on fire action notice to external exit from catering kitchen | this has been completed wrote on assembly location
4124 | Priory Court | PRIORY_S001 | H21 | Scheme | 2022-06-10 12:37 | FRA_4124100620221222.pdf | taylors1 | 4124100620221220 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | m0rpatkwpal48d0mla | Medium Risk closed | Risk Closed | 44746.503 | Obs10 | Fire Safety And Notices | 45087 | Medium | Court Manager | Supply and fit fire exit directional sign outside of flat 11 ceiling directing to fire exit at bottom of staircase | I have raised the job with R&D
4124 | Priory Court | PRIORY_S001 | H21 | Scheme | 2022-06-10 12:37 | FRA_4124100620221222.pdf | taylors1 | 4124100620221220 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | wx0hdaa51bpl48d0mge | Low Risk closed | Risk Closed | 44754.485 | Obs8 | Measures To Limit Fire Spread And Development | 45453 | Low | Court Manager | Refix locking nut to free swing closer to cross corridor door adjacent to flat 37 | this has now been completed from r&d
4124 | Priory Court | PRIORY_S001 | H21 | Scheme | 2022-06-10 12:37 | FRA_4124100620221222.pdf | taylors1 | 4124100620221220 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | yfwbg4sic2gl48d0mhi | Low Risk closed | Risk Closed | 44746.5032 | Obs8 | Measures To Limit Fire Spread And Development | 45453 | Low | Court Manager | Replace stop lath to closing edge of cross corridor door adjacent to flat 7 | RAISED A JOB WITH OPENVIEW
4125 | Winton Court | WINTON_S001 | H21 | Scheme | 2022-08-23 13:37 | FRA_4125230820221330.pdf | taylors1 | 4125230820221330 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | g1r15f5j98l76602rt | Low Risk closed | Risk Closed | 44798.3547 | Obs8 | Measures To Limit Fire Spread And Development | 45527 | Low | Court Manager | Flat 11 replace letterplate | R&D completed 24/08/22
4125 | Winton Court | WINTON_S001 | H21 | Scheme | 2022-08-23 13:37 | FRA_4125230820221330.pdf | taylors1 | 4125230820221330 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | gsr9d58jo96l76602r6 | Low Risk closed | Risk Closed | 44798.3537 | Obs8 | Measures To Limit Fire Spread And Development | 45527 | Low | Court Manager | Flat 15 adjust closer | R&D completed 24/8/22
4125 | Winton Court | WINTON_S001 | H21 | Scheme | 2022-08-23 13:37 | FRA_4125230820221330.pdf | taylors1 | 4125230820221330 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | o8x23y4rscbl76602oz | Low Risk closed | Risk Closed | 44798.3544 | Obs5 | Evacuation Strategy And Training | 45527 | Low | Court Manager | 2 copies of fire zone plan with flats marked | marked office area - zones are in fire file
4125 | Winton Court | WINTON_S001 | H21 | Scheme | 2022-08-23 13:37 | FRA_4125230820221330.pdf | taylors1 | 4125230820221330 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | uh6r9c61jcnl76602tn | Low Risk closed | Risk Closed | 44816.3247 | Obs10 | Fire Safety And Notices | 45527 | Low | Court Manager | Additional fire action notice adj to flat 5 | bought new sign and displayed in the area requested
4125 | Winton Court | WINTON_S001 | H21 | Scheme | 2022-08-23 13:37 | FRA_4125230820221330.pdf | taylors1 | 4125230820221330 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | ryaiqy0yi9l76602ux | Low Risk to be actioned | Risk Open | NULL | Obs11 | Fire Fighting Equipment | 45192 | Low | Other | P50 fire extinguishers located throughout corridors | NULL
4125 | Winton Court | WINTON_S001 | H21 | Scheme | 2022-08-23 13:37 | FRA_4125230820221330.pdf | taylors1 | 4125230820221330 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | euev9862cl76602qm | Low Risk closed | Risk Closed | 44798.3539 | Obs8 | Measures To Limit Fire Spread And Development | 45527 | Low | Court Manager | Flat 8 adjust door closer | R&D completed 24/8/22
4125 | Winton Court | WINTON_S001 | H21 | Scheme | 2022-08-23 13:37 | FRA_4125230820221330.pdf | taylors1 | 4125230820221330 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | 06xvlk3mpobl76602ss | Low Risk closed | Risk Closed | 44797.4351 | Obs10 | Fire Safety And Notices | 45527 | Low | Court Manager | Additional fire action notice adj to flat 14 | re-marked
4125 | Winton Court | WINTON_S001 | H21 | Scheme | 2022-08-23 13:37 | FRA_4125230820221330.pdf | taylors1 | 4125230820221330 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | 71c50z7bpr4l76602pw | Medium Risk closed | Risk Closed | 44798.3532 | Obs8 | Measures To Limit Fire Spread And Development | 45161 | Medium | Court Manager | Adjust replace closer to cross corridor door adjacent to flat 28 not closing to rebate of frame | R&D completed job
4126 | Fountain Court | FOUNTAIN_S001 | H21 | Scheme | 2022-05-31 08:53 | FRA_4126310520220842.pdf | taylors1 | 4126310520220840 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | 77qyf21bdnal3tuqd5q | Low Risk closed | Risk Closed | 44748.427 | Obs8 | Measures To Limit Fire Spread And Development | 45443 | Low | Court Manager | Fire stopping to warden call cable above ceiling in lounge above door | Hole filled by R&D
4126 | Fountain Court | FOUNTAIN_S001 | H21 | Scheme | 2022-05-31 08:53 | FRA_4126310520220842.pdf | taylors1 | 4126310520220840 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | 05f8qzqepe89l3tuqd6u | Low Risk closed | Risk Closed | 44748.4266 | Obs8 | Measures To Limit Fire Spread And Development | 45443 | Low | Court Manager | Replace external exit door lock leading from catering kitchen to a thumb turn remove Yale keep | Thumb turn has been fitted
4126 | Fountain Court | FOUNTAIN_S001 | H21 | Scheme | 2022-05-31 08:53 | FRA_4126310520220842.pdf | taylors1 | 4126310520220840 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | 9ywk45g7doul3tuqdag | Medium Risk closed | Risk Closed | 44756.658 | Obs15 | Management Of Fire Safety | 45077 | Medium | Court Manager | Red fire box required | Redbox supplied and fitted by R&D
4126 | Fountain Court | FOUNTAIN_S001 | H21 | Scheme | 2022-05-31 08:53 | FRA_4126310520220842.pdf | taylors1 | 4126310520220840 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | 83gntgu53utl3tuqd86 | Low Risk closed | Risk Closed | 44721.526 | Obs10 | Fire Safety And Notices | 45443 | Low | Court Manager | Assembly point to write on fire action notice GF staircase adj to flat 4 | Written on sign 'main car park'
4126 | Fountain Court | FOUNTAIN_S001 | H21 | Scheme | 2022-05-31 08:53 | FRA_4126310520220842.pdf | taylors1 | 4126310520220840 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | oedf16ju7rhl3tuqd53 | Low Risk closed | Risk Closed | 44729.5734 | Obs8 | Measures To Limit Fire Spread And Development | 45443 | Low | Court Manager | Adjust closer so door closes tight to rebate GF staircase fire door opp flat 4 | R&D completed adjustments
4126 | Fountain Court | FOUNTAIN_S001 | H21 | Scheme | 2022-05-31 08:53 | FRA_4126310520220842.pdf | taylors1 | 4126310520220840 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | hosawquaywul3tuzx9u | Medium Risk closed | Risk Closed | 44756.6582 | Obs2 | Means Of Giving Warning In Case Of Fire | 45077 | Medium | Court Manager | Red fire box to be fitted in foyer | Red box supplied and fitted by R&D
4126 | Fountain Court | FOUNTAIN_S001 | H21 | Scheme | 2022-05-31 08:53 | FRA_4126310520220842.pdf | taylors1 | 4126310520220840 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | il1zp2jjg0ll3tuqd92 | Low Risk closed | Risk Closed | 44721.5292 | Obs10 | Fire Safety And Notices | 45443 | Low | Court Manager | Assembly point to write on fire action notice adj to final exit door to catering kitchen | Written on 'main car park'
4127 | Marigold Court | MARIGOLD_S001 | H21 | Scheme | 2022-07-13 16:44 | FRA_4127130720221022.pdf | taylors1 | 4127130720221020 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | io5jb5bulpjl5jf9exr | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45486 | Low | Court Manager | Flat 8 adjust lock keep | NULL
4127 | Marigold Court | MARIGOLD_S001 | H21 | Scheme | 2022-07-13 16:44 | FRA_4127130720221022.pdf | taylors1 | 4127130720221020 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | m592g9qfu1fl5jfzxtm | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45486 | Low | Court Manager | Supply and fire exit sign on cross corridor door frame glass adjacent to flat 40 | NULL
4127 | Marigold Court | MARIGOLD_S001 | H21 | Scheme | 2022-07-13 16:44 | FRA_4127130720221022.pdf | taylors1 | 4127130720221020 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | k8l4e8kzb4l5jfxfbw | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45486 | Low | Court Manager | Supply and fire exit sign from ceiling adjacent to flat 23 | NULL
4127 | Marigold Court | MARIGOLD_S001 | H21 | Scheme | 2022-07-13 16:44 | FRA_4127130720221022.pdf | taylors1 | 4127130720221020 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | npdi4j18c6el5jg9plf | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45486 | Low | Court Manager | Adjust closer to latch laundry door | NULL
4127 | Marigold Court | MARIGOLD_S001 | H21 | Scheme | 2022-07-13 16:44 | FRA_4127130720221022.pdf | taylors1 | 4127130720221020 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | o00qiedvd99l5jfa1wm | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45486 | Low | Court Manager | Flat 35 adjust closer to latch door | NULL
4127 | Marigold Court | MARIGOLD_S001 | H21 | Scheme | 2022-07-13 16:44 | FRA_4127130720221022.pdf | taylors1 | 4127130720221020 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | pyx6pr29c3l5jfh8uy | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45486 | Low | Court Manager | Fit a 300x300 intumescent vent panel into store door adjacent to first floor lift overheating with server | NULL
4127 | Marigold Court | MARIGOLD_S001 | H21 | Scheme | 2022-07-13 16:44 | FRA_4127130720221022.pdf | taylors1 | 4127130720221020 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | srni6kovz6jl5jg3v05 | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45486 | Low | Court Manager | Supply and fire exit sign from ceiling adjacent to flat 15 | NULL
4127 | Marigold Court | MARIGOLD_S001 | H21 | Scheme | 2022-07-13 16:44 | FRA_4127130720221022.pdf | taylors1 | 4127130720221020 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | t488807fycbl5jfmzqd | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45120 | Medium | Court Manager | Replace broken cross corridor door hold back adjacent to guest room | NULL
4127 | Marigold Court | MARIGOLD_S001 | H21 | Scheme | 2022-07-13 16:44 | FRA_4127130720221022.pdf | taylors1 | 4127130720221020 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | zim5g7sfdpl5jfurfn | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45486 | Low | Court Manager | Supply and fire exit sign from ceiling adjacent to flat 5 | NULL
4128 | Callendar Court | CALLENDAR_S001 | H21 | Scheme | 2022-03-30 15:40 | FRA_4128300320221126.pdf | lofthousei | 4128300320221120 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | km7qlk452sel1dfaw6z | Observation Only | Risk Closed | 44655.4069 | Obs10 | Fire Safety And Notices | NULL | N/A | Court Manager | Non standard Fire Action Notices used throughout. | Ordered some Fire Action Notices which are displayed throughout the building.
4128 | Callendar Court | CALLENDAR_S001 | H21 | Scheme | 2022-03-30 15:40 | FRA_4128300320221126.pdf | lofthousei | 4128300320221120 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | at47cc3fsrcl1doa8gq | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45381 | Low | Surveyor | Sample inspection shows facade cladding is suitably compartmented, however further sampling is required to verify compartmentation at other floor levels. | NULL
4129 | Beckwith Mews | BECKWITHMEWS_S001 | H21 | Scheme | 2022-08-04 18:48 | FRA_4129040820221216.pdf | whitek2 | 4129040820221210 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | ew9ka5h15mel6eyc3w9 | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45142 | Medium | Court Manager | Evacuation route from kitchen impeared due to freezer requires relocating | NULL
4129 | Beckwith Mews | BECKWITHMEWS_S001 | H21 | Scheme | 2022-08-04 18:48 | FRA_4129040820221216.pdf | whitek2 | 4129040820221210 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | edc5n5gbkqfl6ey0cjc | Medium Risk closed | Risk Closed | 44844.5387 | Obs8 | Measures To Limit Fire Spread And Development | 45142 | Medium | Court Manager | Flat 30 fire door catching on bottom edge requires adjustment | Work carried out by R&D
4129 | Beckwith Mews | BECKWITHMEWS_S001 | H21 | Scheme | 2022-08-04 18:48 | FRA_4129040820221216.pdf | whitek2 | 4129040820221210 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | bswhpuz7uyl6ey0ckj | Medium Risk closed | Risk Closed | 44844.539 | Obs8 | Measures To Limit Fire Spread And Development | 45142 | Medium | Court Manager | Flat 7 requires closer adjusting not latching | Work carried out by R&D
4129 | Beckwith Mews | BECKWITHMEWS_S001 | H21 | Scheme | 2022-08-04 18:48 | FRA_4129040820221216.pdf | whitek2 | 4129040820221210 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | 7e1mcbh56tl6ey0ck3 | Medium Risk closed | Risk Closed | 44844.5379 | Obs8 | Measures To Limit Fire Spread And Development | 45142 | Medium | Court Manager | Flat 18 fire door not closing when activated investigate and | Work completed by R&D
4129 | Beckwith Mews | BECKWITHMEWS_S001 | H21 | Scheme | 2022-08-04 18:48 | FRA_4129040820221216.pdf | whitek2 | 4129040820221210 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | lcar180p86kl6ey5gww | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45142 | Medium | Court Manager | Number of electrical appliances in the kitchen and servery area require PAT testing | NULL
4129 | Beckwith Mews | BECKWITHMEWS_S001 | H21 | Scheme | 2022-08-04 18:48 | FRA_4129040820221216.pdf | whitek2 | 4129040820221210 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | s13qhsid06l6fbfxda | Medium Risk to be actioned | Risk Open | NULL | Obs13 | Other Relevant Fixed Systems | 45142 | Medium | Court Manager | Automatic window vents not working and chain missing arrange necessary repairs | NULL
4129 | Beckwith Mews | BECKWITHMEWS_S001 | H21 | Scheme | 2022-08-04 18:48 | FRA_4129040820221216.pdf | whitek2 | 4129040820221210 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | r5kd9xfk6l6ey0cif | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45142 | Medium | Court Manager | Front servery hot plates -daisey chaining electric extension leads- Requires adequate sockets installing and cables mechanically protected in metal conduit | NULL
4129 | Beckwith Mews | BECKWITHMEWS_S001 | H21 | Scheme | 2022-08-04 18:48 | FRA_4129040820221216.pdf | whitek2 | 4129040820221210 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | zekkjqahrul6ey16ug | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45142 | Medium | Court Manager | Kitchen to servery door needs linking to fire alarm to close when activated | NULL
4129 | Beckwith Mews | BECKWITHMEWS_S001 | H21 | Scheme | 2022-08-04 18:48 | FRA_4129040820221216.pdf | whitek2 | 4129040820221210 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | x67glclmaurl6ey3ia3 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45508 | Low | Court Manager | Cupboard door in kitchen requires replacement | NULL
4130 | Bramble Hollow | BRAMBLEHOLLOW_S001 | H21 | Scheme | 2022-09-12 13:55 | FRA_4130120920221336.pdf | taylors1 | 4130120920221330 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | wvngmovoqxl7yr1ck4 | Low Risk closed | Risk Closed | 44831.7389 | Obs8 | Measures To Limit Fire Spread And Development | 45547 | Low | Court Manager | Fault on aov at end of corridor adjacent to flat 17 | Contacted R & D
4130 | Bramble Hollow | BRAMBLEHOLLOW_S001 | H21 | Scheme | 2022-09-12 13:55 | FRA_4130120920221336.pdf | taylors1 | 4130120920221330 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | r9xfw4mrwinl7yr1ckw | Low Risk closed | Risk Closed | 44831.7395 | Obs8 | Measures To Limit Fire Spread And Development | 45547 | Low | Court Manager | Flat 19 pack bottom hinge to reduce closing edge gap | Contacted R & D
4130 | Bramble Hollow | BRAMBLEHOLLOW_S001 | H21 | Scheme | 2022-09-12 13:55 | FRA_4130120920221336.pdf | taylors1 | 4130120920221330 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | lej1yavud1l7yr1clp | Low Risk closed | Risk Closed | 44901.6349 | Obs8 | Measures To Limit Fire Spread And Development | 45547 | Low | Court Manager | Flat 15 refix letterbox | contacted R & D
4130 | Bramble Hollow | BRAMBLEHOLLOW_S001 | H21 | Scheme | 2022-09-12 13:55 | FRA_4130120920221336.pdf | taylors1 | 4130120920221330 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | lnpltg202mil7yr1cqa | Low Risk closed | Risk Closed | 44831.7411 | Obs8 | Measures To Limit Fire Spread And Development | 45547 | Low | Court Manager | Adjust closer to GF refuse room inner door | Contacted R & D
4130 | Bramble Hollow | BRAMBLEHOLLOW_S001 | H21 | Scheme | 2022-09-12 13:55 | FRA_4130120920221336.pdf | taylors1 | 4130120920221330 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | j2c2035q8nl7yr1cmv | Low Risk closed | Risk Closed | 44868.4895 | Obs8 | Measures To Limit Fire Spread And Development | 45547 | Low | Court Manager | Flat 37 pack bottom hinge to reduce closing edge gap | Contacted R & D
4130 | Bramble Hollow | BRAMBLEHOLLOW_S001 | H21 | Scheme | 2022-09-12 13:55 | FRA_4130120920221336.pdf | taylors1 | 4130120920221330 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | ispf5f2u4jbl7yr1cps | Low Risk closed | Risk Closed | 44831.7393 | Obs8 | Measures To Limit Fire Spread And Development | 45547 | Low | Court Manager | S&F intumescent vent to GF comms room door | Contacted R & D
4130 | Bramble Hollow | BRAMBLEHOLLOW_S001 | H21 | Scheme | 2022-09-12 13:55 | FRA_4130120920221336.pdf | taylors1 | 4130120920221330 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | hxwfb997vhvl7yr1cnp | Low Risk closed | Risk Closed | 44831.7403 | Obs8 | Measures To Limit Fire Spread And Development | 45547 | Low | Court Manager | Adjust closer to staircase fire door not closing to rebate adjacent to flat 46 | Contacted R & D
4130 | Bramble Hollow | BRAMBLEHOLLOW_S001 | H21 | Scheme | 2022-09-12 13:55 | FRA_4130120920221336.pdf | taylors1 | 4130120920221330 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | i3i6sbcrsrpl7yr1cmd | Low Risk closed | Risk Closed | 44901.6363 | Obs8 | Measures To Limit Fire Spread And Development | 45547 | Low | Court Manager | Flat 26 refix letterbox | contacted R & D
4130 | Bramble Hollow | BRAMBLEHOLLOW_S001 | H21 | Scheme | 2022-09-12 13:55 | FRA_4130120920221336.pdf | taylors1 | 4130120920221330 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | 30sej3awanel7yr1con | Low Risk closed | Risk Closed | 44868.4912 | Obs8 | Measures To Limit Fire Spread And Development | 45547 | Low | Court Manager | Adjust closer to cross corridor door adjacent to flat 26 | contacted R & D
4130 | Bramble Hollow | BRAMBLEHOLLOW_S001 | H21 | Scheme | 2022-09-12 13:55 | FRA_4130120920221336.pdf | taylors1 | 4130120920221330 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | dxaxdfxx1m8l7yr1co6 | Medium Risk closed | Risk Closed | 44831.7398 | Obs8 | Measures To Limit Fire Spread And Development | 45181 | Medium | Court Manager | Refix closing lath to staircase door on 1f adjacent to flat 25 | Contacted R & D
4130 | Bramble Hollow | BRAMBLEHOLLOW_S001 | H21 | Scheme | 2022-09-12 13:55 | FRA_4130120920221336.pdf | taylors1 | 4130120920221330 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | aupklb328yl7yr1cp5 | Low Risk closed | Risk Closed | 44831.7415 | Obs8 | Measures To Limit Fire Spread And Development | 45547 | Low | Court Manager | Adjust closer to laundry door to close tight to frame | Contacted R & D
4131 | Woodridge Gardens | WOODRIDGEGARD_S001 | H21 | Scheme | 2022-06-10 12:59 | FRA_4131100620221243.pdf | taylors1 | 4131100620221240 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | a9pevsysd9tl48dr2nf | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45453 | Low | Court Manager | Fit intumescent panel to server cupboard door for ventilation 300mmx300mm | NULL
4131 | Woodridge Gardens | WOODRIDGEGARD_S001 | H21 | Scheme | 2022-06-10 12:59 | FRA_4131100620221243.pdf | taylors1 | 4131100620221240 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | e72cn1cujicl48dr2pu | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45453 | Low | Court Manager | Additional fire escape directional sign to fit at end of corridor floor 1 adjacent to staircase flat 18 | NULL
4131 | Woodridge Gardens | WOODRIDGEGARD_S001 | H21 | Scheme | 2022-06-10 12:59 | FRA_4131100620221243.pdf | taylors1 | 4131100620221240 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | 7ui4cq7x11yl48dr2qi | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45453 | Low | Court Manager | Additional fire escape directional sign to fit at end of corridor adjacent to flat 8 | NULL
4131 | Woodridge Gardens | WOODRIDGEGARD_S001 | H21 | Scheme | 2022-06-10 12:59 | FRA_4131100620221243.pdf | taylors1 | 4131100620221240 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | 48g8f0r84n7l48dr2l7 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45453 | Low | Court Manager | 2f bin store fire thresh to move to allow door to close fully | NULL
4131 | Woodridge Gardens | WOODRIDGEGARD_S001 | H21 | Scheme | 2022-06-10 12:59 | FRA_4131100620221243.pdf | taylors1 | 4131100620221240 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | j6y6x9no5nl48dr2o8 | Low Risk to be actioned | Risk Open | NULL | Obs9 | Escape Lighting | 45453 | Low | Court Manager | AHM advised awaiting return of open view to repair some light fittings and fish key switches | NULL
4131 | Woodridge Gardens | WOODRIDGEGARD_S001 | H21 | Scheme | 2022-06-10 12:59 | FRA_4131100620221243.pdf | taylors1 | 4131100620221240 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | h1uhfnx16mll48dr2p6 | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45453 | Low | Court Manager | Additional fire escape directional sign to fit at end of corridor 2f | NULL
4131 | Woodridge Gardens | WOODRIDGEGARD_S001 | H21 | Scheme | 2022-06-10 12:59 | FRA_4131100620221243.pdf | taylors1 | 4131100620221240 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | yfoh63l36fl48dr2m4 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45453 | Low | Court Manager | Fit intumescent panel to server cupboard door for ventilation 300mmx300mm | NULL
4131 | Woodridge Gardens | WOODRIDGEGARD_S001 | H21 | Scheme | 2022-06-10 12:59 | FRA_4131100620221243.pdf | taylors1 | 4131100620221240 | Extra Care | Extra Care North | EC North 2 | North | North Patch 1 | wk165nlue7il48dr2mq | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45453 | Low | Court Manager | Adjust stop lath to closing leg of frame 2f staircase fire door opposite flat 36 | NULL
4132 | Dovecote Meadow | DOVECOTEMEAD_S001 | H21 | Scheme | 2022-07-14 14:11 | FRA_4132140720221349.pdf | whitek2 | 4132140720221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | y7nflg1vnphl5l12kt8 | Medium Risk closed | Risk Closed | 44761.5191 | Obs6 | Fire Hazards - Elimination & Control | 45121 | Medium | Court Manager | Remove paint extra from store cupboard adjacent to flat 127 next to cupboard S24 seventh floor phase 2 | Paint removed.
4132 | Dovecote Meadow | DOVECOTEMEAD_S001 | H21 | Scheme | 2022-07-14 14:11 | FRA_4132140720221349.pdf | whitek2 | 4132140720221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | xiciyos4jzll5l1j1h3 | Medium Risk closed | Risk Closed | 44761.5188 | Obs8 | Measures To Limit Fire Spread And Development | 45121 | Medium | Court Manager | Flat 72 re-fix timber planted rebate with glue and screws | Repair carried out 18/07/22
4132 | Dovecote Meadow | DOVECOTEMEAD_S001 | H21 | Scheme | 2022-07-14 14:11 | FRA_4132140720221349.pdf | whitek2 | 4132140720221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | xhr12xnipasl5l12kyd | Medium Risk closed | Risk Closed | 44775.4403 | Obs7 | Fire Protection Measures | 45121 | Medium | Court Manager | Corridor fire door phase 1 adjacent to flat 72 needs adjustment to close | Repair carried out by R&D
4132 | Dovecote Meadow | DOVECOTEMEAD_S001 | H21 | Scheme | 2022-07-14 14:11 | FRA_4132140720221349.pdf | whitek2 | 4132140720221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | z53tev5el8cl5l12l25 | Medium Risk closed | Risk Closed | 44791.3769 | Obs8 | Measures To Limit Fire Spread And Development | 45121 | Medium | Court Manager | Flat 122 bottom of door needs easing catching on carpet | Job complete
4132 | Dovecote Meadow | DOVECOTEMEAD_S001 | H21 | Scheme | 2022-07-14 14:11 | FRA_4132140720221349.pdf | whitek2 | 4132140720221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | fsmvqjujdjfl5l12kuj | Medium Risk closed | Risk Closed | 44791.3778 | Obs7 | Fire Protection Measures | 45121 | Medium | Court Manager | Bathing suit level 1 phase 3 door not closing adjust door keep | Job compete
4132 | Dovecote Meadow | DOVECOTEMEAD_S001 | H21 | Scheme | 2022-07-14 14:11 | FRA_4132140720221349.pdf | whitek2 | 4132140720221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | kmsuo0infkl5l12l0k | Medium Risk closed | Risk Closed | 44791.3762 | Obs8 | Measures To Limit Fire Spread And Development | 45121 | Medium | Court Manager | Flat 162 pack bottom hindge to close gap on opening edge | Job compete
4132 | Dovecote Meadow | DOVECOTEMEAD_S001 | H21 | Scheme | 2022-07-14 14:11 | FRA_4132140720221349.pdf | whitek2 | 4132140720221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | r1njommsqqll5l12ktr | Low Risk closed | Risk Closed | 44761.5196 | Obs6 | Fire Hazards - Elimination & Control | 45487 | Low | Court Manager | Recommend signs are put up on flat doors of residents receiving oxygen | Signs on the 3 apartments with oxygen.
4132 | Dovecote Meadow | DOVECOTEMEAD_S001 | H21 | Scheme | 2022-07-14 14:11 | FRA_4132140720221349.pdf | whitek2 | 4132140720221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | t4vyaakrphql5l12kv6 | Medium Risk closed | Risk Closed | 44791.3783 | Obs7 | Fire Protection Measures | 45121 | Medium | Court Manager | Phase 3 level 1 door to lounge requires slight adjustment catching on lead edge | Job complete
4132 | Dovecote Meadow | DOVECOTEMEAD_S001 | H21 | Scheme | 2022-07-14 14:11 | FRA_4132140720221349.pdf | whitek2 | 4132140720221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | qa1ok8frbcml5l12l19 | Medium Risk closed | Risk Closed | 44775.4406 | Obs8 | Measures To Limit Fire Spread And Development | 45121 | Medium | Court Manager | Flat 70 pack bottom hinge to reduce the gap | Repair carried out by R&D
4132 | Dovecote Meadow | DOVECOTEMEAD_S001 | H21 | Scheme | 2022-07-14 14:11 | FRA_4132140720221349.pdf | whitek2 | 4132140720221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | q4un7i1fk6al5l12kzr | Medium Risk closed | Risk Closed | 44761.5203 | Obs7 | Fire Protection Measures | 45121 | Medium | Court Manager | Flat 72 door rebate requires re-fix with glue and screws | Repaired 18/07/22
4132 | Dovecote Meadow | DOVECOTEMEAD_S001 | H21 | Scheme | 2022-07-14 14:11 | FRA_4132140720221349.pdf | whitek2 | 4132140720221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | ocbmj6vgd5l5l1lk7o | Low Risk closed | Risk Closed | 44791.3785 | Obs10 | Fire Safety And Notices | 45487 | Low | Court Manager | Very few directional signs directing to fire escapes this needs to be investigated further. Recommed joint visit with Fire Authority in view of phased evacuation policy | Job complete
4132 | Dovecote Meadow | DOVECOTEMEAD_S001 | H21 | Scheme | 2022-07-14 14:11 | FRA_4132140720221349.pdf | whitek2 | 4132140720221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | 0mv1ekm9x86l5l12kwn | Low Risk closed | Risk Closed | 44791.3781 | Obs7 | Fire Protection Measures | 45487 | Low | Court Manager | Refuse store 8 near flat 88 check fire sealing around pipe pass through ceiling/floor | Job complete
4132 | Dovecote Meadow | DOVECOTEMEAD_S001 | H21 | Scheme | 2022-07-14 14:11 | FRA_4132140720221349.pdf | whitek2 | 4132140720221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | 1doqnmlyh37l5l12kxn | Medium Risk closed | Risk Closed | 44775.4429 | Obs7 | Fire Protection Measures | 45121 | Medium | Court Manager | Phase 1 adjacent to flat 71 corridor fire door catching on bottom edge require adjustment | Repair carried out by R&D
4132 | Dovecote Meadow | DOVECOTEMEAD_S001 | H21 | Scheme | 2022-07-14 14:11 | FRA_4132140720221349.pdf | whitek2 | 4132140720221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | a9q66792igql5l12kz1 | Medium Risk closed | Risk Closed | 44775.4409 | Obs7 | Fire Protection Measures | 45121 | Medium | Court Manager | Corridor fire door phase1 adjacent to flat 20 not closing sticking on bottom edge require slight adjustment | Repaired by R&D
4132 | Dovecote Meadow | DOVECOTEMEAD_S001 | H21 | Scheme | 2022-07-14 14:11 | FRA_4132140720221349.pdf | whitek2 | 4132140720221340 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | 8btiwobxszyl5l12kvy | Low Risk closed | Risk Closed | 44791.3772 | Obs7 | Fire Protection Measures | 45487 | Low | Court Manager | Level 0 phase adjacent to store 1 and 2 fire sealing In ceiling to complete | Job complete
4133 | Springtide Cove | SPRINGTIDECOVE_S001 | H21 | Scheme | 2022-08-02 16:30 | FRA_4133020820221628.pdf | whitek2 | 4133020820221620 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | 861xh136bgl6cc4y4u | Low Risk closed | Risk Closed | 44784.5246 | Obs8 | Measures To Limit Fire Spread And Development | 45506 | Low | Court Manager | Corridor fire door near lift opposite flat 22 requires repairing bottom closing edge | Job completed 11.8.22
4133 | Springtide Cove | SPRINGTIDECOVE_S001 | H21 | Scheme | 2022-08-02 16:30 | FRA_4133020820221628.pdf | whitek2 | 4133020820221620 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | dyxw130afe4l6cc4y6e | Low Risk closed | Risk Closed | 44805.3602 | Obs8 | Measures To Limit Fire Spread And Development | 45506 | Low | Court Manager | Cupboard in activity room requires side door shoot bolts to operate to secure doors into rebate when locked | Works order raised work completed
4133 | Springtide Cove | SPRINGTIDECOVE_S001 | H21 | Scheme | 2022-08-02 16:30 | FRA_4133020820221628.pdf | whitek2 | 4133020820221620 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | c13b48es8vwl6cc4y5k | Medium Risk closed | Risk Closed | 44784.5243 | Obs8 | Measures To Limit Fire Spread And Development | 45140 | Medium | Court Manager | Activity Room door requires adjustment not latching into rebate Also door catching floor ease bottom of door | Raised repair job completed 11.8.22 for both doors
4133 | Springtide Cove | SPRINGTIDECOVE_S001 | H21 | Scheme | 2022-08-02 16:30 | FRA_4133020820221628.pdf | whitek2 | 4133020820221620 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | 73kyeq8z6ztl6cc4y91 | Medium Risk closed | Risk Closed | 44796.3303 | Obs8 | Measures To Limit Fire Spread And Development | 45140 | Medium | Court Manager | Flat 7 Door not closing when activated | Raised repair door completed 15/8/22
4133 | Springtide Cove | SPRINGTIDECOVE_S001 | H21 | Scheme | 2022-08-02 16:30 | FRA_4133020820221628.pdf | whitek2 | 4133020820221620 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | 6hc1s25wpphl6cc4y40 | Low Risk closed | Risk Closed | 44805.36 | Obs7 | Fire Protection Measures | 45506 | Low | Court Manager | Scooters needs to be stored in scooter room | Extract from scooter policy in residents newsletter posted to all residents today 1/9/22
4133 | Springtide Cove | SPRINGTIDECOVE_S001 | H21 | Scheme | 2022-08-02 16:30 | FRA_4133020820221628.pdf | whitek2 | 4133020820221620 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | ncsobmnqoil6cc4y77 | Medium Risk closed | Risk Closed | 44805.3595 | Obs8 | Measures To Limit Fire Spread And Development | 45140 | Medium | Court Manager | Flat 15 Door not closing when activated check closer | Works order raised work now complete
4133 | Springtide Cove | SPRINGTIDECOVE_S001 | H21 | Scheme | 2022-08-02 16:30 | FRA_4133020820221628.pdf | whitek2 | 4133020820221620 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | ngqoav02e7ll6cc4yai | Low Risk closed | Risk Closed | 44784.5239 | Obs10 | Fire Safety And Notices | 45506 | Low | Court Manager | Re-fix sign first floor next to lift | Sign has been put back on wall
4133 | Springtide Cove | SPRINGTIDECOVE_S001 | H21 | Scheme | 2022-08-02 16:30 | FRA_4133020820221628.pdf | whitek2 | 4133020820221620 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | im3bt0v54gkl6cc4y2t | Low Risk closed | Risk Closed | 44805.3591 | Obs7 | Fire Protection Measures | 45506 | Low | Court Manager | Scooters need to be kept in ground floor scooter room | Extract from scooter policy in residents newsletter post to all residents 1/9/22
4133 | Springtide Cove | SPRINGTIDECOVE_S001 | H21 | Scheme | 2022-08-02 16:30 | FRA_4133020820221628.pdf | whitek2 | 4133020820221620 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | xn2k6bzpmeml6cc4y21 | Low Risk closed | Risk Closed | 44805.3607 | Obs7 | Fire Protection Measures | 45506 | Low | Court Manager | Need to ensure scooters are stored and charged in the ground floor scooter store | Extract from newsletter scooter policy will be posted to all residents today 1/9/22
4133 | Springtide Cove | SPRINGTIDECOVE_S001 | H21 | Scheme | 2022-08-02 16:30 | FRA_4133020820221628.pdf | whitek2 | 4133020820221620 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | w5xrndp4e8al6cc4y87 | Medium Risk closed | Risk Closed | 44805.358 | Obs8 | Measures To Limit Fire Spread And Development | 45140 | Medium | Court Manager | Flat 25 Door not closing when activated check closer | Repair raised work now ckmpleted
4134 | Gildacre Fields | GILDACREFIELDS_S001 | H21 | Scheme | 2022-02-22 14:01 | FRA_4134160220221133.pdf | whitek2 | 4134160220221130 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | jnfvc3ijymhkzpj9ln1 | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 44973 | Medium | Court Manager | Corridor fire door between flats 84 and 85 not closing | NULL
4134 | Gildacre Fields | GILDACREFIELDS_S001 | H21 | Scheme | 2022-02-22 14:01 | FRA_4134160220221133.pdf | whitek2 | 4134160220221130 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | qi8vn01orakzph7qkl | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 44973 | Medium | Court Manager | Stairwell door adjacent to flat 40 requires door adjusting to sit into rebate at bottom closing edge | NULL
4135 | Keelboat Lodge | KEELBOATLODGE_S001 | H21 | Scheme | 2022-07-26 13:51 | FRA_4135250720221447.pdf | whitek2 | 4135250720221440 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | qufpnhh9uel61zq6c8 | Low Risk closed | Risk Closed | 44902.5086 | Obs6 | Fire Hazards - Elimination & Control | 45499 | Low | Court Manager | Cleaners cupboard near flats 31 and 46 Ensure all electrical appliances including extension leads are PAT tested annually | Pat test on the 15/12/2022
4135 | Keelboat Lodge | KEELBOATLODGE_S001 | H21 | Scheme | 2022-07-26 13:51 | FRA_4135250720221447.pdf | whitek2 | 4135250720221440 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | ttlb91j8gdgl6204fpq | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45499 | Low | Court Manager | Cupboard opposite flat 7 requires tidying up and surplus items disposed of | NULL
4135 | Keelboat Lodge | KEELBOATLODGE_S001 | H21 | Scheme | 2022-07-26 13:51 | FRA_4135250720221447.pdf | whitek2 | 4135250720221440 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | ied17ojyejol6226d4z | Medium Risk closed | Risk Closed | 44902.5079 | Obs8 | Measures To Limit Fire Spread And Development | 45133 | Medium | Court Manager | Flat 6 Door frame requires re-fix and closer adjusting to close door into rebate | Repair put through and this was done by rnd
4135 | Keelboat Lodge | KEELBOATLODGE_S001 | H21 | Scheme | 2022-07-26 13:51 | FRA_4135250720221447.pdf | whitek2 | 4135250720221440 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | 0iw743bkbm5l6201q2f | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45133 | Medium | Court Manager | Plant room door require adjustment so as it closes into frame rebate | NULL
4135 | Keelboat Lodge | KEELBOATLODGE_S001 | H21 | Scheme | 2022-07-26 13:51 | FRA_4135250720221447.pdf | whitek2 | 4135250720221440 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | 3jstvinoue4l620hja2 | Observation Only | Risk Closed | 44902.502 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Refuse store cleaners cupboard opposite flat 18 would recommend that cleaning products are stored away from electrical switch boxes | Cleaners cleaner cupboard out storing everything right.
4135 | Keelboat Lodge | KEELBOATLODGE_S001 | H21 | Scheme | 2022-07-26 13:51 | FRA_4135250720221447.pdf | whitek2 | 4135250720221440 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | 2zx9oqjbpil61zcn4p | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45499 | Low | Court Manager | Refuse store opposite flat 67 cleaners store remove and dispose domestic items | NULL
4135 | Keelboat Lodge | KEELBOATLODGE_S001 | H21 | Scheme | 2022-07-26 13:51 | FRA_4135250720221447.pdf | whitek2 | 4135250720221440 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | 2mn1uwot8dl61z2p3s | Low Risk closed | Risk Closed | 44902.5024 | Obs6 | Fire Hazards - Elimination & Control | 45499 | Low | Court Manager | Tidy up cupboard opposite flat 52 dispose of unwanted items | All unwanted items disposed of correctly.
4135 | Keelboat Lodge | KEELBOATLODGE_S001 | H21 | Scheme | 2022-07-26 13:51 | FRA_4135250720221447.pdf | whitek2 | 4135250720221440 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | cggd1of041ql621oomc | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45133 | Medium | Court Manager | Bathing suit opposite flat 33 Door requires adjustment to latch into the reate | NULL
4135 | Keelboat Lodge | KEELBOATLODGE_S001 | H21 | Scheme | 2022-07-26 13:51 | FRA_4135250720221447.pdf | whitek2 | 4135250720221440 | Extra Care | Extra Care North | EC North 2 | North | North Patch 8 | wedr5hzrmjel620dneb | Observation Only | Risk Closed | 44902.5016 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Would recommend that residents scooter charges are PAT tested | Pat testing are getting done 15/11/2022
4138 | Cliffords Mews | CLIFFORDMEWS_S001 | H21 | Scheme | 2022-05-09 10:27 | FRA_4138060520221522.pdf | taylors1 | 4138060520221520 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | c3ziwzaq16nl2yi8n0o | Observation Only | Risk Open | NULL | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | AHM advised that a copy of this FRA to be placed within plastic wallet within fire box, copy of scheme fire and evac plan, summary of PCFRA with high risk flats highlighted and three laminated copies of fire zone plan | NULL
4138 | Cliffords Mews | CLIFFORDMEWS_S001 | H21 | Scheme | 2022-05-09 10:27 | FRA_4138060520221522.pdf | taylors1 | 4138060520221520 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | c45pd0m4j1l2yhydy4 | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45055 | Medium | Court Manager | 1 floor cross corridor door adjacent to flat 27/28 Adjust to close | NULL
4138 | Cliffords Mews | CLIFFORDMEWS_S001 | H21 | Scheme | 2022-05-09 10:27 | FRA_4138060520221522.pdf | taylors1 | 4138060520221520 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | f0hd7tu1wwcl2yhmqrn | Low Risk to be actioned | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | 45421 | Low | Court Manager | Provide a framed copy of the fire zone plan adjacent to second floor repeater panel | NULL
4138 | Cliffords Mews | CLIFFORDMEWS_S001 | H21 | Scheme | 2022-05-09 10:27 | FRA_4138060520221522.pdf | taylors1 | 4138060520221520 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | 6s1qqwby6jyl2yi0uly | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45055 | Medium | Court Manager | 1 floor cross corridor door opposite meeting room adjust to close | NULL
4138 | Cliffords Mews | CLIFFORDMEWS_S001 | H21 | Scheme | 2022-05-09 10:27 | FRA_4138060520221522.pdf | taylors1 | 4138060520221520 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | hcqp822c9qel2yhzsxs | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45421 | Low | Court Manager | Bin store 1 floor opposite flat 19 screws missing from bottom hinge | NULL
4138 | Cliffords Mews | CLIFFORDMEWS_S001 | H21 | Scheme | 2022-05-09 10:27 | FRA_4138060520221522.pdf | taylors1 | 4138060520221520 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | jr6td7apb0pl2yi246q | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45055 | Medium | Court Manager | 1 floor meeting room door ease to close | NULL
4138 | Cliffords Mews | CLIFFORDMEWS_S001 | H21 | Scheme | 2022-05-09 10:27 | FRA_4138060520221522.pdf | taylors1 | 4138060520221520 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | mxspvjgkbocl2yhbizk | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | Individual Peeps being completed as flats are let and updated onto fire plan | NULL
4138 | Cliffords Mews | CLIFFORDMEWS_S001 | H21 | Scheme | 2022-05-09 10:27 | FRA_4138060520221522.pdf | taylors1 | 4138060520221520 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | mvmt8n345efl2yi456d | Medium Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45055 | Medium | Court Manager | Fire action notices missing around building to final exit doors and break glass points and require meeting point writing on | NULL
4138 | Cliffords Mews | CLIFFORDMEWS_S001 | H21 | Scheme | 2022-05-09 10:27 | FRA_4138060520221522.pdf | taylors1 | 4138060520221520 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | mwbt6kui33bl2yi2vtc | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45421 | Low | Court Manager | Adjust catering kitchen store door to close | NULL
4138 | Cliffords Mews | CLIFFORDMEWS_S001 | H21 | Scheme | 2022-05-09 10:27 | FRA_4138060520221522.pdf | taylors1 | 4138060520221520 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | prod24s9z1bl2yhvmxs | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45055 | Medium | Court Manager | 2 floor staircase fire door opposite flat 62 ease and adjust to close | NULL
4138 | Cliffords Mews | CLIFFORDMEWS_S001 | H21 | Scheme | 2022-05-09 10:27 | FRA_4138060520221522.pdf | taylors1 | 4138060520221520 | Extra Care | Extra Care North | EC North 1 | North | North Patch 1 | ozbfi5vvgrsl2yhwrfj | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45055 | Medium | Court Manager | 1 floor staircase fire door opposite flat 38 hinge bound | NULL
4201 | Edyvean Walker Court | EDYVEANWALK_S001 | H21 | Scheme | 2022-05-05 11:50 | FRA_4201040520221533.pdf | AndersonV | 4201040520221530 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | hi0iqh9qlvl2srft1v | Medium Risk closed | Risk Closed | 44704.4939 | Obs6 | Fire Hazards - Elimination & Control | 44691 | Medium | Court Manager | Residents need to be reminded that communal areas need to be kept clear and sterile at all times to prevent the risk of fire spread | Sent letter to all resident on first floor, requesting they move items,
4201 | Edyvean Walker Court | EDYVEANWALK_S001 | H21 | Scheme | 2022-05-05 11:50 | FRA_4201040520221533.pdf | AndersonV | 4201040520221530 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | csqja7mm89l2srizgg | Low Risk closed | Risk Closed | 44704.4975 | Obs6 | Fire Hazards - Elimination & Control | 45056 | Low | Court Manager | Mat on stairway block 26-27 exit route requires removing. Exit routes need to be kept clear and free from trip hazards. | Removed mat
4201 | Edyvean Walker Court | EDYVEANWALK_S001 | H21 | Scheme | 2022-05-05 11:50 | FRA_4201040520221533.pdf | AndersonV | 4201040520221530 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | bis34c9zozrl2rp3wgh | Observation Only | Risk Closed | 44704.4962 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Court Manager | Only first floor flats require an FD30 fire door as the ground floor properties open into fresh air. | No action needed
4201 | Edyvean Walker Court | EDYVEANWALK_S001 | H21 | Scheme | 2022-05-05 11:50 | FRA_4201040520221533.pdf | AndersonV | 4201040520221530 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | vhlp5kt8pbrl2sr6szo | Medium Risk closed | Risk Closed | 44704.4971 | Obs6 | Fire Hazards - Elimination & Control | 45051 | Medium | Court Manager | Ashtray outside communal lounge requires removing. A designated smoking area needs to be located away from the communal walkways and suitable provision for extinguishing cigarettes needs to be provided. | Moved ashtray by door, will arrange to have outside area designated for smoking.
4202 | Philip Docker Court | PHILIPDOCK_S001 | H21 | Scheme | 2022-05-16 15:35 | FRA_4202150520221931.pdf | AndersonV | 4202150520221930 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | xh6g1f4jfx8l38h67ut | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45428 | Low | Court Manager | Ground floor lobby fire door by lift requires adjusting as not closing fully into the frame | NULL
4202 | Philip Docker Court | PHILIPDOCK_S001 | H21 | Scheme | 2022-05-16 15:35 | FRA_4202150520221931.pdf | AndersonV | 4202150520221930 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | y7v6sgusg1l38hjb7n | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45062 | Medium | Court Manager | 1st floor stairwell door outside flat 29, intumescent strip is loose | NULL
4202 | Philip Docker Court | PHILIPDOCK_S001 | H21 | Scheme | 2022-05-16 15:35 | FRA_4202150520221931.pdf | AndersonV | 4202150520221930 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | 9oos6elimhel38g95tm | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45064 | Low | Court Manager | Fire Assembly Point sign needs to be displayed | NULL
4202 | Philip Docker Court | PHILIPDOCK_S001 | H21 | Scheme | 2022-05-16 15:35 | FRA_4202150520221931.pdf | AndersonV | 4202150520221930 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | 5oj8hllihndl38h3qt3 | Medium Risk Overdue | Risk Open | NULL | Obs7 | Fire Protection Measures | 44699 | Medium | Court Manager | Ground floor Store room by lift lobby, fire stopping required at ceiling level | NULL
4202 | Philip Docker Court | PHILIPDOCK_S001 | H21 | Scheme | 2022-05-16 15:35 | FRA_4202150520221931.pdf | AndersonV | 4202150520221930 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | 5q1ctmno7uql38hh7c2 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45428 | Low | Court Manager | Ground floor stairwell door by bin store, magnetic hold back not working | NULL
4202 | Philip Docker Court | PHILIPDOCK_S001 | H21 | Scheme | 2022-05-16 15:35 | FRA_4202150520221931.pdf | AndersonV | 4202150520221930 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | qeys91b6sxl38hzphy | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45062 | Medium | Court Manager | Electrical intake room needs to be kept locked at all times | NULL
4203 | Farmers Court | FARMERS_S001 | H21 | Scheme | 2022-02-10 14:10 | FRA_4203090220221317.pdf | AndersonV | 4203090220221310 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | h1jng356m95kzgvddm0 | Medium Risk closed | Risk Closed | 44782.5612 | Obs6 | Fire Hazards - Elimination & Control | 44604 | Medium | Court Manager | Smoking area requires providing with a suitable ashtray to extinguish cigarettes, and placed away from the building. A metal bucket full of sand would suffice. | Bucket of sand now in situ
4203 | Farmers Court | FARMERS_S001 | H21 | Scheme | 2022-02-10 14:10 | FRA_4203090220221317.pdf | AndersonV | 4203090220221310 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | mf1v2nlts29kzfldzzs | Low Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 44969 | Low | Court Manager | In the event of a total building evacuation or mass relocation of residents in inclement weather for the wellbeing of the residents and it is safe to do so, staff will endeavour to establish a refuge point or the use of the residents who are accompanied by staff in the ground floor lounge area, which is close to a final exit door and has at least 2 sets of fire doors between the lounge and the location of the fire. The external assembly point, to be used as a last resort, in the car park and needs to be marked clearly with the correct signage. | NULL
4203 | Farmers Court | FARMERS_S001 | H21 | Scheme | 2022-02-10 14:10 | FRA_4203090220221317.pdf | AndersonV | 4203090220221310 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | 4qtyb9vyw2okzh0zatb | Low Risk closed | Risk Closed | 44782.5641 | Obs10 | Fire Safety And Notices | 44969 | Low | Court Manager | Fire Assembly Point sign needs to be displayed | Fire assembly point provided by wood and wood signs. This was supplied and fitted within a week of the issue being rsised
4203 | Farmers Court | FARMERS_S001 | H21 | Scheme | 2022-02-10 14:10 | FRA_4203090220221317.pdf | AndersonV | 4203090220221310 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | 9wict1fwzynkzguu6tg | Medium Risk closed | Risk Closed | 44782.5629 | Obs6 | Fire Hazards - Elimination & Control | 44967 | Medium | Court Manager | External store requires clearing of combustible materials, due to risk of arson. | External bike store cleared of all materials. This is now checked as part of the weekly compliance health and safety wzlkaround
4203 | Farmers Court | FARMERS_S001 | H21 | Scheme | 2022-02-10 14:10 | FRA_4203090220221317.pdf | AndersonV | 4203090220221310 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | yjaj513uxrpkzgv211n | Medium Risk closed | Risk Closed | 44782.5619 | Obs7 | Fire Protection Measures | 44604 | Medium | Court Manager | Automatic fire door closers to communal dining area not working x2 | These were repaired immediately after the issue was raised
4203 | Farmers Court | FARMERS_S001 | H21 | Scheme | 2022-02-10 14:10 | FRA_4203090220221317.pdf | AndersonV | 4203090220221310 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | wy4s2830xukzh0ga3a | Medium Risk to be actioned | Risk Open | NULL | Obs3 | Details Of Fire Loss | 44967 | Medium | Court Manager | Additional detection required in flat 12, to cover bedrooms and lounge areas. | NULL
4204 | Arthur Russell Court | ARTHURRUSS_S001 | H21 | Scheme | 2022-01-05 12:46 | FRA_4204050120220829.pdf | AndersonV | 4204050120220820 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | vwa2m5gfrksky1fb9za | Medium Risk Overdue | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44569 | Medium | Court Manager | Flats 24,25,28,29, 39 have excessive gaps at the bottom of the front door, requires drop down seal fitting | NULL
4204 | Arthur Russell Court | ARTHURRUSS_S001 | H21 | Scheme | 2022-01-05 12:46 | FRA_4204050120220829.pdf | AndersonV | 4204050120220820 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | v42i8famm8nky1e1urv | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 44931 | Medium | Court Manager | Electrical intake room should be kept locked at all times. With Correct signage to be displayed on the door. "Fire dooir keep locked" | NULL
4204 | Arthur Russell Court | ARTHURRUSS_S001 | H21 | Scheme | 2022-01-05 12:46 | FRA_4204050120220829.pdf | AndersonV | 4204050120220820 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | bmromjvoz4ky1elc2p | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44931 | Medium | Court Manager | Flat 9 front door requires adjusting and repairing on bottom edge | NULL
4204 | Arthur Russell Court | ARTHURRUSS_S001 | H21 | Scheme | 2022-01-05 12:46 | FRA_4204050120220829.pdf | AndersonV | 4204050120220820 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | cwmyjm9y88nky1iuqvb | Observation Only | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | External fire loading from recycling storage units are located in close proximity to the building and accessible for ignition and arson by others. Housing Management have raised this with the Fire Officer and they have advised that the risk is very low. This should be reviewed on an annual basis, or if circumstances change. | NULL
4204 | Arthur Russell Court | ARTHURRUSS_S001 | H21 | Scheme | 2022-01-05 12:46 | FRA_4204050120220829.pdf | AndersonV | 4204050120220820 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | 4dtys5t99omky1dxlnk | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44931 | Medium | Court Manager | Electrical intake room requires clearing of combustible materials. | NULL
4204 | Arthur Russell Court | ARTHURRUSS_S001 | H21 | Scheme | 2022-01-05 12:46 | FRA_4204050120220829.pdf | AndersonV | 4204050120220820 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | 7me1jk4aarwky1epvk7 | Medium Risk Overdue | Risk Open | NULL | Obs10 | Fire Safety And Notices | 44569 | Medium | Court Manager | Assembly point signage requires fitting | NULL
4204 | Arthur Russell Court | ARTHURRUSS_S001 | H21 | Scheme | 2022-01-05 12:46 | FRA_4204050120220829.pdf | AndersonV | 4204050120220820 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | 305t5lca374ky1e4srk | Medium Risk Overdue | Risk Open | NULL | Obs10 | Fire Safety And Notices | 44569 | Medium | Court Manager | Inconsistent fire action notices being displayed in various locations | NULL
4204 | Arthur Russell Court | ARTHURRUSS_S001 | H21 | Scheme | 2022-01-05 12:46 | FRA_4204050120220829.pdf | AndersonV | 4204050120220820 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | lltyj8swf2nky1ew18f | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44931 | Medium | Court Manager | Flat 1 front door is obstructed by the hall carpet | NULL
4204 | Arthur Russell Court | ARTHURRUSS_S001 | H21 | Scheme | 2022-01-05 12:46 | FRA_4204050120220829.pdf | AndersonV | 4204050120220820 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | k4589vyyy1ky1ep2jk | Medium Risk Overdue | Risk Open | NULL | Obs10 | Fire Safety And Notices | 44569 | Medium | Court Manager | Fire Action notices require completing with the correct information regarding the assembly point | NULL
4204 | Arthur Russell Court | ARTHURRUSS_S001 | H21 | Scheme | 2022-01-05 12:46 | FRA_4204050120220829.pdf | AndersonV | 4204050120220820 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | l1gh9cwzvzqky1eg0wp | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 44931 | Medium | Court Manager | Fire door adjacent to flat 5 requires adjusting | NULL
4204 | Arthur Russell Court | ARTHURRUSS_S001 | H21 | Scheme | 2022-01-05 12:46 | FRA_4204050120220829.pdf | AndersonV | 4204050120220820 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | h70yf55snwoky1fkdxc | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 44931 | Medium | Court Manager | Laundry room door not closing fully into the frame | NULL
4204 | Arthur Russell Court | ARTHURRUSS_S001 | H21 | Scheme | 2022-01-05 12:46 | FRA_4204050120220829.pdf | AndersonV | 4204050120220820 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | gt4s0x479iuky1ipbp0 | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 44934 | Low | Court Manager | Several of the Final exit doors are fitted with a thumb turn, instead of a push pad/ bar. Instead of replacing the doors or opening devices I would suggest that a small sign is displayed on the doors advising how to safely exit the door. | NULL
4206 | Charles Watson Court | CHARLESWATS_S001 | H21 | Scheme | 2022-09-20 12:06 | FRA_4206200920220910.pdf | AndersonV | 4206200920220910 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | q25bnsrabwal89yjhga | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45555 | Low | Court Manager | Staircase fire door adjacent to flat 39 requires adjusting- closer operating at the wrong speed | NULL
4206 | Charles Watson Court | CHARLESWATS_S001 | H21 | Scheme | 2022-09-20 12:06 | FRA_4206200920220910.pdf | AndersonV | 4206200920220910 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | p4i6b43w8msl89y02fo | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45555 | Low | Court Manager | Fire door outside flat 12a not closing fully into the frame | NULL
4209 | Rohan Gardens | ROHANGARD_S001 | H21 | Scheme | 2022-11-24 13:00 | FRA_4209241120221228.pdf | AndersonV | 4209241120221220 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | tznerziy4clav1wk5s | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45620 | Low | Court Manager | Residents need to reminded that escape routes should be kept clear and sterile at all times a d free from trip hazards | NULL
4209 | Rohan Gardens | ROHANGARD_S001 | H21 | Scheme | 2022-11-24 13:00 | FRA_4209241120221228.pdf | AndersonV | 4209241120221220 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | s8z6lsqkaclav1wk6c | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45620 | Low | Court Manager | Swing free closer not working in ground floor refuse room | NULL
4209 | Rohan Gardens | ROHANGARD_S001 | H21 | Scheme | 2022-11-24 13:00 | FRA_4209241120221228.pdf | AndersonV | 4209241120221220 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | g08kjlkoxhvlav1wk7x | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45254 | Medium | Court Manager | Cable bunches not adequately fire stopped in refuse store room 2nd floor - recent work carried out by Sky TV | NULL
4209 | Rohan Gardens | ROHANGARD_S001 | H21 | Scheme | 2022-11-24 13:00 | FRA_4209241120221228.pdf | AndersonV | 4209241120221220 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | iui39v7hnulav1wkb4 | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45254 | Medium | Court Manager | Renuvo need to come and remove their rubbish from the plant room | NULL
4209 | Rohan Gardens | ROHANGARD_S001 | H21 | Scheme | 2022-11-24 13:00 | FRA_4209241120221228.pdf | AndersonV | 4209241120221220 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | 1w0t2uvk1kalav1wk9n | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45254 | Medium | Court Manager | 1st Floor comms cupboard in refuse room lobby requires clearing of combustible materials | NULL
4209 | Rohan Gardens | ROHANGARD_S001 | H21 | Scheme | 2022-11-24 13:00 | FRA_4209241120221228.pdf | AndersonV | 4209241120221220 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | 49bt7bf2m23lav1wkc3 | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45259 | Low | Court Manager | Incorrect Fire Action Notices being displayed - various locations. Staff room, refuse room, commercial kitchen. | NULL
4209 | Rohan Gardens | ROHANGARD_S001 | H21 | Scheme | 2022-11-24 13:00 | FRA_4209241120221228.pdf | AndersonV | 4209241120221220 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | cjnehdu3swlav1wk78 | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45254 | Medium | Court Manager | 2nd floor intake room in refuse store lobby - breaches in Fire stopping between conduit and roof void carried out by Sky TV | NULL
4209 | Rohan Gardens | ROHANGARD_S001 | H21 | Scheme | 2022-11-24 13:00 | FRA_4209241120221228.pdf | AndersonV | 4209241120221220 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | c6urs3py0qqlav1wk94 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45620 | Low | Court Manager | Flat 35 has new door fitted - Excessive gap to locking jamb. Door is due to be replaced next week. Note only as this door was recently replaced when void and is not compliant | NULL
4209 | Rohan Gardens | ROHANGARD_S001 | H21 | Scheme | 2022-11-24 13:00 | FRA_4209241120221228.pdf | AndersonV | 4209241120221220 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | e86iq3xcxmlav1wk8g | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45254 | Medium | Court Manager | Flat 28 penetrations to wall above door made by communications cable requires making good - recent works by Sky TV | NULL
4209 | Rohan Gardens | ROHANGARD_S001 | H21 | Scheme | 2022-11-24 13:00 | FRA_4209241120221228.pdf | AndersonV | 4209241120221220 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | 9kddhfqj0xglav1wkab | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45620 | Low | Court Manager | Unable to inspect store room in 1st floor refuse room. Lock is jammed | NULL
4209 | Rohan Gardens | ROHANGARD_S001 | H21 | Scheme | 2022-11-24 13:00 | FRA_4209241120221228.pdf | AndersonV | 4209241120221220 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | 81mt9q1z197lav1wk45 | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45620 | Low | Court Manager | Evidence that some scooter batteries have been PAT tested but not all units are displaying test tabs. These need to be included on the next PAT testing | NULL
4209 | Rohan Gardens | ROHANGARD_S001 | H21 | Scheme | 2022-11-24 13:00 | FRA_4209241120221228.pdf | AndersonV | 4209241120221220 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | xhquyfpe3glav1wk50 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45259 | Low | Court Manager | Back box to swing free closer is damaged 1st floor refuse room | NULL
4210 | Webb Ellis Court | WEBBELLIS_S001 | H21 | Scheme | 2022-10-17 16:51 | FRA_4210171020220911.pdf | AndersonV | 4210171020220910 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | yjiltf2the9l9ckz03x | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45216 | Medium | Court Manager | Fire door within store room needs to be kept locked at all times | NULL
4210 | Webb Ellis Court | WEBBELLIS_S001 | H21 | Scheme | 2022-10-17 16:51 | FRA_4210171020220911.pdf | AndersonV | 4210171020220910 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | w5n0fi3xygdl9cmayue | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45582 | Low | Court Manager | The plant room need cleared of unwanted goods and not used as a storage area | NULL
4210 | Webb Ellis Court | WEBBELLIS_S001 | H21 | Scheme | 2022-10-17 16:51 | FRA_4210171020220911.pdf | AndersonV | 4210171020220910 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | 8irvlt8o0yul9cxr79z | Low Risk to be actioned | Risk Open | NULL | Obs16 | Testing And Maintenance | 45582 | Low | M&E Team | Issues have been identified with multiple emergency lighting failures at Webb Ellis Court. Ed Hayward new M&E Contracts manager to investigate and resolve | NULL
4210 | Webb Ellis Court | WEBBELLIS_S001 | H21 | Scheme | 2022-10-17 16:51 | FRA_4210171020220911.pdf | AndersonV | 4210171020220910 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | a7bs1q5jaqdl9cm44cn | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45582 | Low | Court Manager | Incorrect Fire Action Notice is being displayed by the exit adjacent to the Care office | NULL
4210 | Webb Ellis Court | WEBBELLIS_S001 | H21 | Scheme | 2022-10-17 16:51 | FRA_4210171020220911.pdf | AndersonV | 4210171020220910 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | e43x8q68xmhl9cyd42t | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45219 | Low | Court Manager | No evidence that Mobility scooters are being PAT tested in the scooter store. These need to be included in the next routine PAT testing program. | NULL
4210 | Webb Ellis Court | WEBBELLIS_S001 | H21 | Scheme | 2022-10-17 16:51 | FRA_4210171020220911.pdf | AndersonV | 4210171020220910 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | 704v3n0brcfl9cybkgx | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45582 | Low | Court Manager | Riser cupboard door doors need to be kept locked, several tgat were checked were found to be open | NULL
4210 | Webb Ellis Court | WEBBELLIS_S001 | H21 | Scheme | 2022-10-17 16:51 | FRA_4210171020220911.pdf | AndersonV | 4210171020220910 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | 0fmsv5ryt27ll9cmfy26 | Medium Risk Overdue | Risk Open | NULL | Obs7 | Fire Protection Measures | 44854 | Medium | Court Manager | Commercial kitchen entrance door not closing fully into the frame | NULL
4210 | Webb Ellis Court | WEBBELLIS_S001 | H21 | Scheme | 2022-10-17 16:51 | FRA_4210171020220911.pdf | AndersonV | 4210171020220910 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | 0wlhhx0yzwvgl9cmhbaj | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45216 | Medium | Court Manager | Exit route in commercial kitchen needs to be kept clear and sterile at all times | NULL
4210 | Webb Ellis Court | WEBBELLIS_S001 | H21 | Scheme | 2022-10-17 16:51 | FRA_4210171020220911.pdf | AndersonV | 4210171020220910 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | lhw6dyx0itdl9cjz3ty | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45216 | Medium | Court Manager | Flats 9, 27, 49 & 61 letter plate is missing requires replacing with new | NULL
4210 | Webb Ellis Court | WEBBELLIS_S001 | H21 | Scheme | 2022-10-17 16:51 | FRA_4210171020220911.pdf | AndersonV | 4210171020220910 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | s4t0vlx5jmol9ck0tzi | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45582 | Low | Court Manager | Residents need to be reminded that communal areas need to be kept clear and sterile at all times. Communal exit routes should be free from trip hazards | NULL
4210 | Webb Ellis Court | WEBBELLIS_S001 | H21 | Scheme | 2022-10-17 16:51 | FRA_4210171020220911.pdf | AndersonV | 4210171020220910 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | p3hulrzxyahl9cwp0il | Medium Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45216 | Medium | Court Manager | One member of Care staff have to complete Fire Safety e-learning training. 2 staff members that have now left H21 need removing from the system. | NULL
4211 | Oakwood Gardens | MAYFIELDBUN_S001 | H21 | Scheme | 2022-02-08 14:23 | FRA_4211070220222023.pdf | AndersonV | 4211070220222020 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | ototrdcsojfkzdxqlm1 | Medium Risk Overdue | Risk Open | NULL | Obs7 | Fire Protection Measures | 44600 | Medium | Court Manager | Floor 1 bin store. Riser cupboard door not closed or locked, the locking mechanism has been removed from the door. | NULL
4211 | Oakwood Gardens | MAYFIELDBUN_S001 | H21 | Scheme | 2022-02-08 14:23 | FRA_4211070220222023.pdf | AndersonV | 4211070220222020 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | t1xwo81vghkze67fv5 | Medium Risk closed | Risk Closed | 44758.3971 | Obs8 | Measures To Limit Fire Spread And Development | 44600 | Medium | Court Manager | Flat 17 front door is damaged | Have been provided with a quote for 1200 pounds for replacement. Quote has been forwarded to management , awaiting start date
4211 | Oakwood Gardens | MAYFIELDBUN_S001 | H21 | Scheme | 2022-02-08 14:23 | FRA_4211070220222023.pdf | AndersonV | 4211070220222020 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | jh2vnda7n9fkze607c5 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45330 | Low | Court Manager | Recommend doguards are fitted to commercial kitchen door and 1st floor inner refuse room door. | NULL
4211 | Oakwood Gardens | MAYFIELDBUN_S001 | H21 | Scheme | 2022-02-08 14:23 | FRA_4211070220222023.pdf | AndersonV | 4211070220222020 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | ii763rn5aijkze5xw0j | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44965 | Medium | Court Manager | Various flat front doors as per survey list require repairs/ adjusting so they close fully into the frame on activation of the fire alarm. | NULL
4211 | Oakwood Gardens | MAYFIELDBUN_S001 | H21 | Scheme | 2022-02-08 14:23 | FRA_4211070220222023.pdf | AndersonV | 4211070220222020 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | gkguqtc3xh4kzdzc6f3 | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 44965 | Low | Court Manager | Inconsistent fire action notices being displayed in the bin store, these require changing to the standard EC signs | NULL
4211 | Oakwood Gardens | MAYFIELDBUN_S001 | H21 | Scheme | 2022-02-08 14:23 | FRA_4211070220222023.pdf | AndersonV | 4211070220222020 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | 356ie5a3et5kze6y8bk | Low Risk to be actioned | Risk Open | NULL | Obs14 | Access By Emergency Services | 45330 | Low | Court Manager | In the event of total evacuation or mass relocation, in inclement weather and it is safe to do so, staff will endeavour to establish an assembly point for the use of residents who are accompanied by staff, in one of the ground floor lounge areas, close to a final exit and has at least 2 sets of fire doors between the lounge and the location of the fire. | NULL
4211 | Oakwood Gardens | MAYFIELDBUN_S001 | H21 | Scheme | 2022-02-08 14:23 | FRA_4211070220222023.pdf | AndersonV | 4211070220222020 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | 6ys5zyexk2ekze63t5i | Medium Risk closed | Risk Closed | 44758.3979 | Obs8 | Measures To Limit Fire Spread And Development | 44600 | Medium | Court Manager | Following a serious fire at another Extra Care court. It is required that any flat entrance doors that have automatic opening devices fitted, are checked to ensure that they fail safe in case of an emergency. | Checks have taken place and all devices operate correctly during fire alarm tests
4211 | Oakwood Gardens | MAYFIELDBUN_S001 | H21 | Scheme | 2022-02-08 14:23 | FRA_4211070220222023.pdf | AndersonV | 4211070220222020 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | 6giuid2hxb5kze6qjnz | Medium Risk closed | Risk Closed | 44758.3959 | Obs15 | Management Of Fire Safety | 44965 | Medium | Court Manager | A log must now be kept by the Court Manager of any contractors who access the roof void(s). It is important to manage this, due to fire stopping and compartmentation being compromised in the past, which has now been rectified. | Folder has now been set up in office for this type of work
4211 | Oakwood Gardens | MAYFIELDBUN_S001 | H21 | Scheme | 2022-02-08 14:23 | FRA_4211070220222023.pdf | AndersonV | 4211070220222020 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | er0vxoot2tpkzdxp26a | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 44965 | Medium | Court Manager | Floor 1 inner bin store door not closing fully into the frame, keep is also damaged. Door to be kept shut at all times and not wedged open, or fitted with a swing free closer or dorguard. | NULL
4211 | Oakwood Gardens | MAYFIELDBUN_S001 | H21 | Scheme | 2022-02-08 14:23 | FRA_4211070220222023.pdf | AndersonV | 4211070220222020 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | f626xh5y1llkzdxm0qi | Medium Risk closed | Risk Closed | 44758.3983 | Obs7 | Fire Protection Measures | 44965 | Medium | Court Manager | Floor 2 inner bin store door not closing fully into the frame | Quote read for works, awaiting start date
4211 | Oakwood Gardens | MAYFIELDBUN_S001 | H21 | Scheme | 2022-02-08 14:23 | FRA_4211070220222023.pdf | AndersonV | 4211070220222020 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | yh9l6ladeykzdy9jer | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45330 | Low | Court Manager | 1st Floor comms room outside flat 48 door requires locking and pull handle refixing | NULL
4211 | Oakwood Gardens | MAYFIELDBUN_S001 | H21 | Scheme | 2022-02-08 14:23 | FRA_4211070220222023.pdf | AndersonV | 4211070220222020 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | wpk5opgiivgkzdz47i4 | Medium Risk closed | Risk Closed | 44758.3936 | Obs8 | Measures To Limit Fire Spread And Development | 44965 | Medium | Court Manager | Flat 5 front door is damaged and requires replacing | The quote form the door has been given to the family of the client
4213 | Laurel Gardens | LAURELGARD_S001 | H21 | Scheme | 2021-12-07 14:46 | FRA_4213071220211419.pdf | AndersonV | 4213071220211410 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | tzhe710ulapkww7okxs | Medium Risk closed | Risk Closed | 44566.5633 | Obs8 | Measures To Limit Fire Spread And Development | 44902 | Medium | Court Manager | Flats 13, 40, require front doors adjusting due to excessive gaps | Doors adjusted as needed
4213 | Laurel Gardens | LAURELGARD_S001 | H21 | Scheme | 2021-12-07 14:46 | FRA_4213071220211419.pdf | AndersonV | 4213071220211410 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | s37qtk5shqhkww7puh2 | Medium Risk closed | Risk Closed | 44547.5738 | Obs8 | Measures To Limit Fire Spread And Development | 44902 | Medium | Court Manager | Flats 31, 32 requires front doors adjusting, not latching fully into the frames | Doors adjusted so now catches on latch as required
4215 | Lavender Meadows | LAVENDERMEAD_S001 | H21 | Scheme | 2022-10-13 12:56 | FRA_4215131020221120.pdf | AndersonV | 4215131020221120 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | s2zq4tl73xdl96wthfo | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45212 | Medium | Court Manager | Residents need to be reminded that scooters should not be stored in the communal corridors. Please refer to the H21 scooter policy for storage and charging of such items. | NULL
4215 | Lavender Meadows | LAVENDERMEAD_S001 | H21 | Scheme | 2022-10-13 12:56 | FRA_4215131020221120.pdf | AndersonV | 4215131020221120 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | rw57utdc8mnl96xwzr4 | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45578 | Low | Court Manager | No evidence that Mobility scooters are being PAT tested in the scooter store. | NULL
4215 | Lavender Meadows | LAVENDERMEAD_S001 | H21 | Scheme | 2022-10-13 12:56 | FRA_4215131020221120.pdf | AndersonV | 4215131020221120 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | tv67wbbu99l96xo93m | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45212 | Medium | Court Manager | Commercial kitchen entrance door from server is wedged open. This needs to be kept closed, or fitted with a suitable hold back device, door wedges are not acceptable | NULL
4215 | Lavender Meadows | LAVENDERMEAD_S001 | H21 | Scheme | 2022-10-13 12:56 | FRA_4215131020221120.pdf | AndersonV | 4215131020221120 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | ufrn8spa6yfl96xm8r8 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45578 | Low | Court Manager | Commercial kitchen side door, intumescent strips is loose | NULL
4215 | Lavender Meadows | LAVENDERMEAD_S001 | H21 | Scheme | 2022-10-13 12:56 | FRA_4215131020221120.pdf | AndersonV | 4215131020221120 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | ngs3u8cc2lkl96wthgv | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45213 | Low | Development | Excessive gaps to riser cupboard door outside flat 35&36 | NULL
4215 | Lavender Meadows | LAVENDERMEAD_S001 | H21 | Scheme | 2022-10-13 12:56 | FRA_4215131020221120.pdf | AndersonV | 4215131020221120 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | hlqsvhq2oo9l96wthg4 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45213 | Low | Development | Excessive gaps to riser cupboard door outside flat 38 | NULL
4215 | Lavender Meadows | LAVENDERMEAD_S001 | H21 | Scheme | 2022-10-13 12:56 | FRA_4215131020221120.pdf | AndersonV | 4215131020221120 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | erbjgijusbhl96x7lkf | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45212 | Medium | Court Manager | Residents need to be reminded that communal areas need to be kept clear and sterile at all times to prevent the risk of fire spread | NULL
4215 | Lavender Meadows | LAVENDERMEAD_S001 | H21 | Scheme | 2022-10-13 12:56 | FRA_4215131020221120.pdf | AndersonV | 4215131020221120 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | a1vdx467lgnl96wthf5 | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45212 | Medium | Court Manager | Staff room entrance foyer door. Lock has been removed, the door frame requires making good and the intumescent strips replacing | NULL
4215 | Lavender Meadows | LAVENDERMEAD_S001 | H21 | Scheme | 2022-10-13 12:56 | FRA_4215131020221120.pdf | AndersonV | 4215131020221120 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | 1q9lnhtokngl96zuvgd | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45212 | Medium | Development | Penetrations and voids in concrete ceiling and wall requires sealing | NULL
4215 | Lavender Meadows | LAVENDERMEAD_S001 | H21 | Scheme | 2022-10-13 12:56 | FRA_4215131020221120.pdf | AndersonV | 4215131020221120 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | 0tjzazmhcyvql96wthec | Medium Risk Overdue | Risk Open | NULL | Obs7 | Fire Protection Measures | 44848 | Medium | Court Manager | Several fire exits are obstructed by net curtains. These Require altering to allow easy egress from the building. | NULL
4215 | Lavender Meadows | LAVENDERMEAD_S001 | H21 | Scheme | 2022-10-13 12:56 | FRA_4215131020221120.pdf | AndersonV | 4215131020221120 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | y96uapmlf6rl96wthiu | Low Risk to be actioned | Risk Open | NULL | Obs11 | Fire Fighting Equipment | 45578 | Low | Court Manager | 2nd floor Comms room opposite lift - fire extinguisher requires refitting onto alternative wall, with correct labelling in place too | NULL
4215 | Lavender Meadows | LAVENDERMEAD_S001 | H21 | Scheme | 2022-10-13 12:56 | FRA_4215131020221120.pdf | AndersonV | 4215131020221120 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | vwktevo4fdl96xz1ib | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45212 | Medium | Court Manager | Communal stairwells and corridors should be kept clear and sterile at all times and not used as storage areas | NULL
4215 | Lavender Meadows | LAVENDERMEAD_S001 | H21 | Scheme | 2022-10-13 12:56 | FRA_4215131020221120.pdf | AndersonV | 4215131020221120 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 1 | z1ey9im2g2fl96wthhs | Medium Risk Overdue | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44848 | Medium | Court Manager | Flat 38 swing free closer is damaged | NULL
4301 | Grove Court | GROVEBIRM_S001 | H21 | Scheme | 2022-05-19 14:06 | FRA_4301190520221024.pdf | CrosdaleS | 4301190520221020 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 5 | zrd2pencbtl3cyvfca | Medium Risk closed | Risk Closed | 44760.7188 | Obs6 | Fire Hazards - Elimination & Control | 44729 | Medium | Court Manager | There are 3 extension leads used. Recommended to wall mount hard wired sockets | Sockets fitted to the wall to remove all labelling beneath the desk
4301 | Grove Court | GROVEBIRM_S001 | H21 | Scheme | 2022-05-19 14:06 | FRA_4301190520221024.pdf | CrosdaleS | 4301190520221020 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 5 | 40k8x3kygoml3cytdkl | Observation Only | Risk Closed | 44701.5013 | Obs5 | Evacuation Strategy And Training | NULL | N/A | Court Manager | There are currently no high risk resident's | Continue to monitor and update when necessary
4301 | Grove Court | GROVEBIRM_S001 | H21 | Scheme | 2022-05-19 14:06 | FRA_4301190520221024.pdf | CrosdaleS | 4301190520221020 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 5 | des3kph6q3l3cz4d6f | Low Risk closed | Risk Closed | 44733.5035 | Obs9 | Escape Lighting | 45431 | Low | Court Manager | Persons using the guest bedroom will need to pass through the laundry room in the event of a fire. Supply and fit a Beacon LED Non-maintenance fixed polycarbonate Emergency Fixed Downlight 5w in the Laundry room. | New E/L fitted in laundry room
4301 | Grove Court | GROVEBIRM_S001 | H21 | Scheme | 2022-05-19 14:06 | FRA_4301190520221024.pdf | CrosdaleS | 4301190520221020 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 5 | q8pdsa3eqvjl3czaw0a | Low Risk closed | Risk Closed | 44722.4269 | Obs10 | Fire Safety And Notices | 45431 | Low | Court Manager | Persons using the guest bedroom will need to pass through the laundry room in the event of a fire. Supply and fit a photoluminescent Fire Exit sign above the Laundry room external door | Fire exit sign displayed
4302 | Guillemard Court | GUILLEMARD_S001 | H21 | Scheme | 2022-01-18 11:20 | FRA_4302180120220930.pdf | AndersonV | 4302180120220930 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 4 | 8dgolwbj9bfkyk078nu | Observation Only | Risk Open | NULL | Obs1 | The Building | NULL | N/A | Court Manager | There is no access to the roof voids from the communal areas | NULL
4302 | Guillemard Court | GUILLEMARD_S001 | H21 | Scheme | 2022-01-18 11:20 | FRA_4302180120220930.pdf | AndersonV | 4302180120220930 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 4 | uzl8b2h47qkyjxtg2p | Observation Only | Risk Open | NULL | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | False alarms due to cooking, no further action was required. | NULL
4304 | Westhall Court | WESTHALL_S001 | H21 | Scheme | 2022-02-14 14:04 | FRA_4304140220221026.pdf | AndersonV | 4304140220221020 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 8 | up7vkurm0ukzmlp9wc | Medium Risk to be actioned | Risk Open | NULL | Obs11 | Fire Fighting Equipment | 44971 | Medium | Court Manager | No fire blanket in commercial kitchen | NULL
4304 | Westhall Court | WESTHALL_S001 | H21 | Scheme | 2022-02-14 14:04 | FRA_4304140220221026.pdf | AndersonV | 4304140220221020 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 8 | xzumfy1qqjdkzmjxjxf | Low Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45336 | Low | Court Manager | Some Care staff to complete e-learning, 3 fire warden and 1 for fire safety awareness | NULL
4304 | Westhall Court | WESTHALL_S001 | H21 | Scheme | 2022-02-14 14:04 | FRA_4304140220221026.pdf | AndersonV | 4304140220221020 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 8 | 98eneqifwpwkzml128a | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 44971 | Medium | Court Manager | Accumulation of combustible materials should be avoided within the electrical intake rooms | NULL
4304 | Westhall Court | WESTHALL_S001 | H21 | Scheme | 2022-02-14 14:04 | FRA_4304140220221026.pdf | AndersonV | 4304140220221020 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 8 | a4j2umz5lj7kzmjxjy5 | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44971 | Medium | Court Manager | Ground floor store room requires clearing of combustible materials | NULL
4304 | Westhall Court | WESTHALL_S001 | H21 | Scheme | 2022-02-14 14:04 | FRA_4304140220221026.pdf | AndersonV | 4304140220221020 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 8 | czp80niq39ukzmjxy0k | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45336 | Low | Court Manager | Remove redundant fire action notices and replace with correct EC ones | NULL
4304 | Westhall Court | WESTHALL_S001 | H21 | Scheme | 2022-02-14 14:04 | FRA_4304140220221026.pdf | AndersonV | 4304140220221020 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 8 | 7ilhrj8syikzml65tb | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 44971 | Medium | Court Manager | Means of escape should be kept clear and sterile at all times | NULL
4304 | Westhall Court | WESTHALL_S001 | H21 | Scheme | 2022-02-14 14:04 | FRA_4304140220221026.pdf | AndersonV | 4304140220221020 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 8 | 0mos62896l5kzml8btg | Medium Risk to be actioned | Risk Open | NULL | Obs11 | Fire Fighting Equipment | 44971 | Medium | Court Manager | Extinguisher in commercial kitchen needs hanging and labelling in a suitable and accessible position | NULL
4304 | Westhall Court | WESTHALL_S001 | H21 | Scheme | 2022-02-14 14:04 | FRA_4304140220221026.pdf | AndersonV | 4304140220221020 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 8 | 05sbar0g2i8akzmjxjyz | Medium Risk to be actioned | Risk Open | NULL | Obs11 | Fire Fighting Equipment | 44971 | Medium | Court Manager | Plant room fire extinguisher requires refitting into correct position | NULL
4304 | Westhall Court | WESTHALL_S001 | H21 | Scheme | 2022-02-14 14:04 | FRA_4304140220221026.pdf | AndersonV | 4304140220221020 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 8 | 098utwdoumikzml3nkl | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45336 | Low | Court Manager | Hobbies room fire door and glazing panel are damaged, the door should also not be wedged open, recommend a swing free closer or dorguard is fitted to the door. | NULL
4304 | Westhall Court | WESTHALL_S001 | H21 | Scheme | 2022-02-14 14:04 | FRA_4304140220221026.pdf | AndersonV | 4304140220221020 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 8 | mfxri3bs4ckzmlb6oi | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 44971 | Medium | Court Manager | Commercial kitchen door requires adjusting to ensure it closes fully into the frame, accumulation of dirt under the brush bar is also restricting the flow action of the door. | NULL
4305 | Saxon Court | SAXON_S001 | H21 | Scheme | 2022-10-28 21:09 | FRA_4305281020221842.pdf | HallS | 4305281020221840 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 4 | k4idy1pjtdl9ss8k1j | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45227 | Medium | Court Manager | First floor guest room door set (door, frame & ironmongery) requires replacement by competent accredited fire door contractor as door damaged due to suspected forced entry. | NULL
4305 | Saxon Court | SAXON_S001 | H21 | Scheme | 2022-10-28 21:09 | FRA_4305281020221842.pdf | HallS | 4305281020221840 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 4 | jxfbk9kf6ol9ss8jzu | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45227 | Medium | Court Manager | Communal buggy store door requires replacement of intumescent strip & cold smoke seal to maintain intended fire integrity. | NULL
4305 | Saxon Court | SAXON_S001 | H21 | Scheme | 2022-10-28 21:09 | FRA_4305281020221842.pdf | HallS | 4305281020221840 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 4 | hrie215b1r9l9ssn8q2 | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45593 | Low | Court Manager | Recommendation for scheme managers to include all scooters onsite within the cyclical PAT test. The scheme managers are arranging for testing of scooters and will confirm when completed within the next few weeks. | NULL
4305 | Saxon Court | SAXON_S001 | H21 | Scheme | 2022-10-28 21:09 | FRA_4305281020221842.pdf | HallS | 4305281020221840 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 4 | i75wqcn45wl9sxaf71 | Low Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45593 | Low | Court Manager | Progressive privacy door does not have an emergency release button for emergencies such as power failures as raised by the fire service. Court Manager to contact service contractor and arrange installation. | NULL
4305 | Saxon Court | SAXON_S001 | H21 | Scheme | 2022-10-28 21:09 | FRA_4305281020221842.pdf | HallS | 4305281020221840 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 4 | pxduiu1gail9ss8k0s | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45227 | Medium | Court Manager | Communal scooter store door separating the communal escape route and scooter store opens automatically on activation of the fire alarm. The Assistant Housing Manager is to arrange for Openview to attend site and deactivate this communal buggy store door from opening on activation of the alarm. | NULL
4305 | Saxon Court | SAXON_S001 | H21 | Scheme | 2022-10-28 21:09 | FRA_4305281020221842.pdf | HallS | 4305281020221840 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 4 | 097r3s48as5bl9swp5zy | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45593 | Low | Court Manager | Unnecessary items belonging to residents within the communal corridors adjacent to their front doors at ground level. These could pose a tripping risk where they protrude from the recess. Court Manager advised to notify all resident regarding removal of offending items. | NULL
4305 | Saxon Court | SAXON_S001 | H21 | Scheme | 2022-10-28 21:09 | FRA_4305281020221842.pdf | HallS | 4305281020221840 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 4 | 0dh5kz5505gnl9ss8jys | Low Risk to be actioned | Risk Open | NULL | Obs1 | The Building | 45593 | Low | Surveyor | Fire stopping required around soil pipe that passes vertically through the floor slab from the guest room into the boiler room below. Fire stopping contractors are returning to complete this missing item. | NULL
4305 | Saxon Court | SAXON_S001 | H21 | Scheme | 2022-10-28 21:09 | FRA_4305281020221842.pdf | HallS | 4305281020221840 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 4 | d1ccfl4wt7ul9swx61o | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45593 | Low | Court Manager | Replacement of damaged doorset to day centre storage area caused by suspected forced entry. | NULL
4305 | Saxon Court | SAXON_S001 | H21 | Scheme | 2022-10-28 21:09 | FRA_4305281020221842.pdf | HallS | 4305281020221840 | Extra Care | Extra Care Central | EC Central 2 | Central | Central Patch 4 | bsfjcapw0dhl9sx0ll5 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45593 | Low | Court Manager | Replacement of missing section of intumescent strip to day centre office door following relocation of lock. Infill section of door with hardwood fillet and seal with fire resisting material. | NULL
4307 | Myles Court | MYLESKINN_S001 | H21 | Scheme | 2022-10-14 12:50 | FRA_4307141020221226.pdf | HallS | 4307141020221220 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 4 | w8k641sb7dhl98f9ooo | Low Risk closed | Risk Closed | 44859.323 | Obs10 | Fire Safety And Notices | 45579 | Low | Court Manager | There are two fire safety signs that require replacing to the final exits adjacent to flat 55 by the bin store and in the stairwell. The court manager has arranged to order the required signage immediately. | Both required fire safety signs purchased and implemented through handyman service contractor on 24/10/22. Photos of these included in this completion process.
4308 | Queensridge Court | QUEENSRIDGE_S001 | H21 | Scheme | 2022-02-15 15:28 | FRA_4308150220220927.pdf | CrosdaleS | 4308150220220920 | Extra Care | Extra Care Central | EC Central 5 | Central | Central Patch 5 | 1x93ky7zctakzo6jzlo | Medium Risk closed | Risk Closed | 44904.6109 | Obs9 | Escape Lighting | 44972 | Medium | Court Manager | There are a few lights needing replacing. Replacements are with Open View | lights have been replaced
4308 | Queensridge Court | QUEENSRIDGE_S001 | H21 | Scheme | 2022-02-15 15:28 | FRA_4308150220220927.pdf | CrosdaleS | 4308150220220920 | Extra Care | Extra Care Central | EC Central 5 | Central | Central Patch 5 | 76k7wq3pfytkzo6o32q | Low Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45337 | Low | Court Manager | Documents still have the old logo. | NULL
4308 | Queensridge Court | QUEENSRIDGE_S001 | H21 | Scheme | 2022-02-15 15:28 | FRA_4308150220220927.pdf | CrosdaleS | 4308150220220920 | Extra Care | Extra Care Central | EC Central 5 | Central | Central Patch 5 | 6kxq4g1u6hokzo6qa9t | Low Risk closed | Risk Closed | 44904.6111 | Obs15 | Management Of Fire Safety | 45337 | Low | Court Manager | Training Information data is out of date. If is felt that all staff ard up to date with their training. To be confirmed | all staff have been retrained
4308 | Queensridge Court | QUEENSRIDGE_S001 | H21 | Scheme | 2022-02-15 15:28 | FRA_4308150220220927.pdf | CrosdaleS | 4308150220220920 | Extra Care | Extra Care Central | EC Central 5 | Central | Central Patch 5 | lc3e86o3xclkzo6h1eh | Observation Only | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Other | Domestic cleaners have cleaning filters on their schedules | NULL
4309 | Goldfield Court | GOLDFIELD_S001 | H21 | Scheme | 2022-01-22 11:23 | FRA_4309220120221120.pdf | HallS | 4309220120221120 | Extra Care | Extra Care Central | EC Central 5 | Central | Central Patch 4 | 50qlfky1pigkypqqv7e | Medium Risk closed | Risk Closed | 44680.5114 | Obs2 | Means Of Giving Warning In Case Of Fire | 44948 | Medium | Surveyor | Addition detection required to voids above communal areas that are more than 800mm high where switchgear is present. This work has been commissioned to be carried out by a fire alarm specialist to provide extended fire alarm coverage and early warning. Works are due to commence in February 2022. | The additional detection has now been installed on court.
4309 | Goldfield Court | GOLDFIELD_S001 | H21 | Scheme | 2022-01-22 11:23 | FRA_4309220120221120.pdf | HallS | 4309220120221120 | Extra Care | Extra Care Central | EC Central 5 | Central | Central Patch 4 | e3ohm741uxkypqqv9d | Low Risk closed | Risk Closed | 44736.4076 | Obs15 | Management Of Fire Safety | 45313 | Low | Court Manager | The current fire action notice refers to building occupants tackling a fire if possible. I have advised the scheme manager to replace the action notices immediately with the appropriate signage. | None
4309 | Goldfield Court | GOLDFIELD_S001 | H21 | Scheme | 2022-01-22 11:23 | FRA_4309220120221120.pdf | HallS | 4309220120221120 | Extra Care | Extra Care Central | EC Central 5 | Central | Central Patch 4 | 9hcgzkvp5okypqqv8f | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44948 | Medium | M&E Team | A lightning conductor to the 3 storey section of the building has come loose and is lodged on the first floor external roof area. This requires immediate reinstatement. Service contractor Omega have been informed and a works order will be raised to rectify this. | NULL
4311 | Howard Court (Wolverhampton) | HOWARDWOLV_S001 | H21 | Scheme | 2022-01-12 08:17 | FRA_4311110120221215.pdf | CrosdaleS | 4311110120221210 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 5 | 8c1jkctx9k6kya31wt9 | Low Risk closed | Risk Closed | 44641.4314 | Obs6 | Fire Hazards - Elimination & Control | 45302 | Low | Court Manager | Cooking: Electric oven, hob & cooker hood recently installed (Dec 2021). There's no detail of how often cooking will take place at present. There are detectors and a fire blanket present. | Cooking takes place periodically- around once per week. CM and resident at no 4 have food hygiene certs.
4311 | Howard Court (Wolverhampton) | HOWARDWOLV_S001 | H21 | Scheme | 2022-01-12 08:17 | FRA_4311110120221215.pdf | CrosdaleS | 4311110120221210 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 5 | 9zpf1rp5jxqkya3ohxb | Low Risk closed | Risk Closed | 44705.4761 | Obs10 | Fire Safety And Notices | 45302 | Low | Court Manager | Fire Exit Doors: External leaf Keep Clear sign. Internal leaf Push Bar to Open sign | signs on doors and outside completed
4311 | Howard Court (Wolverhampton) | HOWARDWOLV_S001 | H21 | Scheme | 2022-01-12 08:17 | FRA_4311110120221215.pdf | CrosdaleS | 4311110120221210 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 5 | 2zgpu3lerj9kya3l3jo | Low Risk closed | Risk Closed | 44641.4295 | Obs9 | Escape Lighting | 45302 | Low | Court Manager | Escape Lighting by Flat 3 not working. Job on order | job has been completed
4311 | Howard Court (Wolverhampton) | HOWARDWOLV_S001 | H21 | Scheme | 2022-01-12 08:17 | FRA_4311110120221215.pdf | CrosdaleS | 4311110120221210 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 5 | ski8tq555ekya41bxu | Observation Only | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Other | Poster in the the laundry for residents to clear the tumble drivers after use. Verbal instruction to cleaner to double check. | NULL
4312 | Paterson Court | PATERSON_S001 | H21 | Scheme | 2022-03-09 18:22 | FRA_4312090320220939.pdf | AndersonV | 4312090320220930 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 8 | sj6nfmqekl0jprii3 | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44994 | Medium | Court Manager | Electric arm chair in communal lounge requires checking to ensure it has the correct fire labels and PAT testing | NULL
4312 | Paterson Court | PATERSON_S001 | H21 | Scheme | 2022-03-09 18:22 | FRA_4312090320220939.pdf | AndersonV | 4312090320220930 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 8 | ulku8xchjcl0jvw834 | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44994 | Medium | Court Manager | Mobility scooter being charged in the communal entrance foyer. After speaking with the Court Manager we have agreed to fit an external charging point to remove the risk. The resident has also been advised that until the new charging point is fitted he can only charge it whilst the Court Manager is on duty. the new socket is due to be installed next week. Resident has been informed. | NULL
4312 | Paterson Court | PATERSON_S001 | H21 | Scheme | 2022-03-09 18:22 | FRA_4312090320220939.pdf | AndersonV | 4312090320220930 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 8 | tiocxrnitsbl0jnvmaq | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45360 | Low | Court Manager | Rear fire exit route requires clearing and should be kept clear and sterile at all times | NULL
4312 | Paterson Court | PATERSON_S001 | H21 | Scheme | 2022-03-09 18:22 | FRA_4312090320220939.pdf | AndersonV | 4312090320220930 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 8 | nmmy2o7qx6nl0jocejx | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 44994 | Medium | Court Manager | Tank room requires clearing of combustible materials | NULL
4312 | Paterson Court | PATERSON_S001 | H21 | Scheme | 2022-03-09 18:22 | FRA_4312090320220939.pdf | AndersonV | 4312090320220930 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 8 | ny9278xs1tml0jofcrp | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45360 | Low | Court Manager | Fire Action notice outside flat 12 requires completing to note where the assembly point is. | NULL
4312 | Paterson Court | PATERSON_S001 | H21 | Scheme | 2022-03-09 18:22 | FRA_4312090320220939.pdf | AndersonV | 4312090320220930 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 8 | amm0s4l4r58l0jo81to | Low Risk to be actioned | Risk Open | NULL | Obs9 | Escape Lighting | 45360 | Low | Court Manager | Guest room emergency light requires a new diffuser | NULL
4312 | Paterson Court | PATERSON_S001 | H21 | Scheme | 2022-03-09 18:22 | FRA_4312090320220939.pdf | AndersonV | 4312090320220930 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 8 | 99oqsm2wwhdl0jm3fxo | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45360 | Low | Court Manager | Fire assembly point sign needs to be displayed in the correct location | NULL
4312 | Paterson Court | PATERSON_S001 | H21 | Scheme | 2022-03-09 18:22 | FRA_4312090320220939.pdf | AndersonV | 4312090320220930 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 8 | zd9ikheaqjl0jo2uap | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45360 | Low | Court Manager | In the event of fire do not use lift signs required | NULL
4314 | Mackenzie Court | MACKENZIE_S001 | H21 | Scheme | 2022-09-05 22:50 | FRA_4314050920221006.pdf | HallS | 4314050920221000 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 4 | ei2emxrd3m6l7on9ajj | Low Risk to be actioned | Risk Open | NULL | Obs9 | Escape Lighting | 45540 | Low | Court Manager | There are 4 failed emergency lights outside flats 37. The court manager has raised a works order with Openview. | NULL
4314 | Mackenzie Court | MACKENZIE_S001 | H21 | Scheme | 2022-09-05 22:50 | FRA_4314050920221006.pdf | HallS | 4314050920221000 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 4 | m35qk7jiyi9l7ojryo2 | Observation Only | Risk Closed | 44816.5928 | Obs1 | The Building | NULL | N/A | Court Manager | Mackenzie Court operates an open roof void design above all first floor dwellings. Compartmentation exists to the 3 stairwells and sectionally to each wing of the building. Roof void detection has been installed and linked to each of the 1st floor dwellings below as a precautionary measure to provide early warning. Should there be an activation of a detector within the roof void, the 1st floor flats directly below will receive an alert tone to evacuate. This is an advisory note only. | No action required. FRA updated in fire folder.
4320 | Mattesley Court | MATTESLEY_B001 | H21 | Unknown | 2020-08-26 16:14 | FRA_432026082020.pdf | CrosdaleS | 432026082020 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | m4tpza23u6ekebbwee1 | Medium Risk closed | Risk Closed | 44328.9138 | Obs7 | Fire Protection Measures | 44434 | Medium | Court Manager | Stairwell next to commercial kitchen usedcas storage. Must be removed | Stored items removed
4320 | Mattesley Court | MATTESLEY_S001 | H21 | Scheme | 2022-07-29 08:26 | FRA_4320290720220826.pdf | CrosdaleS | 4320290720220820 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | nawwootj8bl6654y7h | Medium Risk closed | Risk Closed | 44792.5048 | Obs16 | Testing And Maintenance | 45136 | Medium | Court Manager | Final Exit Door near the Commercial Kitchen does not open when the push pad is operated. | MTH CAME OUT AND FIXED THE DOOR. NOW OPENS WITH EASE
4320 | Mattesley Court | MATTESLEY_S001 | H21 | Scheme | 2022-07-29 08:26 | FRA_4320290720220826.pdf | CrosdaleS | 4320290720220820 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | oiwxibuamjl6654y4n | Low Risk closed | Risk Closed | 44792.5064 | Obs9 | Escape Lighting | 45502 | Low | Court Manager | Some are out. There's a delay with supply and replacement. In progress | Emergency lights chased up. Only interim lights out, escape routes still accessible
4320 | Mattesley Court | MATTESLEY_S001 | H21 | Scheme | 2022-07-29 08:26 | FRA_4320290720220826.pdf | CrosdaleS | 4320290720220820 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | ofm705mt3jl6654y25 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45163 | Low | Court Manager | Items being left by stairwell adjacent to the commercial kitchen. Storage for items at Mattesley is a challenge. Mattesley are in the process of converting an unused assisted bathroom into a storage room | NULL
4320 | Mattesley Court | MATTESLEY_B001 | H21 | Unknown | 2020-08-26 16:14 | FRA_432026082020.pdf | CrosdaleS | 432026082020 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | r0ikhqp4umqkeb6dpcz | Medium Risk closed | Risk Closed | 44328.915 | Obs7 | Fire Protection Measures | 44434 | Medium | Court Manager | Fire Exit Doors x2 in Dining Room & x4 Lounge should be simple to operate. Currently fitted with a push bar and thumb turn. Recommend to remove the thumb turn or complete replacement with fit either panic bolt, push bar, or quick release locks | When contractor attended they advised doors would open in the event of a fire even if thumb turn on
4320 | Mattesley Court | MATTESLEY_S001 | H21 | Scheme | 2022-07-29 08:26 | FRA_4320290720220826.pdf | CrosdaleS | 4320290720220820 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | c0c5djdky2l6654y3z | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45502 | Low | Court Manager | Cross corridor door outside Flat 48 does not close due to the carpet. A possible adjustment to the door closure may resolve this. | NULL
4320 | Mattesley Court | MATTESLEY_S001 | H21 | Scheme | 2022-07-29 08:26 | FRA_4320290720220826.pdf | CrosdaleS | 4320290720220820 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | b2aw9wqmwsul6654y6k | Low Risk closed | Risk Closed | 44792.5054 | Obs15 | Management Of Fire Safety | 45502 | Low | Court Manager | False Alarms are recorded digitally on Erica. No current access available at the time of the assessment. | Logged in red fire folder in CAM office
4320 | Mattesley Court | MATTESLEY_B001 | H21 | Unknown | 2020-08-26 16:14 | FRA_432026082020.pdf | CrosdaleS | 432026082020 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | 39tusjg2hwykeb6koy2 | Low Risk closed | Risk Closed | 44474.5844 | Obs7 | Fire Protection Measures | 44799 | Low | Court Manager | Damaged Fire Door leading to Flat 30. To be checked | Informed Sylvia Drysdale surveyor
4320 | Mattesley Court | MATTESLEY_B001 | H21 | Unknown | 2020-08-26 16:14 | FRA_432026082020.pdf | CrosdaleS | 432026082020 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | 3whf9qnjb4wkeb5yda7 | Medium Risk closed | Risk Closed | 44127.704 | Obs10 | Fire Safety And Notices | 44434 | Medium | Court Manager | 'Fire Exit Keep Clear' signs should be affixed on final exit doors (doors that open onto areas that have a potential to become obstructed by storage, vehicle parking or other uncontrolled occurances) | Fire excited keep clear now in place
4320 | Mattesley Court | MATTESLEY_B001 | H21 | Unknown | 2020-08-26 16:14 | FRA_432026082020.pdf | CrosdaleS | 432026082020 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | 429w8hppvr1keb5tmv5 | Low Risk closed | Risk Closed | 44328.9159 | Obs10 | Fire Safety And Notices | 44799 | Low | Court Manager | 'Fire Action Notice' should be adjacent to each fire alarm break glass call point or other suitable location: final exits on ground, 1st and 2nd floor. | Fire notices in place now
4320 | Mattesley Court | MATTESLEY_S001 | H21 | Scheme | 2022-07-29 08:26 | FRA_4320290720220826.pdf | CrosdaleS | 4320290720220820 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | 6ncidtrk9kcl6654y5g | Low Risk closed | Risk Closed | 44792.5057 | Obs10 | Fire Safety And Notices | 45502 | Low | Court Manager | 'Fire Exit' signs should be visible on the inner leaf 'Keep Clear' sign on the outer leaf | Replacement signs gone up
4320 | Mattesley Court | MATTESLEY_S001 | H21 | Scheme | 2022-07-29 08:26 | FRA_4320290720220826.pdf | CrosdaleS | 4320290720220820 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | vbrz38sg5ql6654y2x | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45502 | Low | Court Manager | Cross corridor doors are showing gaps on approx 4mm gaps possibly due to the recent rise in temperatures. Doors may need overhauling or ease and adjusted in the first instance. | NULL
4320 | Mattesley Court | MATTESLEY_S001 | H21 | Scheme | 2022-07-29 08:26 | FRA_4320290720220826.pdf | CrosdaleS | 4320290720220820 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | xj0aatpbqbl6654y3h | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45502 | Low | Court Manager | Service Cupboards: Fire stop holes. For example opposite Flat 43 | NULL
4321 | Knaves Court | KNAVES_S001 | H21 | Scheme | 2022-01-18 16:32 | FRA_4321180120221138.pdf | CrosdaleS | 4321180120221130 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | ndtj2k6s3unkyk1mn8r | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45309 | Low | Court Manager | Fire Action Notice not displayed next to call points | NULL
4321 | Knaves Court | KNAVES_S001 | H21 | Scheme | 2022-01-18 16:32 | FRA_4321180120221138.pdf | CrosdaleS | 4321180120221130 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | n4ii8i74urlkyk2efb5 | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45309 | Low | Court Manager | There is a current verbal procedure to both resident's and domestic staff. | NULL
4321 | Knaves Court | KNAVES_S001 | H21 | Scheme | 2022-01-18 16:32 | FRA_4321180120221138.pdf | CrosdaleS | 4321180120221130 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | krn26w1ozgpkyk1p5ba | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45309 | Low | Court Manager | Fire Exit Keep Clear sign to be affixed on the external leaf on final exit doors | NULL
4322 | Deighton Court | DEIGHTON_S001 | H21 | Scheme | 2022-08-09 15:57 | FRA_4322090820221347.pdf | CrosdaleS | 4322090820221340 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | rkmfn61g0al6m8tahw | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45513 | Low | Court Manager | A few Final Exit Doors do not have the 'Push Pad/Bar To Exit' sign fixed the internal face of the door | NULL
4323 | Alrewych Court | ALREWYCH_S001 | H21 | Scheme | 2022-08-04 15:55 | FRA_4323040820221424.pdf | CrosdaleS | 4323040820221420 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | spzpj5bz5ul6f5cuc6 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45508 | Low | Court Manager | Commercial Kitchen to hall door, Adjust door closer | NULL
4323 | Alrewych Court | ALREWYCH_S001 | H21 | Scheme | 2022-08-04 15:55 | FRA_4323040820221424.pdf | CrosdaleS | 4323040820221420 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | sygyk1oh5ubl6f5e2jf | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45508 | Low | Court Manager | The Shed, adjust door closure to door to restaurant and lobby to WCs | NULL
4323 | Alrewych Court | ALREWYCH_S001 | H21 | Scheme | 2022-08-04 15:55 | FRA_4323040820221424.pdf | CrosdaleS | 4323040820221420 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | nxvyiot1bdl6f5aw16 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45508 | Low | Court Manager | Cross corridor door next to Flat 31 to adjust door closures | NULL
4323 | Alrewych Court | ALREWYCH_S001 | H21 | Scheme | 2022-08-04 15:55 | FRA_4323040820221424.pdf | CrosdaleS | 4323040820221420 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | 664xc1ev35tl6f2klzf | Medium Risk to be actioned | Risk Open | NULL | Obs16 | Testing And Maintenance | 45142 | Medium | Court Manager | The AOVs are not working since May 2022. 1st floor AOVs are jammed opened. 2nd floor AOVs won't open. Repair appointment scheduled for 08/08/22 | NULL
4323 | Alrewych Court | ALREWYCH_S001 | H21 | Scheme | 2022-08-04 15:55 | FRA_4323040820221424.pdf | CrosdaleS | 4323040820221420 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | ccpwfry5i9kl6f58ps3 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45508 | Low | Court Manager | Fire Exit Door next to Flat 6 does not open. Top latch is jammed | NULL
4323 | Alrewych Court | ALREWYCH_S001 | H21 | Scheme | 2022-08-04 15:55 | FRA_4323040820221424.pdf | CrosdaleS | 4323040820221420 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | e809712l30fl6f2klwb | Low Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45508 | Low | Court Manager | FYI it would be beneficial for night staff to attend a fire alarm test on a Tuesday and include as part of new staff induction | NULL
4323 | Alrewych Court | ALREWYCH_S001 | H21 | Scheme | 2022-08-04 15:55 | FRA_4323040820221424.pdf | CrosdaleS | 4323040820221420 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | xrvngfiht5l6f2kly9 | Medium Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45142 | Medium | Court Manager | New Carers are in the process of being inducted | NULL
4323 | Alrewych Court | ALREWYCH_S001 | H21 | Scheme | 2022-08-04 15:55 | FRA_4323040820221424.pdf | CrosdaleS | 4323040820221420 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | zb4e89mmwuol6f2klx2 | Low Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45508 | Low | Court Manager | Housing Manager Fire Training booked on September 2022 course | NULL
4324 | Winehala Court | WINEHALA_S001 | H21 | Scheme | 2022-02-01 17:21 | FRA_4324010220221704.pdf | CrosdaleS | 4324010220221700 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | 49imh32ecbykz4dsisv | Low Risk closed | Risk Closed | 44642.3691 | Obs10 | Fire Safety And Notices | 45323 | Low | Court Manager | Fire Notices are not consistent against each break glass | All notices have been changed and are consistent
4325 | The Watermill | THEWATERMILL_S001 | H21 | Scheme | 2022-09-15 17:45 | FRA_4325150920220947.pdf | CrosdaleS | 4325150920220940 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | 5788xh1dxrl82u6now | Observation Only | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Other | There is detection within the resident's rooms which is connected the the main fire panel. When activated the alarm is direct to the call centre | NULL
4325 | The Watermill | THEWATERMILL_S001 | H21 | Scheme | 2022-09-15 17:45 | FRA_4325150920220947.pdf | CrosdaleS | 4325150920220940 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | c2yap3lozw8l832uazj | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45217 | Low | Court Manager | Commercial Kitchen | NULL
4325 | The Watermill | THEWATERMILL_S001 | H21 | Scheme | 2022-09-15 17:45 | FRA_4325150920220947.pdf | CrosdaleS | 4325150920220940 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | u21gulppuwl834ag8f | Medium Risk to be actioned | Risk Open | NULL | Obs9 | Escape Lighting | 45184 | Medium | Court Manager | No emergency lights working in the day centre. | NULL
4325 | The Watermill | THEWATERMILL_S001 | H21 | Scheme | 2022-09-15 17:45 | FRA_4325150920220947.pdf | CrosdaleS | 4325150920220940 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | spn263ua6fkl82ukzss | Medium Risk to be actioned | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | 45184 | Medium | Court Manager | The recommended evacuation aided sheets for bed bound resident's on air flow mattresses are the 'parachute' type. These can remain under the bed's airflow mattress. Easily accessible and mobilise invthe event of a fire. To be ordered. | NULL
4325 | The Watermill | THEWATERMILL_S001 | H21 | Scheme | 2022-09-15 17:45 | FRA_4325150920220947.pdf | CrosdaleS | 4325150920220940 | PPP-PFI | Walsall PPP Services | Walsall PPP Services | Central | Central Patch 5 | hpvxfsz510hl832y5qb | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45184 | Medium | Court Manager | Fire doors to commercial kitchen, damaged fire seal | NULL
4327 | Oakley Gardens | OAKLEYGARD_S001 | H21 | Scheme | 2022-03-16 18:43 | FRA_4327160320220915.pdf | HallS | 4327160320220910 | Extra Care | Extra Care Central | EC Central 5 | Central | Central Patch 4 | im4wrxvl05kl0tcqwj5 | Low Risk closed | Risk Closed | 44704.6929 | Obs3 | Details Of Fire Loss | 45367 | Low | Court Manager | Recommendation for all residents dwellings to be checked and any remaining incandescent / filament bulbs within laundry cupboards to be replaced either with a new bulb or a complete new fitting to prevent the installation of non LED light bulbs. | All lights replaced with LED
4327 | Oakley Gardens | OAKLEYGARD_S001 | H21 | Scheme | 2022-03-16 18:43 | FRA_4327160320220915.pdf | HallS | 4327160320220910 | Extra Care | Extra Care Central | EC Central 5 | Central | Central Patch 4 | nhfgymccfbil0twd13o | Medium Risk closed | Risk Closed | 44648.6002 | Obs6 | Fire Hazards - Elimination & Control | 45001 | Medium | Court Manager | Some residents have large ornaments & plastic plants outside their properties within the communal corridors which could obstruct communal access & egress in the event of an emergency. These are to be relocated out of the communal escape routes immediately. | Memo sent and all have been removed
4332 | Harmony House | HARMONYHOUSE_S001 | H21 | Scheme | 2021-12-24 11:13 | FRA_4332231220211516.pdf | HallS | 4332231220211510 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 1 | tgzuxhlg7kpkxj536mp | Low Risk Overdue | Risk Open | NULL | Obs1 | The Building | 44896 | Low | Other | Improvements required to fire stopping around service penetrations where they pass above communal fire break doors. An accredited fire stopping contractor has been instructed to survey and provide a quotation for rectification of the fire stopping works. | NULL
4332 | Harmony House | HARMONYHOUSE_S001 | H21 | Scheme | 2021-12-24 11:13 | FRA_4332231220211516.pdf | HallS | 4332231220211510 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 1 | cdylkwkje1kxj5fzyy | Low Risk to be actioned | Risk Open | NULL | Obs9 | Escape Lighting | 45283 | Low | Court Manager | There are approximately 10 emergency light fittings on court that have failed. The court manager has raised a repair with a local contractor to rectify the failures. | NULL
4332 | Harmony House | HARMONYHOUSE_S001 | H21 | Scheme | 2021-12-24 11:13 | FRA_4332231220211516.pdf | HallS | 4332231220211510 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 1 | 070teh6q0bdakxj4p5or | Low Risk Overdue | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44896 | Low | Other | The residents front doors are not equipped with intumescent letter plates. The court manager has received a quotation for rectification but this was shelved as replacement cross corridor doors & residents front doors have been scheduled for replacement in 2022. | NULL
4333 | Barbara Glasgow House | BARBARAGLAS_S001 | H21 | Scheme | 2021-12-23 14:40 | FRA_4333231220211437.pdf | HallS | 4333231220211430 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 1 | ddzjajl4ueukxj2jrr5 | Medium Risk closed | Risk Closed | 44778.7504 | Obs8 | Measures To Limit Fire Spread And Development | 44539 | Medium | Other | There are open gaps above some fire break doors around the court which require redress. A works order has been raised for an accredited fire stopping contractor to rectify all ineffective fire stopping. Works scheduled to commence in January 2022 | Works now completed as confirmed by Surveyor (Sam Hall)
4333 | Barbara Glasgow House | BARBARAGLAS_S001 | H21 | Scheme | 2021-12-23 14:40 | FRA_4333231220211437.pdf | HallS | 4333231220211430 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 1 | plssiy6xdw9kxj2jrpu | Low Risk closed | Risk Closed | 44778.7507 | Obs1 | The Building | 45283 | Low | Other | Improvements required to fire stopping around service penetrations where they pass above communal fire break doors. A works order has been raised for an accredited fire stopping contractor to attend and remedy the poor fire stopping around service penetrations. Works scheduled to commence in January 2022 | works now completed as confirmed by Surveyor (Sam Hall)
4333 | Barbara Glasgow House | BARBARAGLAS_S001 | H21 | Scheme | 2021-12-23 14:40 | FRA_4333231220211437.pdf | HallS | 4333231220211430 | Retirement Housing | Mid West | West Mids Hereford and Worcs | Central | Central Patch 1 | plssiy6xdw9kxj2jrpu | Low Risk closed | Risk Closed | 44778.7502 | Obs1 | The Building | 45283 | Low | Other | Improvements required to fire stopping around service penetrations where they pass above communal fire break doors. A works order has been raised for an accredited fire stopping contractor to attend and remedy the poor fire stopping around service penetrations. Works scheduled to commence in January 2022 | Works now completed as confirmed by Surveyor (Sam Hall)
4401 | Burchell Court | BURCHELL_S001 | H21 | Scheme | 2022-01-12 16:51 | FRA_4401120120221644.pdf | mayesd | 4401120120221640 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | nm5l74vg63kybrw88i | Medium Risk closed | Risk Closed | 44607.5322 | Obs7 | Fire Protection Measures | 44938 | Medium | Court Manager | Communal lighting outside the flat front doors does not have a fire rated Dome. The loft hatch within the flats is also not fire rated which compromises the 30-minute fire resistance. The light fittings outside the flats require replacement with with a suited fire rated fitting. This affects 10 flats on the new build side of the court | Electrician on site 15/02/22 Lights changed to fire rated with switch to turn on and off
4401 | Burchell Court | BURCHELL_S001 | H21 | Scheme | 2022-01-12 16:51 | FRA_4401120120221644.pdf | mayesd | 4401120120221640 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | nklf6fxkdxkybrw87l | Medium Risk closed | Risk Closed | 44711.6709 | Obs7 | Fire Protection Measures | 44938 | Medium | Court Manager | The door opposite the lounge adjacent to the laundry is not a fire door and requires replacement to a suitable FD 30 door | Door has now been replaced with new fire door.
4401 | Burchell Court | BURCHELL_S001 | H21 | Scheme | 2022-01-12 16:51 | FRA_4401120120221644.pdf | mayesd | 4401120120221640 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | t1ucuina65kybrw8cr | Low Risk closed | Risk Closed | 44599.4114 | Obs10 | Fire Safety And Notices | 45303 | Low | Court Manager | Remove redundant fire action notices | Redundant notices taken down.
4401 | Burchell Court | BURCHELL_S001 | H21 | Scheme | 2022-01-12 16:51 | FRA_4401120120221644.pdf | mayesd | 4401120120221640 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | l07k1nagz1gkybrw8bt | Low Risk closed | Risk Closed | 44603.4019 | Obs8 | Measures To Limit Fire Spread And Development | 45303 | Low | Court Manager | Flat 36 Automatic door closer installed. One screw is needed to fix the closer to the frame | Wo 1512363 Completed by HP on 10.02.22
4401 | Burchell Court | BURCHELL_S001 | H21 | Scheme | 2022-01-12 16:51 | FRA_4401120120221644.pdf | mayesd | 4401120120221640 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | mfyd8nmvgenkybrw8b4 | Low Risk closed | Risk Closed | 44585.3916 | Obs8 | Measures To Limit Fire Spread And Development | 45303 | Low | Court Manager | Arrange for a blanking plate to be fitted over the the redundant wiring opposite flat 47 | WO 1512357 cost £36.00 completed 19.01.22
4401 | Burchell Court | BURCHELL_S001 | H21 | Scheme | 2022-01-12 16:51 | FRA_4401120120221644.pdf | mayesd | 4401120120221640 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | csg2anc1rx8kybrw89l | Low Risk closed | Risk Closed | 44607.5032 | Obs8 | Measures To Limit Fire Spread And Development | 45303 | Low | Court Manager | Along the communal corridor wall from flats 10 to 14 there are minor compartmentation breaches from the flats to the corridors. These will need to be adequately fire stopped | Handyman onsite 15.02.22 completed
4401 | Burchell Court | BURCHELL_S001 | H21 | Scheme | 2022-01-12 16:51 | FRA_4401120120221644.pdf | mayesd | 4401120120221640 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | 6kzb7mhb7fekybrw8ac | Medium Risk closed | Risk Closed | 44585.3907 | Obs8 | Measures To Limit Fire Spread And Development | 44938 | Medium | Court Manager | Flat 17 a closer is required | WO 1512367 cost £160.00 completed 19.01.22
4401 | Burchell Court | BURCHELL_S001 | H21 | Scheme | 2022-01-12 16:51 | FRA_4401120120221644.pdf | mayesd | 4401120120221640 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | ywxmz618bemkybrw86a | Low Risk to be actioned | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | 45303 | Low | Surveyor | Following on from the fire alarm upgrade that took place there are redundant detectors identified within some properties. These were left as lockdown measures were imposed at the time of completion. The surveyor needs to arrange the removal of these detectors | NULL
4402 | Chapman Court | CHAPMAN_S001 | H21 | Scheme | 2022-01-12 16:44 | FRA_4402120120221635.pdf | mayesd | 4402120120221630 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | 9b3ijtn8c0qkybrpojj | Medium Risk closed | Risk Closed | 44574.561 | Obs8 | Measures To Limit Fire Spread And Development | 44938 | Medium | Court Manager | Threshold smoke seals are required at the base of Flat 41, store room d, and the guest room | All ordered through safe links on 130122 to be installed asp
4405 | Randall Schofield Court | RANDALLSCHO_S001 | H21 | Scheme | 2022-06-14 09:14 | FRA_4405140620220854.pdf | mayesd | 4405140620220850 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | ahtdcu66lgkl4dvzntj | Medium Risk closed | Risk Closed | 44747.5658 | Obs8 | Measures To Limit Fire Spread And Development | 45091 | Medium | Court Manager | Flat 28 internal door wedge requires removal | Reported to handyperson
4405 | Randall Schofield Court | RANDALLSCHO_S001 | H21 | Scheme | 2022-06-14 09:14 | FRA_4405140620220854.pdf | mayesd | 4405140620220850 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | 0tuy8ncgb3jql4dvbla2 | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45457 | Low | Surveyor | Some fire stopping required where cables penetrate between communal compartment walls above suspended ceiling. It is recommended to attend to these when the suspended ceiling is replaced this financial year | NULL
4405 | Randall Schofield Court | RANDALLSCHO_S001 | H21 | Scheme | 2022-06-14 09:14 | FRA_4405140620220854.pdf | mayesd | 4405140620220850 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | 2cwhf1q6fh9l4dvblcb | Low Risk closed | Risk Closed | 44727.6219 | Obs8 | Measures To Limit Fire Spread And Development | 45457 | Low | Court Manager | Repair communal compartment door by lounge | Repair raised with handyman
4405 | Randall Schofield Court | RANDALLSCHO_S001 | H21 | Scheme | 2022-06-14 09:14 | FRA_4405140620220854.pdf | mayesd | 4405140620220850 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | kkimug9cwxl4dvblbf | Medium Risk closed | Risk Closed | 44727.623 | Obs8 | Measures To Limit Fire Spread And Development | 45091 | Medium | Court Manager | Chair in first floor upper corridor stairwell does not appear to be fire rated and needs to be removed | Chair removed from landing and stored until resident decides what to do with it
4405 | Randall Schofield Court | RANDALLSCHO_S001 | H21 | Scheme | 2022-06-14 09:14 | FRA_4405140620220854.pdf | mayesd | 4405140620220850 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | xbjrj26sdp9l4dvbld0 | Medium Risk closed | Risk Closed | 44727.6223 | Obs8 | Measures To Limit Fire Spread And Development | 45091 | Medium | Court Manager | Flat 14 latching mechanism on a overhead closer requires adjustment | Repair raised with handyman
4405 | Randall Schofield Court | RANDALLSCHO_S001 | H21 | Scheme | 2022-06-14 09:14 | FRA_4405140620220854.pdf | mayesd | 4405140620220850 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | vmo1nw5s90hl4dvbldp | Medium Risk closed | Risk Closed | 44747.5651 | Obs8 | Measures To Limit Fire Spread And Development | 45091 | Medium | Court Manager | Flat 17 Internal door hold open device requires removal | Work order raised with handyperson
4409 | Hogshill Gardens | HOGSHILLGARD_S001 | H21 | Scheme | 2022-02-17 11:24 | FRA_4409170220221115.pdf | mayesd | 4409170220221110 | Extra Care | Extra Care South | EC South 4 | South | South Patch 1 | vzuue5jloekzqw7i43 | Medium Risk closed | Risk Closed | 44669.2613 | Obs5 | Evacuation Strategy And Training | 44974 | Medium | Court Manager | At the time of undertaking the on-site fire risk assessment training could not be validated as the court manager was unavailable. This will be followed up up at my next site visit or or if the information were to be sent via email. | WAS FOLLOWED UP AND COMPLETED
4409 | Hogshill Gardens | HOGSHILLGARD_S001 | H21 | Scheme | 2022-02-17 11:24 | FRA_4409170220221115.pdf | mayesd | 4409170220221110 | Extra Care | Extra Care South | EC South 4 | South | South Patch 1 | g4p0lst612kzqw06fw | Observation Only | Risk Closed | 44613.2727 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | Flat 17 has oxygen | CHECKED ALL GOOD AT FLAT 17 OXYGEN STORED WELL
4409 | Hogshill Gardens | HOGSHILLGARD_S001 | H21 | Scheme | 2022-02-17 11:24 | FRA_4409170220221115.pdf | mayesd | 4409170220221110 | Extra Care | Extra Care South | EC South 4 | South | South Patch 1 | ue3yriop29lkzqw2faf | Medium Risk closed | Risk Closed | 44615.5822 | Obs4 | The Occupant - Information Provided By The Court Manager | 44974 | Medium | Court Manager | At the time of undertaking the on site fire risk assessment the PCFRA,s could not be validated as the Court Manager was unavailable. This will be followed-up up at my next site visit or or or if the information were too be sent via email. | NONE
4409 | Hogshill Gardens | HOGSHILLGARD_S001 | H21 | Scheme | 2022-02-17 11:24 | FRA_4409170220221115.pdf | mayesd | 4409170220221110 | Extra Care | Extra Care South | EC South 4 | South | South Patch 1 | ooc82itap2gkzqw06ek | Medium Risk closed | Risk Closed | 44669.2615 | Obs2 | Means Of Giving Warning In Case Of Fire | 44974 | Medium | Court Manager | Remove duplicate zone plans adjacent to the fire panel | INFORMED AND COMPLETED
4409 | Hogshill Gardens | HOGSHILLGARD_S001 | H21 | Scheme | 2022-02-17 11:24 | FRA_4409170220221115.pdf | mayesd | 4409170220221110 | Extra Care | Extra Care South | EC South 4 | South | South Patch 1 | 5ntbmkhvfo5kzqw06gz | Medium Risk closed | Risk Closed | 44665.6637 | Obs6 | Fire Hazards - Elimination & Control | 44974 | Medium | Surveyor | Following on from the removal of the timber cladding it is piled into a skip adjacent to the building. This needs to be removed accordingly | Skip removed
4409 | Hogshill Gardens | HOGSHILLGARD_S001 | H21 | Scheme | 2022-02-17 11:24 | FRA_4409170220221115.pdf | mayesd | 4409170220221110 | Extra Care | Extra Care South | EC South 4 | South | South Patch 1 | 4vt9g06ktx7kzqw06in | Low Risk closed | Risk Closed | 44616.4296 | Obs10 | Fire Safety And Notices | 45339 | Low | Court Manager | Remove redundant extinguisher sign in main entrance lobby | I took extinguisher sign out of main entrance when I take a photo I not sure if it is saving as no where to say saved.
4409 | Hogshill Gardens | HOGSHILLGARD_S001 | H21 | Scheme | 2022-02-17 11:24 | FRA_4409170220221115.pdf | mayesd | 4409170220221110 | Extra Care | Extra Care South | EC South 4 | South | South Patch 1 | efolrnajl0gkzqw06hx | Low Risk closed | Risk Closed | 44615.582 | Obs10 | Fire Safety And Notices | 45339 | Low | Court Manager | Remove exit sign below fire exit light on ground floor exit | ALL OK NO CONCERNS
4412 | Bell Mead | JBBELLMEAD_S001 | H21 | Scheme | 2022-01-14 13:28 | FRA_4412140120221309.pdf | mayesd | 4412140120221300 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | af2knb1czktkyefbalo | Observation Only | Risk Closed | 44578.3738 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Court Manager | It is advisable the fire alarm system is planned for replacement in the next 3 years. During which time any cable penetrations are to have new fire stopping work completed | N/A
4412 | Bell Mead | JBBELLMEAD_S001 | H21 | Scheme | 2022-01-14 13:28 | FRA_4412140120221309.pdf | mayesd | 4412140120221300 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | 6c7me4qjktwkyefj917 | Medium Risk closed | Risk Closed | 44578.371 | Obs8 | Measures To Limit Fire Spread And Development | 44940 | Medium | Court Manager | Flat 7 front door does not self close fully and requires adjustment | repair WO raised and work completed 22/12/2021
4412 | Bell Mead | JBBELLMEAD_S001 | H21 | Scheme | 2022-01-14 13:28 | FRA_4412140120221309.pdf | mayesd | 4412140120221300 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | nom8pjuq6uhkyefevrn | Low Risk closed | Risk Closed | 44578.3726 | Obs6 | Fire Hazards - Elimination & Control | 45305 | Low | Court Manager | Communal meter box doors should be secured | Advised resident to keep closed and locked. completed 13/12/2021
4412 | Bell Mead | JBBELLMEAD_S001 | H21 | Scheme | 2022-01-14 13:28 | FRA_4412140120221309.pdf | mayesd | 4412140120221300 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | fjzonkvatkjkyefkh8w | Low Risk closed | Risk Closed | 44578.3732 | Obs8 | Measures To Limit Fire Spread And Development | 45305 | Low | Court Manager | Flat 17 front door does not fully latch and requires adjustment | repair completed 14/01/2022
4412 | Bell Mead | JBBELLMEAD_S001 | H21 | Scheme | 2022-01-14 13:28 | FRA_4412140120221309.pdf | mayesd | 4412140120221300 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 1 | hgjn1b6gfdwkyefjr05 | Medium Risk closed | Risk Closed | 44578.3714 | Obs8 | Measures To Limit Fire Spread And Development | 44940 | Medium | Court Manager | 3rd floor bin room door requires closer to be fitted | work completed 2212/2021
4414 | Meadow Court | JBMEADOW_S001 | H21 | Scheme | 2022-08-03 13:34 | FRA_4414030820221058.pdf | ComleyB | 4414030820221050 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 5 | ha3rup2nh0dl6dk53kb | Low Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45507 | Low | Court Manager | Copy of court floor plans/building layout to be inserted in fire box. Plans should clearly show location of electric and gas main isolation points. | NULL
4414 | Meadow Court | JBMEADOW_S001 | H21 | Scheme | 2022-08-03 13:34 | FRA_4414030820221058.pdf | ComleyB | 4414030820221050 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 5 | q9r3z14s6l6djzv9t | Medium Risk closed | Risk Closed | 44805.3822 | Obs5 | Evacuation Strategy And Training | 45141 | Medium | Court Manager | Resident fire box information sheet to be updated in fire box. To be placed in visible folder not in letter envelope. | completed
4414 | Meadow Court | JBMEADOW_S001 | H21 | Scheme | 2022-08-03 13:34 | FRA_4414030820221058.pdf | ComleyB | 4414030820221050 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 5 | sm7s9y45q9l6dik968 | Low Risk Overdue | Risk Open | NULL | Obs15 | Management Of Fire Safety | 44792 | Low | Court Manager | Fire Safety Responsibilities matrix to be completed and placed in fire safety management folder (section 2) | NULL
4414 | Meadow Court | JBMEADOW_S001 | H21 | Scheme | 2022-08-03 13:34 | FRA_4414030820221058.pdf | ComleyB | 4414030820221050 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 5 | rtpdvk66pdkl6dko4h4 | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45276 | Low | Court Manager | Door mats to be removed from communal corridors. | NULL
4414 | Meadow Court | JBMEADOW_S001 | H21 | Scheme | 2022-08-03 13:34 | FRA_4414030820221058.pdf | ComleyB | 4414030820221050 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 5 | 7jkj81t6v0gl6dk9m40 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45507 | Low | Court Manager | Flat 5 Automatic closure to be reconnected | NULL
4414 | Meadow Court | JBMEADOW_S001 | H21 | Scheme | 2022-08-03 13:34 | FRA_4414030820221058.pdf | ComleyB | 4414030820221050 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 5 | 23tbay966sul6dl57xo | Low Risk closed | Risk Closed | 44782.4598 | Obs6 | Fire Hazards - Elimination & Control | 45507 | Low | Court Manager | Tumble drier ducts to be cleaned and annually maintained. | They are cleaned weekly by the cleaner .
4414 | Meadow Court | JBMEADOW_S001 | H21 | Scheme | 2022-08-03 13:34 | FRA_4414030820221058.pdf | ComleyB | 4414030820221050 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 5 | 3lmn7y9ad6il6dkvu22 | Low Risk closed | Risk Closed | 44782.4604 | Obs7 | Fire Protection Measures | 45276 | Low | Court Manager | Plant pot to be stored tight to corner or removed from communal corridor. Currently impeding on exit route. | Requested that resident in flat 4 removes it as I have previously .
4414 | Meadow Court | JBMEADOW_S001 | H21 | Scheme | 2022-08-03 13:34 | FRA_4414030820221058.pdf | ComleyB | 4414030820221050 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 5 | 1b3nknmm9jcl6dj3fb5 | Low Risk closed | Risk Closed | 44805.3816 | Obs15 | Management Of Fire Safety | 45507 | Low | Court Manager | All compliance checks stored on PEBBLES and ERICA. Court manager to provide evidence latest log of checks. | all compliance on 1st touch
4414 | Meadow Court | JBMEADOW_S001 | H21 | Scheme | 2022-08-03 13:34 | FRA_4414030820221058.pdf | ComleyB | 4414030820221050 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 5 | ag6sgbspqdl6dl9oyl | Low Risk closed | Risk Closed | 44782.48 | Obs7 | Fire Protection Measures | 45507 | Low | Court Manager | Accumulation of items in communal area. Items to be stored in flat not communal corridor. | Resident asked to remove all items and advised this is not permitted ,
4414 | Meadow Court | JBMEADOW_S001 | H21 | Scheme | 2022-08-03 13:34 | FRA_4414030820221058.pdf | ComleyB | 4414030820221050 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 5 | 9vcpqaszg2dl6diglvz | Low Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45507 | Low | Court Manager | Ensure Fire Strategy is up to date and is latest version in fire safety management folder | NULL
4414 | Meadow Court | JBMEADOW_S001 | H21 | Scheme | 2022-08-03 13:34 | FRA_4414030820221058.pdf | ComleyB | 4414030820221050 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 5 | 8fjx83m69z7l6dj62p0 | Low Risk closed | Risk Closed | 44805.3794 | Obs15 | Management Of Fire Safety | 45507 | Low | Court Manager | Completed copy of resident fire box information sheet to be placed in fire safety management folder. | completed paperwork
4414 | Meadow Court | JBMEADOW_S001 | H21 | Scheme | 2022-08-03 13:34 | FRA_4414030820221058.pdf | ComleyB | 4414030820221050 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 5 | 8ryoozzbbr6l6dkh5r0 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45507 | Low | Court Manager | Flat 7 door not fully closing. Door to be eased and adjusted. | NULL
4414 | Meadow Court | JBMEADOW_S001 | H21 | Scheme | 2022-08-03 13:34 | FRA_4414030820221058.pdf | ComleyB | 4414030820221050 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 5 | fenyzlsho26l6dk2883 | Low Risk closed | Risk Closed | 44782.461 | Obs5 | Evacuation Strategy And Training | 45507 | Low | Court Manager | Fire detectors not to be stored in fire box. | They were stored in there by Openview for ease of access . I will remove and put in office
4414 | Meadow Court | JBMEADOW_S001 | H21 | Scheme | 2022-08-03 13:34 | FRA_4414030820221058.pdf | ComleyB | 4414030820221050 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 5 | crig10kgmmol6dkjxaq | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45507 | Low | Court Manager | Flat 8 door not fully closing. Door to be eased and adjusted. | NULL
4414 | Meadow Court | JBMEADOW_S001 | H21 | Scheme | 2022-08-03 13:34 | FRA_4414030820221058.pdf | ComleyB | 4414030820221050 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 5 | wg8q6eei07bl6dkru95 | Low Risk closed | Risk Closed | 44782.4615 | Obs7 | Fire Protection Measures | 45507 | Low | Court Manager | Walker to be stored inside flat, not in communal corridor. | Moved to cupboard .
4414 | Meadow Court | JBMEADOW_S001 | H21 | Scheme | 2022-08-03 13:34 | FRA_4414030820221058.pdf | ComleyB | 4414030820221050 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 5 | xndsdhzp51l6did68w | Low Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45507 | Low | Court Manager | Health and Safety Policy to be updated. | NULL
4414 | Meadow Court | JBMEADOW_S001 | H21 | Scheme | 2022-08-03 13:34 | FRA_4414030820221058.pdf | ComleyB | 4414030820221050 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 5 | wuj1f8r27arl6djf3zo | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45141 | Medium | Court Manager | Flat 2 Door not fully closing and daylight visible on latch side. Door may require replacing with new FD30. | NULL
4414 | Meadow Court | JBMEADOW_S001 | H21 | Scheme | 2022-08-03 13:34 | FRA_4414030820221058.pdf | ComleyB | 4414030820221050 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 5 | x6vtkq4mjp9l6dl29je | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45507 | Low | Court Manager | Radiant bar electric heater, in laundry, to be replaced with modern panel heater or oil filled radiator. | NULL
4414 | Meadow Court | JBMEADOW_S001 | H21 | Scheme | 2022-08-03 13:34 | FRA_4414030820221058.pdf | ComleyB | 4414030820221050 | Retirement Housing | Mid South | East and West Sussex | South | South Patch 5 | zhapdfnoztl6diultz | Low Risk closed | Risk Closed | 44805.3818 | Obs15 | Management Of Fire Safety | 45507 | Low | Court Manager | Fire Safety Training Records sheet to be completed and placed in fire safety management folder | completed
4415 | Monaveen | MONAVEEN_S001 | H21 | Scheme | 2022-05-20 13:36 | FRA_4415200520221006.pdf | ComleyB | 4415200520221000 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | vtkwo198ybsl3eeenem | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45432 | Low | Court Manager | Flat 19 front door not fully closing, keep to be eased and adjusted and door mat removed from corridor. | NULL
4415 | Monaveen | MONAVEEN_S001 | H21 | Scheme | 2022-05-20 13:36 | FRA_4415200520221006.pdf | ComleyB | 4415200520221000 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | d11nmgeoampl3ee3obr | Medium Risk Overdue | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44702 | Medium | Development | Rear fire exit door not opening or closing. Due to be completed by Highwood prior to handover. | NULL
4415 | Monaveen | MONAVEEN_S001 | H21 | Scheme | 2022-05-20 13:36 | FRA_4415200520221006.pdf | ComleyB | 4415200520221000 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | 8i4lorhfkybl3eex8z2 | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45432 | Low | Court Manager | Door mat to be removed from front of flat 44 | NULL
4415 | Monaveen | MONAVEEN_S001 | H21 | Scheme | 2022-05-20 13:36 | FRA_4415200520221006.pdf | ComleyB | 4415200520221000 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | 9lbos18bvjl3eem8be | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45067 | Low | Development | Fire exit sign to be moved and direct downstairs | NULL
4415 | Monaveen | MONAVEEN_S001 | H21 | Scheme | 2022-05-20 13:36 | FRA_4415200520221006.pdf | ComleyB | 4415200520221000 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | bfef5w4hvlrl3eeoa72 | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45432 | Low | Court Manager | Fire exit sign to be installed to direct through door | NULL
4415 | Monaveen | MONAVEEN_S001 | H21 | Scheme | 2022-05-20 13:36 | FRA_4415200520221006.pdf | ComleyB | 4415200520221000 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | 129shdqghil3ee6ytq | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45432 | Low | Court Manager | Fire exit Sign to direct downstairs | NULL
4415 | Monaveen | MONAVEEN_S001 | H21 | Scheme | 2022-05-20 13:36 | FRA_4415200520221006.pdf | ComleyB | 4415200520221000 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | 6vxd4uvcrpnl3eezxhy | Medium Risk to be actioned | Risk Open | NULL | Obs1 | The Building | 45066 | Medium | Court Manager | Evidence of smoking on timber decking of guest room visitors and guests to be advised of smoking policy. | NULL
4415 | Monaveen | MONAVEEN_S001 | H21 | Scheme | 2022-05-20 13:36 | FRA_4415200520221006.pdf | ComleyB | 4415200520221000 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | 4dprsppiogsl3efa01e | Low Risk to be actioned | Risk Open | NULL | Obs9 | Escape Lighting | 45432 | Low | Court Manager | Emergency light timer to be adjusted to provide adequate lighting for sufficient time. 2nd floor meter cupboard. | NULL
4415 | Monaveen | MONAVEEN_S001 | H21 | Scheme | 2022-05-20 13:36 | FRA_4415200520221006.pdf | ComleyB | 4415200520221000 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | 5s2mw86lfabl3eery0k | Medium Risk to be actioned | Risk Open | NULL | Obs1 | The Building | 45066 | Medium | Development | Firesock not installed correctly to 2nd floor meter cupboard | NULL
4415 | Monaveen | MONAVEEN_S001 | H21 | Scheme | 2022-05-20 13:36 | FRA_4415200520221006.pdf | ComleyB | 4415200520221000 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | u0c3mlrbgdrl3edbfma | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45432 | Low | Court Manager | Flat 16 front door not fully closing. Keep to be adjusted | NULL
4415 | Monaveen | MONAVEEN_S001 | H21 | Scheme | 2022-05-20 13:36 | FRA_4415200520221006.pdf | ComleyB | 4415200520221000 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | toic7wygzol3e9fede | Low Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45432 | Low | Court Manager | Court manager to complete Fire Safety training and record in court fire management folder (section 9). Dates to be included on record sheet for other employees. | NULL
4415 | Monaveen | MONAVEEN_S001 | H21 | Scheme | 2022-05-20 13:36 | FRA_4415200520221006.pdf | ComleyB | 4415200520221000 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | qbcgv9z861hl3ef6kkd | Medium Risk Overdue | Risk Open | NULL | Obs1 | The Building | 44702 | Medium | Development | Confirm water meter cupboard is compartmentised with roof structure. Plaster board joins have been sealed but still gaps and only single layer of Plaster board. Ceiling not fully Fire stopped. | NULL
4415 | Monaveen | MONAVEEN_S001 | H21 | Scheme | 2022-05-20 13:36 | FRA_4415200520221006.pdf | ComleyB | 4415200520221000 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | q72q8bbouw8l3eejtz1 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45432 | Low | Court Manager | Flat 21 fŕont door not automatically closing. Door closure to be 'reconnected | NULL
4415 | Monaveen | MONAVEEN_S001 | H21 | Scheme | 2022-05-20 13:36 | FRA_4415200520221006.pdf | ComleyB | 4415200520221000 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | q4o64wvxqgql3ef3y1s | Medium Risk Overdue | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44702 | Medium | Development | Ventilation still not installed to 2nd floor server cupboard. Cupboard very hot and server risk of overheating. | NULL
4415 | Monaveen | MONAVEEN_S001 | H21 | Scheme | 2022-05-20 13:36 | FRA_4415200520221006.pdf | ComleyB | 4415200520221000 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | qewyd412ixrl3ed61ya | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45432 | Low | Court Manager | Mobility scooter chargers to be PAT tested | NULL
4415 | Monaveen | MONAVEEN_S001 | H21 | Scheme | 2022-05-20 13:36 | FRA_4415200520221006.pdf | ComleyB | 4415200520221000 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | qr9pza8p2xgl3edwdko | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45432 | Low | Court Manager | Flat 5 front door to be eased and adjusted | NULL
4415 | Monaveen | MONAVEEN_S001 | H21 | Scheme | 2022-05-20 13:36 | FRA_4415200520221006.pdf | ComleyB | 4415200520221000 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | p48bnscakd9l3ee8gbq | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45066 | Medium | Court Manager | Mobility to be stored in flat or communal store, not in corridor. | NULL
4415 | Monaveen | MONAVEEN_S001 | H21 | Scheme | 2022-05-20 13:36 | FRA_4415200520221006.pdf | ComleyB | 4415200520221000 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | hbhl76x17p6l3ed4moi | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45432 | Low | Court Manager | Boxes and pallet to be removed from mobility scooter store | NULL
4415 | Monaveen | MONAVEEN_S001 | H21 | Scheme | 2022-05-20 13:36 | FRA_4415200520221006.pdf | ComleyB | 4415200520221000 | Extra Care | Extra Care South | EC South 4 | South | South Patch 5 | m9ewuwihq5pl3eetqiw | Medium Risk to be actioned | Risk Open | NULL | Obs1 | The Building | 45066 | Medium | Development | Development to confirm 2nd floor meter cupboard is compartmentation includes roof. Single layer plaster board and exposed roof plate. | NULL
4502 | Lane Fox Court | LANEFOX_S001 | H21 | Scheme | 2022-01-10 14:10 | FRA_4502100120221409.pdf | lofthousei | 4502100120221400 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 4 | ka6d8t3ys8ky8rhec1 | Low Risk closed | Risk Closed | 44572.344 | Obs8 | Measures To Limit Fire Spread And Development | 45301 | Low | Court Manager | Smoke brush seal to flat 6 is damaged, replace or repair | Repaired
4502 | Lane Fox Court | LANEFOX_S001 | H21 | Scheme | 2022-01-10 14:10 | FRA_4502100120221409.pdf | lofthousei | 4502100120221400 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 4 | f6do9qyvqafky8rheba | Observation Only | Risk Closed | 44572.337 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | Flat 4, deaf. Measures in place. | Person centred fire risk assessment held in fire box
4503 | Mowat Court | MOWAT_S001 | H21 | Scheme | 2022-10-18 18:37 | FRA_4503181020221833.pdf | spencem | 4503181020221830 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 5 | dijjxw1fpqul9ehi9os | Medium Risk closed | Risk Closed | 44874.5294 | Obs7 | Fire Protection Measures | 44852 | Medium | Court Manager | Accumulation of residents belongings in many stairwells may impede escape or assistance. | Letter to tenants, newsletter. Removed items
4503 | Mowat Court | MOWAT_S001 | H21 | Scheme | 2022-10-18 18:37 | FRA_4503181020221833.pdf | spencem | 4503181020221830 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 5 | 4741n6o94pel9ehi9pl | Low Risk closed | Risk Closed | 44861.4313 | Obs8 | Measures To Limit Fire Spread And Development | 45583 | Low | Court Manager | Signs and notices that are not directly related to fire safety should be removed from fire exits and circulation doors. "Fire Door Keep Locked Shut" or Fire Door Keep Clear" Signs should be fitted and be clearly visible. Glazing / 'field of vision' should also be unobstructed. | Removed all old signage
4503 | Mowat Court | MOWAT_S001 | H21 | Scheme | 2022-10-18 18:37 | FRA_4503181020221833.pdf | spencem | 4503181020221830 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 5 | l718uf0fz0kl9ehi9q0 | Observation Only | Risk Closed | 44858.4006 | Obs9 | Escape Lighting | NULL | N/A | Surveyor | LED Emergency lighting has been installed in the shared stairwells since the last fire risk assessment. | Observation Only
4503 | Mowat Court | MOWAT_S001 | H21 | Scheme | 2022-10-18 18:37 | FRA_4503181020221833.pdf | spencem | 4503181020221830 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 5 | mtuc0lhexoml9ehi9nt | Low Risk closed | Risk Closed | 44910.3604 | Obs5 | Evacuation Strategy And Training | 45583 | Low | Court Manager | The key for the red fire box should be located in a break glass key box holder. | O Haras to fix a KB2 Key box Break glass
4503 | Mowat Court | MOWAT_S001 | H21 | Scheme | 2022-10-18 18:37 | FRA_4503181020221833.pdf | spencem | 4503181020221830 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 5 | j7x79jkp6yl9ehi9qa | Low Risk closed | Risk Closed | 44874.5287 | Obs9 | Escape Lighting | 45583 | Low | Court Manager | An emergency light / directional legend in the communal hallway is showing fault. (Red LED) | Now working 're checked all ok
4503 | Mowat Court | MOWAT_S001 | H21 | Scheme | 2022-10-18 18:37 | FRA_4503181020221833.pdf | spencem | 4503181020221830 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 5 | nq8jms81smbl9ehi9p8 | Medium Risk closed | Risk Closed | 44861.4329 | Obs8 | Measures To Limit Fire Spread And Development | 45217 | Medium | Court Manager | Doors on escape routes should be kept shut or kept locked shut when not in use.The cupboard containing the communal electrical distrbution board was unlocked during the inspection. | It was opened for access to the fuse board as electrician had to fix plug in the laundry. I was covering another scheme. Now locked
4503 | Mowat Court | MOWAT_S001 | H21 | Scheme | 2022-10-18 18:37 | FRA_4503181020221833.pdf | spencem | 4503181020221830 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 5 | tm858bud1ifl9ehi9og | Medium Risk closed | Risk Closed | 44861.435 | Obs6 | Fire Hazards - Elimination & Control | 45217 | Medium | Court Manager | Combustible materials must not be stored in the vacinity of the electrical distribution boards. | Clearing out the cupboard, we did have the bird seed there now moved to the garage.
4503 | Mowat Court | MOWAT_S001 | H21 | Scheme | 2022-10-18 18:37 | FRA_4503181020221833.pdf | spencem | 4503181020221830 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 5 | tyeqxehww48l9ehi9qo | Low Risk closed | Risk Closed | 44867.617 | Obs10 | Fire Safety And Notices | 45217 | Low | Court Manager | Sings and notices should be relevanat to the location and not excessive for the complexity of the building. Remove unnesscessary signs and notices and make good. For instance, "Fire Door Keep Clear" signs should be mounted externally, when the door opens outwards, and there is a risk of obstruction by a third party. | All done
4503 | Mowat Court | MOWAT_S001 | H21 | Scheme | 2022-10-18 18:37 | FRA_4503181020221833.pdf | spencem | 4503181020221830 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 5 | vffwptmnrmnl9ehi9o7 | Medium Risk closed | Risk Closed | 44861.4335 | Obs6 | Fire Hazards - Elimination & Control | 45217 | Medium | Court Manager | Bins are stored in a locked protected enclosure but some are stored against the building. Bins should not be in direct contact with the building. If they are susceptible to being moved they should be secured in place with a lock and chain. | Will monitor and move when necessary
4503 | Mowat Court | MOWAT_S001 | H21 | Scheme | 2022-10-18 18:37 | FRA_4503181020221833.pdf | spencem | 4503181020221830 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 5 | xlhr90o90apl9ehi9n9 | Medium Risk Overdue | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | 44852 | Medium | Surveyor | There is limited Part 6 detection in each flat providing coverage in the hallway of each property and in the roof voids. The sleeping accommodation is off the lounge in some properties. Recommend that a new Grade D1/2 Category LD1 system be extended to the lounge and kitchen of the dwelling. | NULL
4505 | Turnbull Court | TURNBULL_S001 | H21 | Scheme | 2022-01-05 13:16 | FRA_4505050120220939.pdf | lofthousei | 4505050120220930 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 4 | miih10s8pqrky1esg6k | Low Risk closed | Risk Closed | 44573.3312 | Obs8 | Measures To Limit Fire Spread And Development | 45296 | Low | Court Manager | Cross corridor Fire Door adjacent to Flat 14, intumescent strip loose - requires gluing in place. | Action completed, strip glued
4505 | Turnbull Court | TURNBULL_S001 | H21 | Scheme | 2022-01-05 13:16 | FRA_4505050120220939.pdf | lofthousei | 4505050120220930 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 4 | jiajfk8zvtgky1dhcbu | Low Risk to be actioned | Risk Open | NULL | Obs9 | Escape Lighting | 45296 | Low | M&E Team | High percentage of failing fittings, service contractor advising full replacement | NULL
4506 | Kipling Court 1 | KIPLING1_S001 | H21 | Scheme | 2022-07-15 11:50 | FRA_4506150720221126.pdf | PriestleyC | 4506150720221120 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 10 | fxv2gt3c78ul5mbsdrx | Medium Risk closed | Risk Closed | 44761.6032 | Obs8 | Measures To Limit Fire Spread And Development | 45122 | Medium | Court Manager | Flat 28 door needs easing | Order raised 1550893 O'Hara appointed - 28-day request
4506 | Kipling Court 1 | KIPLING1_S001 | H21 | Scheme | 2022-07-15 11:50 | FRA_4506150720221126.pdf | PriestleyC | 4506150720221120 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 10 | sbwg05oepnl5mbqof7 | Medium Risk closed | Risk Closed | 44761.6029 | Obs8 | Measures To Limit Fire Spread And Development | 45122 | Medium | Court Manager | No door closer on flat 6 | Order raised 1550891 O'Hara appointed - 28-day request
4506 | Kipling Court 1 | KIPLING1_S001 | H21 | Scheme | 2022-07-15 11:50 | FRA_4506150720221126.pdf | PriestleyC | 4506150720221120 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 10 | 6lsbrcaodo8l5mbrni8 | Medium Risk closed | Risk Closed | 44777.4795 | Obs8 | Measures To Limit Fire Spread And Development | 45122 | Medium | Court Manager | Flat 8 door won't close due to brush strip | I have attend removed draught excluder and refitted higher, door tested 5-times closed perfectly, no issues.
4506 | Kipling Court 1 | KIPLING1_S001 | H21 | Scheme | 2022-07-15 11:50 | FRA_4506150720221126.pdf | PriestleyC | 4506150720221120 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 10 | ffacesnyhwl5mc06l7 | Low Risk closed | Risk Closed | 44761.6034 | Obs7 | Fire Protection Measures | 45488 | Low | Court Manager | Extend step from rear of block and lift and relay uneven flags | Order raised 1550890 O'Hara appointed - 28-day request
4507 | St Oswald Court | STOSWALD_S001 | H21 | Scheme | 2022-10-17 10:19 | FRA_4507171020221004.pdf | lofthousei | 4507171020221000 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 10 | q6oqokmw2ikl9ckajyf | Low Risk closed | Risk Closed | 44889.5655 | Obs7 | Fire Protection Measures | 45582 | Low | Court Manager | Fire Exit doors: by Flat 10, Flat 11 & Flat 5 self closers are affecting ease of opening doors - adjust self closers to reduce resistance. | Esker have attended and fixed all the doors as per instruction
4507 | St Oswald Court | STOSWALD_S001 | H21 | Scheme | 2022-10-17 10:19 | FRA_4507171020221004.pdf | lofthousei | 4507171020221000 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 10 | kc3a7qfc2al9ck18v5 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45219 | Low | Surveyor | Fire Exit door to stairwell adjacent to laundry: door blade catching on frame (on leading edge) adjust hinges to allow unhindered closing. | NULL
4507 | St Oswald Court | STOSWALD_S001 | H21 | Scheme | 2022-10-17 10:19 | FRA_4507171020221004.pdf | lofthousei | 4507171020221000 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 10 | mq6zi35bc3l9ck758s | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45216 | Medium | Surveyor | Fire Exit door adjacent to Flat 1, hinge fixings appear damaged making door extremely difficult to operate. Recommend door and frame are replaced. | NULL
4508 | Croft Foulds Court | CROFTFOUL_S001 | H21 | Scheme | 2022-01-21 14:37 | FRA_4508210120221436.pdf | lofthousei | 4508210120221430 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 4 | mkmha6n43ukyoiawiy | Observation Only | Risk Closed | 44582.6163 | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | Court Manager is aware that a number incidents in flats are occurring but call challenged by Careline so no alarm raised. | Fire alarm is not fully activated. Smoke alarms go in flats occasionally and appello answer and give advice regarding clearing smoke so no alarm is activated.
4508 | Croft Foulds Court | CROFTFOUL_S001 | H21 | Scheme | 2022-01-21 14:37 | FRA_4508210120221436.pdf | lofthousei | 4508210120221430 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 4 | jx2ouxnabq9kyoiawg2 | Low Risk closed | Risk Closed | 44582.6142 | Obs4 | The Occupant - Information Provided By The Court Manager | 45312 | Low | Court Manager | PCFRA's all due for review. No high risks identified on previous assessments. | Updated all the PCFRA'S today.
4508 | Croft Foulds Court | CROFTFOUL_S001 | H21 | Scheme | 2022-01-21 14:37 | FRA_4508210120221436.pdf | lofthousei | 4508210120221430 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 4 | y147w57x1vqkyoiawi9 | Observation Only | Risk Closed | 44582.6222 | Obs14 | Access By Emergency Services | NULL | N/A | Other | Fire fighting vehicles have direct access to front of building, but limited indirect access to rear parts. | Discussed with surveyor and this is an observation only
4508 | Croft Foulds Court | CROFTFOUL_S001 | H21 | Scheme | 2022-01-21 14:37 | FRA_4508210120221436.pdf | lofthousei | 4508210120221430 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 4 | vy0pw7jt6rmkyoiawhd | Observation Only | Risk Open | NULL | Obs9 | Escape Lighting | NULL | N/A | Surveyor | Corridor lighting in poor condition but serviceable, consider upgrade | NULL
4509 | Charles Jones Court | CHARLESJONE_S001 | H21 | Scheme | 2022-03-10 15:31 | FRA_4509100320221510.pdf | spencem | 4509100320221510 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 5 | vcvc8vkgyszl0l4n1gg | Low Risk closed | Risk Closed | 44643.5993 | Obs8 | Measures To Limit Fire Spread And Development | 45361 | Low | Court Manager | Flat 78 - Repair required to casing where Perko Doors closer removed. Infill intumescent strip between hinges. | Works completed 23.03.22
4509 | Charles Jones Court | CHARLESJONE_S001 | H21 | Scheme | 2022-03-10 15:31 | FRA_4509100320221510.pdf | spencem | 4509100320221510 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 5 | v3qnw6urmj2l0l4n1gz | Low Risk closed | Risk Closed | 44643.6 | Obs8 | Measures To Limit Fire Spread And Development | 45361 | Low | Court Manager | Flat 74 - significant gap underneath of door. Install Lorient drop seal to base of door to eliminate gap. | Works completed 23.03.22
4509 | Charles Jones Court | CHARLESJONE_S001 | H21 | Scheme | 2022-03-10 15:31 | FRA_4509100320221510.pdf | spencem | 4509100320221510 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 5 | x9y9m9bg2q8l0l4n1i4 | Low Risk closed | Risk Closed | 44680.4024 | Obs10 | Fire Safety And Notices | 45361 | Low | Court Manager | New fire action notices to be installed to 2nd block stairwells. 2 Fire action notices need assembly point completing. | All 7 stairwells on Cat 1 blocks have new signs
4509 | Charles Jones Court | CHARLESJONE_S001 | H21 | Scheme | 2022-03-10 15:31 | FRA_4509100320221510.pdf | spencem | 4509100320221510 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 5 | ys7pfn9q6qll0l4v4p7 | Low Risk closed | Risk Closed | 44680.402 | Obs7 | Fire Protection Measures | 45361 | Low | Court Manager | On inspection of the Residential doors it is apparent that repairs have not been carried out to the door edges where modifications have taken place. Intumescent strips should be continuous between hinges and door and frames made good where equipment has been removed. Gaps under doors should be approximately 4-6 mm maximum. | 15 doors have been attended to with required repair 28.04.22
4509 | Charles Jones Court | CHARLESJONE_S001 | H21 | Scheme | 2022-03-10 15:31 | FRA_4509100320221510.pdf | spencem | 4509100320221510 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 5 | kvxtkx71xsel0l4n1ho | Low Risk closed | Risk Closed | 44643.5989 | Obs8 | Measures To Limit Fire Spread And Development | 45361 | Low | Court Manager | Flat 11 - Adjust door closer to allow door to latch correctly | Works completed 23.03.22
4509 | Charles Jones Court | CHARLESJONE_S001 | H21 | Scheme | 2022-03-10 15:31 | FRA_4509100320221510.pdf | spencem | 4509100320221510 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 5 | sae2wfv2h5cl0l4n1fl | Medium Risk closed | Risk Closed | 44663.3736 | Obs6 | Fire Hazards - Elimination & Control | 44639 | Medium | Court Manager | Combustible materials (Wood, sofa) located close to the fabric of the building. | All items have been booked in for collection with Local Authority and removed. Residents are reminded frequently that bulky items should be removed as soon as possible
4509 | Charles Jones Court | CHARLESJONE_S001 | H21 | Scheme | 2022-03-10 15:31 | FRA_4509100320221510.pdf | spencem | 4509100320221510 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 5 | dye6xym4fyhl0l4n1hc | Low Risk closed | Risk Closed | 44643.5997 | Obs8 | Measures To Limit Fire Spread And Development | 45361 | Low | Court Manager | Flat 15 - Adjust door closer to allow door to latch correctly | Works completed 23.03.22
4509 | Charles Jones Court | CHARLESJONE_S001 | H21 | Scheme | 2022-03-10 15:31 | FRA_4509100320221510.pdf | spencem | 4509100320221510 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 5 | bnams1ixg0al0l4narx | Low Risk closed | Risk Closed | 44643.3703 | Obs10 | Fire Safety And Notices | 45361 | Low | Court Manager | Fire Action Notices should be filled in with the assembly point location. | Completed
4509 | Charles Jones Court | CHARLESJONE_S001 | H21 | Scheme | 2022-03-10 15:31 | FRA_4509100320221510.pdf | spencem | 4509100320221510 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 5 | 362pqit4tj2l0l4r3bc | Low Risk closed | Risk Closed | 44753.6235 | Obs7 | Fire Protection Measures | 45361 | Low | Court Manager | Locked external boundary gate on escape route - Keyless egress should be provided or alternative arrangement made to allow egress to a place of safety. | Discussed with Technical Surveyor 're access to the garden to the right in the event of evacuation, rather than change the lock on the gate. To be reviewed
4510 | Ward Court | WARD_B001 | H21 | Unknown | 2019-12-23 15:21 | FRA_451023122019.pdf | SpenceM | 451023122019 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | 32gtiuheadzk4ikorab | Low Risk closed | Risk Closed | 43885.5053 | Obs10 | Fire Safety And Notices | 44553 | Low | Court Manager | Do not use lift signs should be placed outside lift on all floors | Contractor contacted
4510 | Ward Court | WARD_B001 | H21 | Unknown | 2019-12-23 15:21 | FRA_451023122019.pdf | SpenceM | 451023122019 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | 3u0sygm8ji3k4ikor5m | Medium Risk Overdue | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44188 | Medium | Development | Fire stopping required to cable penetration made for car charging point cable in electricity room. | NULL
4510 | Ward Court | WARD_S001 | H21 | Scheme | 2022-10-27 12:27 | FRA_4510271020221147.pdf | SpenceM | 4510271020221140 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | 2ntxqqbdb9yl9qxz4s1 | Low Risk closed | Risk Closed | 44901.4262 | Obs11 | Fire Fighting Equipment | 45592 | Low | Court Manager | Fire extinguisher missing within the laundry. Needs to be one present due to being a high risk room. | fire extinguisher put in room
4510 | Ward Court | WARD_B001 | H21 | Unknown | 2019-12-23 15:21 | FRA_451023122019.pdf | SpenceM | 451023122019 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | 1rildm30iaok4ikor0d | Observation Only | Risk Open | NULL | Obs1 | The Building | NULL | N/A | Other | The roof void space above the common corridor has been fitted with smoke detection and a new zoned alarm system has been installed since the last inspection. | NULL
4510 | Ward Court | WARD_S001 | H21 | Scheme | 2022-10-27 12:27 | FRA_4510271020221147.pdf | SpenceM | 4510271020221140 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | 004sekh1ut14ql9qxz4q0 | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45241 | Low | Court Manager | Fire action notices to have assembly point filled out in all locations. | NULL
4510 | Ward Court | WARD_S001 | H21 | Scheme | 2022-10-27 12:27 | FRA_4510271020221147.pdf | SpenceM | 4510271020221140 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | 3yeyqnl754el9qxz4lc | High Risk Closed | Risk Closed | 44874.616 | Obs6 | Fire Hazards - Elimination & Control | 44953 | High | Court Manager | Combustible materials e.g. wallpaper up against Apello servo box with grills covered and emitting excessive heat. | Items removed
4510 | Ward Court | WARD_B001 | H21 | Unknown | 2019-12-23 15:21 | FRA_451023122019.pdf | SpenceM | 451023122019 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | 43w2n1pzc2hk4ikorb6 | Low Risk closed | Risk Closed | 43885.5055 | Obs10 | Fire Safety And Notices | 44553 | Low | Court Manager | Add assembly point location to fire action notices throughout the site | Completed
4510 | Ward Court | WARD_B001 | H21 | Unknown | 2019-12-23 15:21 | FRA_451023122019.pdf | SpenceM | 451023122019 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | 54nstfl9buhk4ikorty | Low Risk closed | Risk Closed | 43885.5028 | Obs16 | Testing And Maintenance | 44553 | Low | Court Manager | A number or pieces of equipment in the boiler house require maintenance. | GOS completed the works required
4510 | Ward Court | WARD_S001 | H21 | Scheme | 2022-10-27 12:27 | FRA_4510271020221147.pdf | SpenceM | 4510271020221140 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | 50hx3xju29ml9qxz4je | Low Risk closed | Risk Closed | 44901.4251 | Obs6 | Fire Hazards - Elimination & Control | 45592 | Low | Court Manager | Excessive items within communal store cupboards and doors not locked shut. | excess items removed and doors locked
4510 | Ward Court | WARD_B001 | H21 | Unknown | 2019-12-23 15:21 | FRA_451023122019.pdf | SpenceM | 451023122019 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | 57q1i646gzwk4ikorct | Low Risk closed | Risk Closed | 43885.5023 | Obs10 | Fire Safety And Notices | 44553 | Low | Court Manager | The boiler house door should be fitted with warning notices and authorised personell access only. | Contractor contacted
4510 | Ward Court | WARD_B001 | H21 | Unknown | 2019-12-23 15:21 | FRA_451023122019.pdf | SpenceM | 451023122019 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | adrtyjyxq3ik4ikor82 | Medium Risk Overdue | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44188 | Medium | Surveyor | The roof compartmentation is sub divided into flats but doesnt follow the line of the stairs or intermediate corridor door. Recommend extending compartment walls to above mid and end corridor doors at first floor level. | NULL
4510 | Ward Court | WARD_B001 | H21 | Unknown | 2019-12-23 15:21 | FRA_451023122019.pdf | SpenceM | 451023122019 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | aahkz0u73ahk4ikor6u | Medium Risk closed | Risk Closed | 43885.5059 | Obs8 | Measures To Limit Fire Spread And Development | 44188 | Medium | Court Manager | Communal loft hatches should be upgraded to resist fire and smoke and be lockable | Contractor contacted
4510 | Ward Court | WARD_B001 | H21 | Unknown | 2019-12-23 15:21 | FRA_451023122019.pdf | SpenceM | 451023122019 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | dm9rqxkpx2dk4ikorc0 | Low Risk closed | Risk Closed | 43885.5014 | Obs10 | Fire Safety And Notices | 44553 | Low | Court Manager | Fire directional signs throughout the court should be reviewed. Signs should be relevant to the location. | Contacted contractor to put New signs up
4510 | Ward Court | WARD_B001 | H21 | Unknown | 2019-12-23 15:21 | FRA_451023122019.pdf | SpenceM | 451023122019 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | czla40wdrepk4ikor3v | Low Risk closed | Risk Closed | 43885.5049 | Obs6 | Fire Hazards - Elimination & Control | 44553 | Low | Court Manager | Boxes blocking air vents to server cabinet. Removed during inspection reduced to Low Risk. | Area kept clear at all times
4510 | Ward Court | WARD_B001 | H21 | Unknown | 2019-12-23 15:21 | FRA_451023122019.pdf | SpenceM | 451023122019 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | s88yrwqgeak4ikorfm | Low Risk closed | Risk Closed | 43885.5018 | Obs15 | Management Of Fire Safety | 44553 | Low | Court Manager | The red fire box should be fixed to wall in reception in an accesible and signed location. | Contractor contacted to do job
4510 | Ward Court | WARD_B001 | H21 | Unknown | 2019-12-23 15:21 | FRA_451023122019.pdf | SpenceM | 451023122019 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | tfnekew0a3k4ikppie | Low Risk Overdue | Risk Open | NULL | Obs16 | Testing And Maintenance | 44553 | Low | M&E Team | The fire extinguisher in the boiler house should be changed for a F50 type extinguisher. | NULL
4510 | Ward Court | WARD_S001 | H21 | Scheme | 2022-10-27 12:27 | FRA_4510271020221147.pdf | SpenceM | 4510271020221140 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | p51ldk3ph7dl9qxz4nq | Medium Risk closed | Risk Closed | 44901.4217 | Obs8 | Measures To Limit Fire Spread And Development | 45226 | Medium | Court Manager | Flat front door no 5 and no 9 require minor works to ensure doors close fully. | joinery adjusted the doors
4510 | Ward Court | WARD_B001 | H21 | Unknown | 2019-12-23 15:21 | FRA_451023122019.pdf | SpenceM | 451023122019 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | o6bnap0rs9gk4ikor1r | Medium Risk closed | Risk Closed | 43885.5046 | Obs1 | The Building | 44188 | Medium | Court Manager | Recommend that the corridor loft hatches are upgraded to 30 minutes fire resistance and are locked down with a key and that a 30 minute fire resisting barrier is contructed above the mid-corridor compartment door in the roof space. | Contractor contacted
4510 | Ward Court | WARD_S001 | H21 | Scheme | 2022-10-27 12:27 | FRA_4510271020221147.pdf | SpenceM | 4510271020221140 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | mhd0rynf9l9qxz4t4 | Medium Risk closed | Risk Closed | 44901.42 | Obs15 | Management Of Fire Safety | 45226 | Medium | Court Manager | Electric meter room door unlocked needs to be locked at all times. | ensure door locked
4510 | Ward Court | WARD_B001 | H21 | Unknown | 2019-12-23 15:21 | FRA_451023122019.pdf | SpenceM | 451023122019 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | n8rv5zct7sk4ikor9c | Low Risk closed | Risk Closed | 44820.4848 | Obs9 | Escape Lighting | 44553 | Low | Surveyor | The escape and communal lighting has a number of defects reported during the last service. The communal and emergency lighting is due for replacement in April 2020. | Closing risk
4510 | Ward Court | WARD_S001 | H21 | Scheme | 2022-10-27 12:27 | FRA_4510271020221147.pdf | SpenceM | 4510271020221140 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | fuon5kc684ll9qxz4mn | Medium Risk closed | Risk Closed | 44901.4206 | Obs7 | Fire Protection Measures | 45226 | Medium | Court Manager | Laundry fire door was wedged open at time of visit. Automatic door closer to be used to hold door open only. | removed wedge from room
4510 | Ward Court | WARD_S001 | H21 | Scheme | 2022-10-27 12:27 | FRA_4510271020221147.pdf | SpenceM | 4510271020221140 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | j086kyjyq78l9qxz4ib | Medium Risk closed | Risk Closed | 44902.5097 | Obs6 | Fire Hazards - Elimination & Control | 45226 | Medium | Court Manager | Right hand Dryer hose compressed and misaligned from outside vent. Hose to be shortened to correct length and reconected to dryer and vent outlet. | job ordered
4510 | Ward Court | WARD_S001 | H21 | Scheme | 2022-10-27 12:27 | FRA_4510271020221147.pdf | SpenceM | 4510271020221140 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | ytn7cixtlhdl9qxz4qz | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45592 | Low | Court Manager | Instructions for access to be listed on door entry panel for emergency services. | NULL
4510 | Ward Court | WARD_B001 | H21 | Unknown | 2019-12-23 15:21 | FRA_451023122019.pdf | SpenceM | 451023122019 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | yvk8donwphk4ikoreh | Low Risk Overdue | Risk Open | NULL | Obs13 | Other Relevant Fixed Systems | 44553 | Low | Surveyor | Investigate requirement for lift fire interlink cable and connect as found. | NULL
4510 | Ward Court | WARD_S001 | H21 | Scheme | 2022-10-27 12:27 | FRA_4510271020221147.pdf | SpenceM | 4510271020221140 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | xuinebo5dlel9qxz4op | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45592 | Low | Court Manager | First floor cross corridor outside flat 26 and flat 29 doors require easing over carpet. End stairwell ground and first floor internal door also not closing fully. | NULL
4510 | Ward Court | WARD_S001 | H21 | Scheme | 2022-10-27 12:27 | FRA_4510271020221147.pdf | SpenceM | 4510271020221140 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | vk99bxut55l9qxz4kh | Medium Risk closed | Risk Closed | 44901.4265 | Obs6 | Fire Hazards - Elimination & Control | 45226 | Medium | Court Manager | Electric meter room not locked shut and accesible to residents. | door locked
4511 | Stanley Cryer Court | STANLEYCRYE_S001 | H21 | Scheme | 2022-02-14 15:11 | FRA_4511140220221247.pdf | PriestleyC | 4511140220221240 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 2 | 7ypcjwodot8kzmp4tz9 | Low Risk closed | Risk Closed | 44622.4725 | Obs8 | Measures To Limit Fire Spread And Development | 45336 | Low | Court Manager | No smoke seal on inside of letter box - flat 23 | Letterbox complete replaced on 2nd March 2022
4512 | Charlesworth Court | CHARLESWORTH_S001 | H21 | Scheme | 2021-12-13 08:34 | FRA_4512131220210750.pdf | spencem | 4512131220210750 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 5 | wjq76td3q58kx4dmadi | Medium Risk closed | Risk Closed | 44560.6151 | Obs8 | Measures To Limit Fire Spread And Development | 44908 | Medium | Court Manager | Flat 143 door closer arm is missing and needs a repair or replacement. | Door closer already installed on the inside of of flat on fire door complete with arm.
4513 | Merlin Court | MERLIN_S001 | H21 | Scheme | 2022-02-21 11:38 | FRA_4513210220220922.pdf | PriestleyC | 4513210220220920 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 2 | wftt5tww3cjkzwjrnoy | Low Risk closed | Risk Closed | 44686.5402 | Obs4 | The Occupant - Information Provided By The Court Manager | 45343 | Low | Court Manager | PCFRA's need updating | All complete
4513 | Merlin Court | MERLIN_S001 | H21 | Scheme | 2022-02-21 11:38 | FRA_4513210220220922.pdf | PriestleyC | 4513210220220920 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 2 | vre5ksz1qlkzwlwkdj | Low Risk closed | Risk Closed | 44635.6034 | Obs8 | Measures To Limit Fire Spread And Development | 45343 | Low | Court Manager | Adjust closer on flat 47 | Closer adjusted
4513 | Merlin Court | MERLIN_S001 | H21 | Scheme | 2022-02-21 11:38 | FRA_4513210220220922.pdf | PriestleyC | 4513210220220920 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 2 | zzcvdnaakekzwkfqq5 | Low Risk closed | Risk Closed | 44614.4537 | Obs6 | Fire Hazards - Elimination & Control | 45343 | Low | Court Manager | items in salon not PAT tested | These items are new and were not in salon when pat testing took place in Jan 2021 they will be included in next pat testing
4513 | Merlin Court | MERLIN_S001 | H21 | Scheme | 2022-02-21 11:38 | FRA_4513210220220922.pdf | PriestleyC | 4513210220220920 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 2 | e0d9sbao93kzwk5kru | Low Risk closed | Risk Closed | 44614.4555 | Obs11 | Fire Fighting Equipment | 45343 | Low | Court Manager | Remove old style extinguisher from snooker room | Removed and stored in cms office store cupboard
4513 | Merlin Court | MERLIN_S001 | H21 | Scheme | 2022-02-21 11:38 | FRA_4513210220220922.pdf | PriestleyC | 4513210220220920 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 2 | exwblladobdkzwkzzdz | Low Risk closed | Risk Closed | 44614.4575 | Obs6 | Fire Hazards - Elimination & Control | 45343 | Low | Court Manager | Check PAT testing on mobility scooter chargers | Scooters added after Last pat test in Jan 2021 they will be included in next pat test
4513 | Merlin Court | MERLIN_S001 | H21 | Scheme | 2022-02-21 11:38 | FRA_4513210220220922.pdf | PriestleyC | 4513210220220920 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 2 | 9k296ix4zl8kzwlx3ms | Low Risk closed | Risk Closed | 44635.6036 | Obs8 | Measures To Limit Fire Spread And Development | 45343 | Low | Court Manager | Ease and adjust flat 44 door | Door adjusted
4513 | Merlin Court | MERLIN_S001 | H21 | Scheme | 2022-02-21 11:38 | FRA_4513210220220922.pdf | PriestleyC | 4513210220220920 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 2 | jsq7graub5skzwktzcj | Medium Risk closed | Risk Closed | 44635.6032 | Obs7 | Fire Protection Measures | 44978 | Medium | Court Manager | Check Door into scooter store is fd30 it does not have a closer on | Fitter fit
4515 | Avery Tulip Court | AVERYTULI_S001 | H21 | Scheme | 2022-06-09 10:09 | FRA_4515080620221115.pdf | PriestleyC | 4515080620221110 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | nk1p937ckjsl45h1u8l | Low Risk closed | Risk Closed | 44727.5075 | Obs8 | Measures To Limit Fire Spread And Development | 45451 | Low | Court Manager | Ease and adjust flat 9 & 29 door | All door have been eased
4517 | Wellington Court | WELLINGTON_S001 | H21 | Scheme | 2022-10-27 15:53 | FRA_4517271020221421.pdf | SpenceM | 4517271020221420 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | galghqi7xs9l9r4q8eu | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45592 | Low | Court Manager | Further investigate and fire stop redundant flue within laundry cupboard. | NULL
4517 | Wellington Court | WELLINGTON_S001 | H21 | Scheme | 2022-10-27 15:53 | FRA_4517271020221421.pdf | SpenceM | 4517271020221420 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | 93espiax3rul9r42xv4 | Medium Risk closed | Risk Closed | 44890.4072 | Obs8 | Measures To Limit Fire Spread And Development | 45226 | Medium | Court Manager | No 11 door closer not connected. | H21 - 1574818 - Wellington Court. Saira, The door closer arm has been sorted and the door closer releases when the power switch is turned off. We need to make sure the door closes when the fire alarm activated - this is not something I can test. The next time you do your fire alarm test if you ask the tenant to open his door and then ask him if it closed when the alarm goes off Kind Regards, Philip Electrician at PLB Services CM completed fire test, the door when opened shuts when fire test initiated.
4517 | Wellington Court | WELLINGTON_S001 | H21 | Scheme | 2022-10-27 15:53 | FRA_4517271020221421.pdf | SpenceM | 4517271020221420 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | a716u117f0dl9r4kqng | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45226 | Medium | Court Manager | Outside dryer vent blocked up with excessive dust requires regular cleaning. | NULL
4517 | Wellington Court | WELLINGTON_S001 | H21 | Scheme | 2022-10-27 15:53 | FRA_4517271020221421.pdf | SpenceM | 4517271020221420 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | wfvhyk4e6mql9r3gris | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45226 | Medium | Surveyor | Currently lounge fire escape door is inward opening which is incorrect and awaiting replacement following being incorrect installed as part of a SIP project. | NULL
4520 | Elm Tree Court | ELMTREE_S001 | H21 | Scheme | 2022-05-31 15:06 | FRA_4520310520221442.pdf | spencem | 4520310520221440 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | ur2kppzi9v2l3u7m4wj | Medium Risk closed | Risk Closed | 44755.3678 | Obs6 | Fire Hazards - Elimination & Control | 45077 | Medium | Court Manager | The communal kitchen is no longer in use and there is a build up of stored material. Ensure that all electrical appliances and electric heaters are isolated from the electricity supply and to door kept 'locked shut 'when not in use. | All items removed from the kitchen and all appliances switched off.
4520 | Elm Tree Court | ELMTREE_B001 | H21 | Unknown | 2020-07-30 12:40 | FRA_452030072020.pdf | SpenceM | 452030072020 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | zvktcd7pq6kd8n5mhs | Low Risk closed | Risk Closed | 44046.571 | Obs7 | Fire Protection Measures | 44772 | Low | Surveyor | Observation from Type 4 fire risk assessment. Some of the kitchens within the domestic flats do not have detection the ceiling down stand between the lounge and kitchen is marginally in excess of 10% of the ceiling height. Ceiling height is 2.4 metres downstand is 300mm. | Not all of the kitchens have excessive down stands, which in most cases is only 30-50mm in excess of the recommendation. The detector in the lounge adjacent is a smoke detector. These devices have activated in the past when a resident has burnt something. It would be uneconomical to install additional detection when the existing detectors have proven to provide adequate cover. Additional detection may also give rise to false alarms therefore no action will be taken at this time and the situation should be monitored.
4520 | Elm Tree Court | ELMTREE_S001 | H21 | Scheme | 2022-05-31 15:06 | FRA_4520310520221442.pdf | spencem | 4520310520221440 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | bbhy0cjqegbl3u7m4yh | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45443 | Low | Court Manager | The nominated point of assembly should be signed with an "Assembly Point" sign and pictogram. | NULL
4520 | Elm Tree Court | ELMTREE_B001 | H21 | Unknown | 2020-07-30 12:40 | FRA_452030072020.pdf | SpenceM | 452030072020 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | b8eol8sa67kd8n5moj | Low Risk closed | Risk Closed | 44103.8545 | Obs10 | Fire Safety And Notices | 44772 | Low | Court Manager | Observation from Type 4 fire risk assessment There are multiple types of fire action notices throughout the building. Replace with standard Housing 21 policy notices. | All signs provided by Martin Spence
4520 | Elm Tree Court | ELMTREE_B001 | H21 | Unknown | 2020-07-30 12:40 | FRA_452030072020.pdf | SpenceM | 452030072020 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | fdwn34lq3kikd8n5mqj | Low Risk closed | Risk Closed | 44046.5717 | Obs11 | Fire Fighting Equipment | 44772 | Low | Surveyor | Observation from Type 4 fire risk assessment Extinguisher s should not be sited in the communal areas this may encourage occupants to enter a dwelling which is on fire without having raised the alarm first. | No action taken. Fire Extinguishers are sited in accordance with the revised Housing 21 policy.
4520 | Elm Tree Court | ELMTREE_B001 | H21 | Unknown | 2020-07-30 12:40 | FRA_452030072020.pdf | SpenceM | 452030072020 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | dhzn0xi84lpkd8od4vl | Medium Risk closed | Risk Closed | 44103.8551 | Obs6 | Fire Hazards - Elimination & Control | 44407 | Medium | Court Manager | Combustible materials stored outside of containers and sited adjacent to electrical equipment within 1.8 m of the building. Resite domestic wheelie bin and remove all excess materials from site. | All bin area cleared and resisted in bin area .
4520 | Elm Tree Court | ELMTREE_B001 | H21 | Unknown | 2020-07-30 12:40 | FRA_452030072020.pdf | SpenceM | 452030072020 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | 5uccssrr9i3kd8n5mk0 | Low Risk closed | Risk Closed | 44230.4456 | Obs8 | Measures To Limit Fire Spread And Development | 44772 | Low | Court Manager | Observation from Type 4 fire risk assessment. The cross corridor adjacent to flat 24 excessive gaps between doors. The cross corridor doors from the lift lobby on the first floor leading to flat 32 has excessive gaps between the doors. On the ground floor the cross corridor doors from the lift lobby leading to the flat has excessive gaps between the doors. The doors to fire exit from the laundry has a key type lock at the time of inspection the door wasn't locked it ideally should be fitted with a thumb turn. There is an excessive gap at the head of the kitchen door. | All doors fixed with oharas and support from Martin spence
4520 | Elm Tree Court | ELMTREE_S001 | H21 | Scheme | 2022-05-31 15:06 | FRA_4520310520221442.pdf | spencem | 4520310520221440 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | 0815s2n6swy6l3u7m4v0 | Low Risk closed | Risk Closed | 44774.7416 | Obs6 | Fire Hazards - Elimination & Control | 45076 | Low | Court Manager | Air handing equipment unit in the rear fenced off enclosure. Clean leaves, debris and saplings from around the unit to avoid blockages and subsequent overheating. | Area cleared.
4520 | Elm Tree Court | ELMTREE_B001 | H21 | Unknown | 2020-07-30 12:40 | FRA_452030072020.pdf | SpenceM | 452030072020 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | jrzuyqx7gmpkd8n5ml7 | Low Risk closed | Risk Closed | 44046.5731 | Obs8 | Measures To Limit Fire Spread And Development | 44772 | Low | Surveyor | Observations from Type 4 fire risk assessment. Various intumescent fire stopping and making good around the building in communal parts loft spaces and ancillary rooms. | Additional fire stopping and remedial works have been carried out in response to the Type 4 FRA observations. A pictorial report and FIRAS certificate has been received for all areas identified.
4520 | Elm Tree Court | ELMTREE_B001 | H21 | Unknown | 2020-07-30 12:40 | FRA_452030072020.pdf | SpenceM | 452030072020 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | mm2yv8ny8yjkd8n5mne | Low Risk closed | Risk Closed | 44103.8543 | Obs10 | Fire Safety And Notices | 44772 | Low | Court Manager | A number of the fire directional signs are either pre-emptive or do not direct occupants to the nearest available exit. Revise signage during redecoration. | Signage to be changed at next redecoration
4520 | Elm Tree Court | ELMTREE_S001 | H21 | Scheme | 2022-05-31 15:06 | FRA_4520310520221442.pdf | spencem | 4520310520221440 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | ll6eynzbsezl3u7m4x4 | Medium Risk closed | Risk Closed | 44755.3682 | Obs6 | Fire Hazards - Elimination & Control | 45077 | Medium | Court Manager | There is a build up of stored materials alongside charging equipment in the buggy store. Efforts should be made to remove or relocate flammable goods from the room. | All items removed from the buggy store room.
4520 | Elm Tree Court | ELMTREE_B001 | H21 | Unknown | 2020-07-30 12:40 | FRA_452030072020.pdf | SpenceM | 452030072020 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | llum8o75hckkd8n5mc7 | Observation Only | Risk Open | NULL | Obs1 | The Building | NULL | N/A | Other | The building has recently undergone a compartment survey and remedial works by a competent FIRRAS registered installer. | NULL
4520 | Elm Tree Court | ELMTREE_B001 | H21 | Unknown | 2020-07-30 12:40 | FRA_452030072020.pdf | SpenceM | 452030072020 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | obhdcir4nfkd8n5mdu | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Other | Example of PCRFA front sheet. Individual documents in file | NULL
4520 | Elm Tree Court | ELMTREE_B001 | H21 | Unknown | 2020-07-30 12:40 | FRA_452030072020.pdf | SpenceM | 452030072020 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | ocbh4aj1kyokd8n5mfu | Observation Only | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | NULL | N/A | Other | Example training record | NULL
4520 | Elm Tree Court | ELMTREE_S001 | H21 | Scheme | 2022-05-31 15:06 | FRA_4520310520221442.pdf | spencem | 4520310520221440 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | os15bk2n6mdl3u7m50d | Low Risk closed | Risk Closed | 44712.6875 | Obs10 | Fire Safety And Notices | 45076 | Low | Court Manager | A number of the fire directional signs are either pre-emptive or do not direct occupants to the nearest available exit. Revise signage during redecoration. | no action required as this has been ongoing for last 3 inspections - Martin to arrange at redecoration.
4521 | Box Tree Court | BOXTREE_S001 | H21 | Scheme | 2022-02-22 13:55 | FRA_4521220220221354.pdf | lofthousei | 4521220220221350 | Extra Care | Extra Care North | EC North 5 | North | North Patch 4 | rnyu4ar10qfkzy6w173 | Low Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45344 | Low | Court Manager | HCM to use Fire Responsibilities Matrix Checklist with Hair Salon and Caterers as appropriate. | NULL
4521 | Box Tree Court | BOXTREE_S001 | H21 | Scheme | 2022-02-22 13:55 | FRA_4521220220221354.pdf | lofthousei | 4521220220221350 | Extra Care | Extra Care North | EC North 5 | North | North Patch 4 | mb9n4hly4egkzy6w15t | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45344 | Low | Court Manager | Evidence of PAT test for scooters required | NULL
4521 | Box Tree Court | BOXTREE_S001 | H21 | Scheme | 2022-02-22 13:55 | FRA_4521220220221354.pdf | lofthousei | 4521220220221350 | Extra Care | Extra Care North | EC North 5 | North | North Patch 4 | 0nbxz7iz4mnakzy6w155 | Low Risk closed | Risk Closed | 44805.6906 | Obs6 | Fire Hazards - Elimination & Control | 45344 | Low | Court Manager | Portable appliance testing will be due by November 2022. HCM to ensure Compliance Team arrange testing | PAT testing to be carried out on 7.9.22
4521 | Box Tree Court | BOXTREE_S001 | H21 | Scheme | 2022-02-22 13:55 | FRA_4521220220221354.pdf | lofthousei | 4521220220221350 | Extra Care | Extra Care North | EC North 5 | North | North Patch 4 | zbsqnkamo4jkzy6w16n | Low Risk closed | Risk Closed | 44804.625 | Obs15 | Management Of Fire Safety | 45344 | Low | Court Manager | Record of false alarms to be kept using ERICA | We record false alarms on Erica
4522 | Lady Ida Lodge | LADYIDALODGE_S001 | H21 | Scheme | 2022-07-21 15:32 | FRA_4522210720221148.pdf | PriestleyC | 4522210720221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 4 | utlcskufdyl5uwuu3i | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45128 | Medium | Development | Excessive gaps on fire compartment doors to stairs (various locations, all need checking) | NULL
4522 | Lady Ida Lodge | LADYIDALODGE_S001 | H21 | Scheme | 2022-07-21 15:32 | FRA_4522210720221148.pdf | PriestleyC | 4522210720221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 4 | uvvopoy80tdl5ux1ngt | Low Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45494 | Low | Court Manager | Update red fire box info | NULL
4522 | Lady Ida Lodge | LADYIDALODGE_S001 | H21 | Scheme | 2022-07-21 15:32 | FRA_4522210720221148.pdf | PriestleyC | 4522210720221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 4 | vcssjkv8m2l5uwuucv | Low Risk to be actioned | Risk Open | NULL | Obs13 | Other Relevant Fixed Systems | 45494 | Low | Court Manager | Check all smoke vents operate. Open/ close facility not working on any openers | NULL
4522 | Lady Ida Lodge | LADYIDALODGE_S001 | H21 | Scheme | 2022-07-21 15:32 | FRA_4522210720221148.pdf | PriestleyC | 4522210720221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 4 | wiz7lhhuvsrl5uz06pt | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45128 | Medium | Development | Various flat doors warped and not fitting correctly | NULL
4522 | Lady Ida Lodge | LADYIDALODGE_S001 | H21 | Scheme | 2022-07-21 15:32 | FRA_4522210720221148.pdf | PriestleyC | 4522210720221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 4 | yqzobg1lfwl5uxmh8f | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45128 | Medium | Court Manager | Door wedged open on flat 29 | NULL
4522 | Lady Ida Lodge | LADYIDALODGE_S001 | H21 | Scheme | 2022-07-21 15:32 | FRA_4522210720221148.pdf | PriestleyC | 4522210720221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 4 | x7os4wdtjddl5uwuu6a | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45128 | Medium | Development | Gaps too large around store door opposite flat 19 | NULL
4522 | Lady Ida Lodge | LADYIDALODGE_S001 | H21 | Scheme | 2022-07-21 15:32 | FRA_4522210720221148.pdf | PriestleyC | 4522210720221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 4 | 2ekrvvjxns3l5v4gumn | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45494 | Low | Development | Fire escape signage in old block too high, not easily visible. | NULL
4522 | Lady Ida Lodge | LADYIDALODGE_S001 | H21 | Scheme | 2022-07-21 15:32 | FRA_4522210720221148.pdf | PriestleyC | 4522210720221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 4 | 3p500pnov9fl5uwuu93 | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45128 | Medium | Court Manager | Cross corridor doors not close properly adj flat 33 and require easing | NULL
4522 | Lady Ida Lodge | LADYIDALODGE_S001 | H21 | Scheme | 2022-07-21 15:32 | FRA_4522210720221148.pdf | PriestleyC | 4522210720221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 4 | 5ibaaqdievhl5uyhjyp | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45494 | Low | Court Manager | Free swing closer does not work on flat 31 (door closer permanently operational) | NULL
4522 | Lady Ida Lodge | LADYIDALODGE_S001 | H21 | Scheme | 2022-07-21 15:32 | FRA_4522210720221148.pdf | PriestleyC | 4522210720221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 4 | 7o6j6niswuol5uwuuau | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45128 | Low | Court Manager | No fire action notice at MCP adj flat 17 | NULL
4522 | Lady Ida Lodge | LADYIDALODGE_S001 | H21 | Scheme | 2022-07-21 15:32 | FRA_4522210720221148.pdf | PriestleyC | 4522210720221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 4 | bnueu335kvcl5uwuu8a | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45128 | Medium | Court Manager | Check if roller shutter linked to fire alarm, catering staff unaware. | NULL
4522 | Lady Ida Lodge | LADYIDALODGE_S001 | H21 | Scheme | 2022-07-21 15:32 | FRA_4522210720221148.pdf | PriestleyC | 4522210720221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 4 | a8p62gub0whl5ux2kro | Low Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45494 | Low | Court Manager | 2 care staff need to complete e-learning | NULL
4522 | Lady Ida Lodge | LADYIDALODGE_S001 | H21 | Scheme | 2022-07-21 15:32 | FRA_4522210720221148.pdf | PriestleyC | 4522210720221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 4 | 9z71xrkk91l5uyorsg | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45128 | Medium | Court Manager | Door closer not connected on flat 61 | NULL
4522 | Lady Ida Lodge | LADYIDALODGE_S001 | H21 | Scheme | 2022-07-21 15:32 | FRA_4522210720221148.pdf | PriestleyC | 4522210720221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 4 | ag5oeta3seql5uwuu7m | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45128 | Medium | Court Manager | Fire door wedged open into kitchen | NULL
4522 | Lady Ida Lodge | LADYIDALODGE_S001 | H21 | Scheme | 2022-07-21 15:32 | FRA_4522210720221148.pdf | PriestleyC | 4522210720221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 4 | 8wigem04e16l5uwuu4d | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45494 | Low | Court Manager | Table on corridor near flat 19 may impede escape route and lamp covers MCP | NULL
4522 | Lady Ida Lodge | LADYIDALODGE_S001 | H21 | Scheme | 2022-07-21 15:32 | FRA_4522210720221148.pdf | PriestleyC | 4522210720221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 4 | n3qs8rhcjg9l5uyuu5i | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45128 | Medium | Development | Gaps round door on flat 56 too big | NULL
4522 | Lady Ida Lodge | LADYIDALODGE_S001 | H21 | Scheme | 2022-07-21 15:32 | FRA_4522210720221148.pdf | PriestleyC | 4522210720221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 4 | gk3418cpgw8l5uwuubp | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45494 | Low | Court Manager | Lift near laundry and flat 30 needs "Do not use in case of fire" sign | NULL
4522 | Lady Ida Lodge | LADYIDALODGE_S001 | H21 | Scheme | 2022-07-21 15:32 | FRA_4522210720221148.pdf | PriestleyC | 4522210720221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 4 | hhq0xcy3qbhl5uwuua6 | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45494 | Low | Court Manager | Lift near laundry and flat 20 and care office needs "Do not use in case of fire" sign | NULL
4522 | Lady Ida Lodge | LADYIDALODGE_S001 | H21 | Scheme | 2022-07-21 15:32 | FRA_4522210720221148.pdf | PriestleyC | 4522210720221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 4 | hxtr98nia46l5uwuu6v | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45128 | Medium | Development | Gaps too large in doors adj care office and from dining room | NULL
4522 | Lady Ida Lodge | LADYIDALODGE_S001 | H21 | Scheme | 2022-07-21 15:32 | FRA_4522210720221148.pdf | PriestleyC | 4522210720221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 4 | tpsyudom8gl5uwuu4x | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45128 | Medium | Development | Dual operation device on Laundry, small lounge, door adj flat 13, main entrance door nr care office, doors nr flat 11, Needs changing to single action e.g. split lever handles and thumb turn removing | NULL
4522 | Lady Ida Lodge | LADYIDALODGE_S001 | H21 | Scheme | 2022-07-21 15:32 | FRA_4522210720221148.pdf | PriestleyC | 4522210720221140 | Extra Care | Extra Care North | EC North 5 | North | North Patch 4 | udpkpdjyzq8l5uwuu5p | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45128 | Medium | Development | Fire stopping around pipes in cupboard opposite flat 19 | NULL
4528 | Kipling Court 2 | KIPLING2_S001 | H21 | Scheme | 2022-07-15 12:05 | FRA_4528150720221150.pdf | PriestleyC | 4528150720221150 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 10 | d9ph5aiqpll5mco6yf | Low Risk closed | Risk Closed | 44757.6285 | Obs8 | Measures To Limit Fire Spread And Development | 45488 | Low | Court Manager | Door closers needadjusting on flats 82,84,75&78 check all doors | Adjusted closers on flats 82,84,75 &78 To check all other doors
4531 | Bowler Close | BOWLERCLOS_S001 | H21 | Scheme | 2022-06-09 10:12 | FRA_4531090620221009.pdf | PriestleyC | 4531090620221000 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | cyr2d2bndxbl46ssqkj | Low Risk closed | Risk Closed | 44727.5077 | Obs8 | Measures To Limit Fire Spread And Development | 45452 | Low | Court Manager | Ease flat entrance door flat 8 | flat 8 door has now been eased
4533 | Falkland Court | FALKLAND_S001 | H21 | Scheme | 2022-02-07 15:58 | FRA_4533070220221552.pdf | PriestleyC | 4533070220221550 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 2 | aey75ccmg6kzcvj4mf | Low Risk closed | Risk Closed | 44603.5289 | Obs8 | Measures To Limit Fire Spread And Development | 45329 | Low | Court Manager | Check missing door closer on flat 2 | Pictures saved to fire risk assessment folder. Tablet does not have a signal at the property so unable to upload.
4533 | Falkland Court | FALKLAND_S001 | H21 | Scheme | 2022-02-07 15:58 | FRA_4533070220221552.pdf | PriestleyC | 4533070220221550 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 2 | nezv18os7kfkzcvhai9 | Low Risk to be actioned | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | 45329 | Low | Court Manager | PCFRA's to update and complete | NULL
4533 | Falkland Court | FALKLAND_S001 | H21 | Scheme | 2022-02-07 15:58 | FRA_4533070220221552.pdf | PriestleyC | 4533070220221550 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 2 | icapx507xrpkzcvhaj1 | Low Risk closed | Risk Closed | 44692.4136 | Obs11 | Fire Fighting Equipment | 45329 | Low | Court Manager | Fire extinguishers should be removed from corridors as per H21 policy at next makover (due this financial year) | Fire extinguishers, brackets & signs removed on all floors. We have left in situe - by laundry, court managers office, electrical cupboard. 1 inside the scooter room & another in lift motor room.
4533 | Falkland Court | FALKLAND_S001 | H21 | Scheme | 2022-02-07 15:58 | FRA_4533070220221552.pdf | PriestleyC | 4533070220221550 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 2 | kzykdheq0ckzcvhajq | Low Risk closed | Risk Closed | 44644.6246 | Obs15 | Management Of Fire Safety | 45329 | Low | Court Manager | Cleaner to complete fire safety training | Training completed 14/03/2022
4534 | Wellesley Court | WELLESLEY_S001 | H21 | Scheme | 2022-02-16 11:59 | FRA_4534160220221006.pdf | spencem | 4534160220221000 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | l66qryu7jtjkzpgrgs5 | Medium Risk closed | Risk Closed | 44677.5234 | Obs8 | Measures To Limit Fire Spread And Development | 44973 | Medium | Court Manager | Flat 25 Door - Screws missing to hinges Flat 7 Door - Door closer not effective Flat 3 Door - Door sticking on carpet | WO raised and completed.
4534 | Wellesley Court | WELLESLEY_S001 | H21 | Scheme | 2022-02-16 11:59 | FRA_4534160220221006.pdf | spencem | 4534160220221000 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | hth1lct8x29kzpguqn5 | Low Risk closed | Risk Closed | 44609.5172 | Obs10 | Fire Safety And Notices | 45337 | Low | Court Manager | Fire action notices should be completed with the correct assembly point which is the car park. | Fire sign completed with car park outside F8.
4534 | Wellesley Court | WELLESLEY_S001 | H21 | Scheme | 2022-02-16 11:59 | FRA_4534160220221006.pdf | spencem | 4534160220221000 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | 8k8q9rmapgrkzpgcs9p | Low Risk closed | Risk Closed | 44609.5228 | Obs7 | Fire Protection Measures | 45338 | Low | Court Manager | Scooter unattended on communal corridor. | Spoken with resident regarding health & safety, explained to resident scooter could not be left outside of flat for even a short space of time.
4534 | Wellesley Court | WELLESLEY_S001 | H21 | Scheme | 2022-02-16 11:59 | FRA_4534160220221006.pdf | spencem | 4534160220221000 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | d4024gq6em1kzph6ry7 | Low Risk closed | Risk Closed | 44635.4949 | Obs7 | Fire Protection Measures | 45338 | Low | Court Manager | Steps and flags outside the lower ground floor fire exit, adjacent to the lift are uneven. | WO raised OHaras attended 15/3/2022
4534 | Wellesley Court | WELLESLEY_S001 | H21 | Scheme | 2022-02-16 11:59 | FRA_4534160220221006.pdf | spencem | 4534160220221000 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | dm6urxeaa7ykzph2wym | Medium Risk closed | Risk Closed | 44635.4968 | Obs7 | Fire Protection Measures | 44973 | Medium | Court Manager | A number of the external fire exit doors were difficult to operate. Ensure that all external fire exit doors are easy to use and are not sticking in the opening or threshold. Ease overhaul and adjust where found. | WO raised and completed by Ohara services.
4534 | Wellesley Court | WELLESLEY_S001 | H21 | Scheme | 2022-02-16 11:59 | FRA_4534160220221006.pdf | spencem | 4534160220221000 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | c9yccf4ogxpkzpgwn7l | Low Risk closed | Risk Closed | 44609.5866 | Obs10 | Fire Safety And Notices | 45338 | Low | Court Manager | Ad-hoc running man signs should be removed from door glazing. | Removed from 1st floor near lift.
4534 | Wellesley Court | WELLESLEY_S001 | H21 | Scheme | 2022-02-16 11:59 | FRA_4534160220221006.pdf | spencem | 4534160220221000 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | 7c7iwn4ls89kzpgdzea | Medium Risk closed | Risk Closed | 44635.4993 | Obs7 | Fire Protection Measures | 44973 | Medium | Court Manager | A number of store rooms (controlled locations) we unlocked or not able to be locked at the time of inspection. Store rooms without locking mechanisms should be provided with them and labelled "Fire Door Keep Locked Shut". Also holes in store room door to be made good during improvements. | New lock fitted in store room and hole filled by Ohara services 15/3/2022
4534 | Wellesley Court | WELLESLEY_S001 | H21 | Scheme | 2022-02-16 11:59 | FRA_4534160220221006.pdf | spencem | 4534160220221000 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | 54tmai1enbzkzphle8m | Low Risk closed | Risk Closed | 44677.5257 | Obs8 | Measures To Limit Fire Spread And Development | 45338 | Low | Court Manager | Electromagnetic door closer installed without a local test switch. Change product seen in picture with a switchable type to allow for testing. | Door closer connected to fire and in working order. Building surveyor happy to keep existing door closer without test switch.
4534 | Wellesley Court | WELLESLEY_S001 | H21 | Scheme | 2022-02-16 11:59 | FRA_4534160220221006.pdf | spencem | 4534160220221000 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | 3u2v0yh3b27kzpgjiq0 | Low Risk closed | Risk Closed | 44657.6585 | Obs7 | Fire Protection Measures | 45338 | Low | Court Manager | Acoustic door closer to the lounge not working and may give rise to using a wedge. Arrange for commissioning and service of door closer and leave in good working order. | WO raised to PLB
4534 | Wellesley Court | WELLESLEY_S001 | H21 | Scheme | 2022-02-16 11:59 | FRA_4534160220221006.pdf | spencem | 4534160220221000 | Retirement Housing | Yorks Lancs | Lancashire and West Yorkshire | North | North Patch 10 | 1owvdntd7cvkzpfxkf3 | Medium Risk closed | Risk Closed | 44756.4109 | Obs6 | Fire Hazards - Elimination & Control | 44607 | Medium | Court Manager | The bins are stored externally at the end of the car park and not in a secured locked and closure away from the public. There are no reports of vandalism or arson but the location has a tendency to accumulate ad-hoc refuse and larger items. Consideration should be given to the control over the location and a plan put in place. | WO raised to OHaras bin store completed.
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | 3t9hc9k75lakyyfyq24 | Low Risk closed | Risk Closed | 44827.3864 | Obs15 | Management Of Fire Safety | 45319 | Low | Court Manager | In the interests of co-operation and coordination the findings of all fire risk assessments, including those of outside agencies should be shared with each other. | 23-09-22 - Risk assessment has now been shared with the outside agencies operating in the scheme - the delay in sharing is because of the length of time taken to close all actions down.
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | 36d0i52t1l2kyyf3ids | Low Risk closed | Risk Closed | 44601.4196 | Obs8 | Measures To Limit Fire Spread And Development | 45319 | Low | Court Manager | Doors that are on the escape route that have no self closing device should be kept locked shut when not in use and have a" Fire Door Keep Locked Shut" sign/disc fixed to the corridor side of each door. | Doors are now locked shut and staff have been advised.
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | 1xv577e5zhqkyyfmwjw | Observation Only | Risk Closed | 44595.4335 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Overloading of sockets in Leasehold Office. Microwave and kettle combined in excess of 3.5 KW . Rectified during inspection. | I have emailed the team and asked that they do not overload sockets in future.
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | 51p2s8c5kq4kyygadgk | Low Risk closed | Risk Closed | 44600.4966 | Obs16 | Testing And Maintenance | 45319 | Low | Court Manager | Fans not working in second floor refuse room. | WO raised with electrician, he advised one fan is working while the other is not so he had ordered a new fan which he will install ASAP.
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | 5drxvq3hi3fkyyjem6u | Medium Risk closed | Risk Closed | 44600.5288 | Obs6 | Fire Hazards - Elimination & Control | 44954 | Medium | Court Manager | Care staff room. Wall mount the extension serving the DECT handsets to prevent damage or being covered with something | W/O raised, electrician modified the extension to enable it to be fastened to the wall.
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | 74h7zf7977rkyye3xl8 | Low Risk closed | Risk Closed | 44595.642 | Obs9 | Escape Lighting | 45319 | Low | Court Manager | The communal emergency lighting is defective in places and has been approved for capital replacement. Measures should be taken to implement temporary repairs and control measures until the project is underway in April 2022 if any intolerable risk is present. | Checked all emergency lights and walked around after 10 mins and highlighted where repairs are necessary before the refit. Lower ground floor lighting is ok. Ground floor dark area near the lift but there isclughting in either side so low risk but one to monitor closely. Restaurant poor but adequate lighting. 1st floor lighting is poor but in the actual event of a power outage there should adequate lighting. 2nd floor light outside 41 area is dark but there is light on either side of the flat - low risk but one to monitor closely. Where lighting is adequate doesn't mean it falls under the standards which are expected.
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | 6pzfev4uitykyygs3q8 | Low Risk closed | Risk Closed | 44599.6606 | Obs8 | Measures To Limit Fire Spread And Development | 45319 | Low | Court Manager | Dining area entrance door does not fit correctly in the opening and the gaps are too big. Square up door using sash clamps, if possible , dowel joints and rehang. | Doors have been rehung.
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | bvglkriszu8kyyh6vv1 | Low Risk closed | Risk Closed | 44600.7529 | Obs7 | Fire Protection Measures | 45319 | Low | Court Manager | Sluice room in Commercial kitchen. Repair /rehang door. | Door rehung, wood boxing replaced.
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | f8dbtrg3asrkyyfulpy | Low Risk closed | Risk Closed | 44728.5724 | Obs13 | Other Relevant Fixed Systems | 45319 | Low | Court Manager | Only one of the two lifts return to ground during a fire alarm test. | Duplicate action.
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | e0dtr3497qokyygpu6c | Medium Risk closed | Risk Closed | 44600.7566 | Obs6 | Fire Hazards - Elimination & Control | 44954 | Medium | Court Manager | Community computer suite. Ensure all flammable materials are separated and equipment air vents are unobstructed before use. | This task has been handed over to the licensee and Day Centre Manager.
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | 7yxldw2kwoxkyyh1emg | Low Risk closed | Risk Closed | 44600.4727 | Obs6 | Fire Hazards - Elimination & Control | 45319 | Low | Court Manager | Correctly fix commercial kitchen insect-ecuter to wall , clip cables and replace defective component / bulb. | WO raised for Electrician to replace bulbs and rehang.
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | 9hfx3k44ekwkyygz6cp | Low Risk closed | Risk Closed | 44600.526 | Obs8 | Measures To Limit Fire Spread And Development | 45319 | Low | Court Manager | Re-fix damaged stop lath to commercial kitchen door and fit white batwing type cold smoke seals the casing on completion. | Repair to the door.
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | ak4eh3qsw4akyyg4g3u | Medium Risk closed | Risk Closed | 44595.6191 | Obs6 | Fire Hazards - Elimination & Control | 44954 | Medium | Court Manager | There is an electric focal fire in the second floor communal lounge. There is a risk of it being left on and/or furnishings being stored in front of it. Consider the requirement for additional heat in this location and disconnect if not needed. | Fire has been diconected, just used for display.
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | bhedxetgewzkyyha06k | Low Risk closed | Risk Closed | 44603.4668 | Obs10 | Fire Safety And Notices | 45319 | Low | Court Manager | Boiler Room and electrical distribution doors require "authorised personnel access only" warning signs and the relevant hazard room identification pictogram . | Signs put on with zip ties to prevent damage to the doors.
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | b93w8byd70wkyyhrh79 | Low Risk closed | Risk Closed | 44599.6633 | Obs16 | Testing And Maintenance | 45319 | Low | Court Manager | Fault code showing on Andrews gas fire water heaters. Need investigation and repair | W/O raised , GOS have visited and advised there is further work required on the boiler and he has spoken to Robert Clak and Martin Spence and it has now in the hands of asset management.
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | ar9vx8lzoqzkyyg80ay | Low Risk closed | Risk Closed | 44599.6505 | Obs8 | Measures To Limit Fire Spread And Development | 45319 | Low | Court Manager | Replace riser duct cladding to heating controls and seal perimeter with intumescent sealant. Second floor refuse room. | Cladding replaced and sealed.
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | i75elcrrpjikyyhiyd8 | Medium Risk closed | Risk Closed | 44594.5839 | Obs6 | Fire Hazards - Elimination & Control | 44954 | Medium | Court Manager | Main office comms room. Clean out room and separate combustibles from ignition sources and vent grilles to appliances. | Space cleared and locked shut when not in use.
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | j1n97byvruikyyhlx52 | Medium Risk closed | Risk Closed | 44900.6396 | Obs8 | Measures To Limit Fire Spread And Development | 44954 | Medium | Surveyor | Redundant boiler flue in boiler house. Seal whole base of flue with 1 hour fire stopping materials. | Contractor appointed to seal base of redundant flue with fire retardant materials. Inspected and complete 05/12/22
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | jahz2alwumhkyye3xkc | Low Risk closed | Risk Closed | 44827.4777 | Obs7 | Fire Protection Measures | 44962 | Low | Surveyor | There is no fire ceiling above the upper floor suspended ceiling. This has been noted on the Type 4 inspection. Works to fully fire stop the roof space above are now complete. There is fire separation at compartment walls and above fire breaks and there is detection in the roof space. | Confirmation of discussion with Cambridge Fire Authority. They confirmed that the ceiling was sufficient providing the adjacent compartment walls had been inspected and properly fire stopped in all areas up to the roof pitch. This has been competed and a certificate provided.
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | gk6yc2fd4inkyyg0y6l | Medium Risk closed | Risk Closed | 44610.6876 | Obs16 | Testing And Maintenance | 44954 | Medium | Court Manager | The safe and sound Tunstall units do not appear to be electrically tested and are not fixed or wall mounted away from combustible materials. Provide evidence of electrical safety and relocate units adjacent to curtains and furnishings | 11th Feb - Units have now been PAT tested 15th Feb - Safe and sound have been contacted about mounting the units to the window or wall as our electrician said if they are moved they will lose signal so unable to carry out works. 18th Feb units gave now been mounted to the wall.
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | gptlatq5ruskyygw9in | Medium Risk closed | Risk Closed | 44622.3614 | Obs6 | Fire Hazards - Elimination & Control | 44954 | Medium | Court Manager | Commercial Kitchen fridges in dining area. Risk of damage to trailing leads and potential overloading of dual extension lead. Check voltages and run cabling in trunking around walls with wall mounted outlets. | New socket installed to reduce use of extension
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | kqd30zkfkc8kyygbj75 | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45319 | Low | Surveyor | Consider additional fire directional signage in stairwells and at final exit doors where missing. Coordinate works with the communal and emergency lighting project. | NULL
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | n44z3pghowdkyygfehx | Medium Risk closed | Risk Closed | 44607.5303 | Obs8 | Measures To Limit Fire Spread And Development | 44954 | Medium | Court Manager | Doors stops were evident during the inspection. Doors on escape routes that are controlled locations do not require a door closer providing they have the correct signage. Consider acoustic door closers or Doorguard products instead of door stops if required. | Door stops have been removed and new metal signs on door that are required to be locked shut.
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | p9l003m1pzbkyyhxawk | Medium Risk closed | Risk Closed | 44600.4693 | Obs8 | Measures To Limit Fire Spread And Development | 44954 | Medium | Court Manager | Commercial kitchen office and stores are controlled locations and should be kept locked shut or fitted with self closing devices | Let's given to staff to ensure doors are locked shut.
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | r3udd6s62lekyygmbzb | Medium Risk closed | Risk Closed | 44593.4461 | Obs6 | Fire Hazards - Elimination & Control | 44954 | Medium | Court Manager | Kettle and oscillating fan in Care Staff room are not tested and appear to be heat damaged. Remove from site or prove fit for purpose. Remove excess material from above microwave oven in same location. | BMDC cleared microwave, fan removed and disposed off, kettle replaced with one PAT tested.
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | wdyshdxe99jkyyhtztr | Low Risk closed | Risk Closed | 44622.3619 | Obs11 | Fire Fighting Equipment | 45319 | Low | Court Manager | Relocate Co2 fire extinguisher to left hand side of boiler house exit door where is can be accessed properly. | Fire extinguisher relocated.
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | w0dbxvzdnznkyygi6m5 | Low Risk closed | Risk Closed | 44600.6802 | Obs8 | Measures To Limit Fire Spread And Development | 45319 | Low | Court Manager | Care staff room door is poorly fitting and has holes above the push lock. Adjust door in the opening to equal out the gaps and change intumescent strip to combine fire and smoke. Fill holes in door with matching timber dowels | Lock replaced, dowels installed, intumecent installed.
4544 | Mary Seacole Court | MARYSEACOLE_S001 | H21 | Scheme | 2022-01-28 15:49 | FRA_4544280120221237.pdf | spencem | 4544280120221230 | Extra Care | Extra Care North | EC North 5 | North | North Patch 5 | zdp06l9erkokyyenh9h | Medium Risk closed | Risk Closed | 44595.5247 | Obs8 | Measures To Limit Fire Spread And Development | 44954 | Medium | Court Manager | Flammable materials should be separated from ignition sources. Remove boxes and material stored beneath steel cabinets containing electrical equipment. Noted in several location around the building. | Removed boxes from under steel cabinets.
4546 | Acre Court | ACRE_S001 | H21 | Scheme | 2022-04-29 11:34 | FRA_4546290420221128.pdf | lofthousei | 4546290420221120 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 10 | n6ediwi14nl2kakekv | Low Risk closed | Risk Closed | 44693.7072 | Obs4 | The Occupant - Information Provided By The Court Manager | 45411 | Low | Court Manager | Court Manager to review PCFRA's in line with new procedure. | All PCFRA`s have now been reviewed and completed
4546 | Acre Court | ACRE_S001 | H21 | Scheme | 2022-04-29 11:34 | FRA_4546290420221128.pdf | lofthousei | 4546290420221120 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 10 | n0mfnba499il2kakens | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45411 | Low | Surveyor | Electric meter box covers, not fire resistant, also requires fire stopping to cable penetrations | NULL
4546 | Acre Court | ACRE_S001 | H21 | Scheme | 2022-04-29 11:34 | FRA_4546290420221128.pdf | lofthousei | 4546290420221120 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 10 | llxcys9phwil2kakep9 | Low Risk closed | Risk Closed | 44684.6021 | Obs10 | Fire Safety And Notices | 45411 | Low | Court Manager | Assembly Point details to be inserted on all FAN's | All FAN`s are up to do with correct inforamtion
4546 | Acre Court | ACRE_S001 | H21 | Scheme | 2022-04-29 11:34 | FRA_4546290420221128.pdf | lofthousei | 4546290420221120 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 10 | k897dzo9gtl2kakejr | Observation Only | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Residents are confused by the communal alarm (voice instruction to evacuate) as it is audiable in the flats to a level that residents believe it relates to them, despite stay-put policy. | NULL
4546 | Acre Court | ACRE_S001 | H21 | Scheme | 2022-04-29 11:34 | FRA_4546290420221128.pdf | lofthousei | 4546290420221120 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 10 | jwnus9oig2il2kaken7 | Low Risk closed | Risk Closed | 44684.6015 | Obs7 | Fire Protection Measures | 45411 | Low | Court Manager | Fire Exit door from communal lounge is fitted with incorrect lock, requires single operation keyless exit and non dead-locking mechanism. | Tested and lock meets requirements as discussed with Ian Lofthouse.
4546 | Acre Court | ACRE_S001 | H21 | Scheme | 2022-04-29 11:34 | FRA_4546290420221128.pdf | lofthousei | 4546290420221120 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 10 | 9zm99in47fpl2kakeod | Medium Risk closed | Risk Closed | 44774.5668 | Obs8 | Measures To Limit Fire Spread And Development | 45045 | Medium | Court Manager | Fire door to buggy store on tie back, not suitable for high risk location. The backs to be removed. Consider forward or swing-free closer | Door guards that close on sound of fire alarm now fitted to 3 x buggy store fire doors as requested.
4546 | Acre Court | ACRE_S001 | H21 | Scheme | 2022-04-29 11:34 | FRA_4546290420221128.pdf | lofthousei | 4546290420221120 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 10 | ez34kldhpnl2kakemr | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45411 | Low | Surveyor | Doors to riser cupboards are not fitted with cold smoke seals and gaps between frame require fire stopping. | NULL
4547 | Leasowe Court | LEASOWE_S001 | H21 | Scheme | 2022-01-12 13:51 | FRA_4547120120221348.pdf | lofthousei | 4547120120221340 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 10 | 7e8aaqtqf2kkybllk7g | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45303 | Low | Surveyor | Fire stopping required to cable penetrations | NULL
4547 | Leasowe Court | LEASOWE_S001 | H21 | Scheme | 2022-01-12 13:51 | FRA_4547120120221348.pdf | lofthousei | 4547120120221340 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 10 | kk4r682ty3kybllk6t | Low Risk closed | Risk Closed | 44574.427 | Obs6 | Fire Hazards - Elimination & Control | 45303 | Low | Court Manager | Combustible materials behind driers, area should be sterile | Removed brushes and sticks from behind dryer and put in shed outside
4547 | Leasowe Court | LEASOWE_S001 | H21 | Scheme | 2022-01-12 13:51 | FRA_4547120120221348.pdf | lofthousei | 4547120120221340 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 10 | kd9vtcvgl5kyblly2o | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45303 | Low | Surveyor | Approx 60% flat entrance doors not fitted with cold smoke seals - supply and fit suitable seals. | NULL
4547 | Leasowe Court | LEASOWE_S001 | H21 | Scheme | 2022-01-12 13:51 | FRA_4547120120221348.pdf | lofthousei | 4547120120221340 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 10 | thp6bh45eekybllk4y | Observation Only | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Surveyor | Electric meter boxes not fire resistant, and cable penetrations not fire stopped but fire risk extremely low. | NULL
4547 | Leasowe Court | LEASOWE_S001 | H21 | Scheme | 2022-01-12 13:51 | FRA_4547120120221348.pdf | lofthousei | 4547120120221340 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 10 | nov613tpdfkybllk6a | Medium Risk closed | Risk Closed | 44574.4303 | Obs6 | Fire Hazards - Elimination & Control | 44938 | Medium | Court Manager | Buggy store door wedged open. Must be closed at all times | Notice put on scooter door a correct fire door keep shut sign ordered, removed wedge from door and shut. Also sent letters to residents advising this door when in use must be closed straight behind them. Cm to check twice daily this is shut start if shift and end
4547 | Leasowe Court | LEASOWE_S001 | H21 | Scheme | 2022-01-12 13:51 | FRA_4547120120221348.pdf | lofthousei | 4547120120221340 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 10 | v8q4ug13fq7kybllk5i | Low Risk closed | Risk Closed | 44574.541 | Obs6 | Fire Hazards - Elimination & Control | 45303 | Low | Court Manager | Store cupboard unlocked, should be fire door keeped locked. | Had handy man come change locks so I could lock door as previously no keys that fit door. Also removed contents inside door us now shut and locked
4547 | Leasowe Court | LEASOWE_S001 | H21 | Scheme | 2022-01-12 13:51 | FRA_4547120120221348.pdf | lofthousei | 4547120120221340 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 10 | x5k1qdgm1qkkybllk80 | Low Risk closed | Risk Closed | 44574.5429 | Obs8 | Measures To Limit Fire Spread And Development | 45303 | Low | Court Manager | Fire door to buggy store not closing fully, catching on carpet - ease and adjust door | Fire door has been eased and adjusted by joiner today on work order 1511745
4602 | Ludlow Hewitt Court | LUDLOWHEWI_S001 | H21 | Scheme | 2022-07-26 11:11 | FRA_4602260720220902.pdf | fowlerb1 | 4602260720220900 | Retirement Housing | South West | North East Somerset Wilts and Avon | South | South Patch 2 | jtcr4t656w8l6205ogm | Observation Only | Risk Closed | 44768.5406 | Obs10 | Fire Safety And Notices | NULL | N/A | Court Manager | Fire action notice | Information only
4602 | Ludlow Hewitt Court | LUDLOWHEWI_S001 | H21 | Scheme | 2022-07-26 11:11 | FRA_4602260720220902.pdf | fowlerb1 | 4602260720220900 | Retirement Housing | South West | North East Somerset Wilts and Avon | South | South Patch 2 | g6r2j1l8ro4l61z4wen | Observation Only | Risk Closed | 44832.4428 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel for information only | Information only
4602 | Ludlow Hewitt Court | LUDLOWHEWI_S001 | H21 | Scheme | 2022-07-26 11:11 | FRA_4602260720220902.pdf | fowlerb1 | 4602260720220900 | Retirement Housing | South West | North East Somerset Wilts and Avon | South | South Patch 2 | 2gc1vqcxeynl61z297o | Observation Only | Risk Closed | 44832.4426 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Surveyor | FFE | Information only
4602 | Ludlow Hewitt Court | LUDLOWHEWI_S001 | H21 | Scheme | 2022-07-26 11:11 | FRA_4602260720220902.pdf | fowlerb1 | 4602260720220900 | Retirement Housing | South West | North East Somerset Wilts and Avon | South | South Patch 2 | caqjaq0c8val6200dba | Observation Only | Risk Closed | 44768.5409 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Court Manager | Windows opened manually | Information only
4603 | Frederick Taylor Court | FREDERICKTAY_BUNGALOWS | H21 | Unknown | 2020-06-17 11:04 | FRA_460317062020.pdf | butcherm | 460317062020 | Retirement Housing | South West | North East Somerset Wilts and Avon | South | South Patch 2 | n4v7um5hj5gkbj6ndzt | Observation Only | Risk Open | NULL | Obs15 | Management Of Fire Safety | NULL | N/A | Other | Tests and checks recorded on Pebbles system | NULL
4603 | Frederick Taylor Court | FREDERICKTAY_S001 | H21 | Scheme | 2022-06-07 14:01 | FRA_4603070620221317.pdf | fowlerb1 | 4603070620221310 | Retirement Housing | South West | North East Somerset Wilts and Avon | South | South Patch 2 | piyr07krmgjl44502ke | Observation Only | Risk Closed | 44719.5884 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel for information only | For information only
4603 | Frederick Taylor Court | FREDERICKTAY_BUNGALOWS | H21 | Unknown | 2020-06-17 11:04 | FRA_460317062020.pdf | butcherm | 460317062020 | Retirement Housing | South West | North East Somerset Wilts and Avon | South | South Patch 2 | u90lylfi4akbj6iqh0 | Medium Risk closed | Risk Closed | 44099.4889 | Obs8 | Measures To Limit Fire Spread And Development | 44364 | Medium | Court Manager | Communal kitchen door adjusted door closer snap shut | Door has been adjusted
4603 | Frederick Taylor Court | FREDERICKTAY_S001 | H21 | Scheme | 2022-06-07 14:01 | FRA_4603070620221317.pdf | fowlerb1 | 4603070620221310 | Retirement Housing | South West | North East Somerset Wilts and Avon | South | South Patch 2 | rz218b7smxl4460yzn | Low Risk closed | Risk Closed | 44736.3531 | Obs14 | Access By Emergency Services | 45450 | Low | Court Manager | Fire assembly point sign to be fitted to lamp post outside communal lounge | sign too big for lamp post had to site on wall opposite car park.
4605 | Hedley Davis Court | HEDLEYDAVI_S001 | H21 | Scheme | 2022-09-14 11:25 | FRA_4605140920221010.pdf | fowlerb1 | 4605140920221010 | Retirement Housing | South West | North East Somerset Wilts and Avon | South | South Patch 2 | rubpyu9vf2bl81fd4ng | Observation Only | Risk Closed | 44832.4495 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel for information only | Information only
4605 | Hedley Davis Court | HEDLEYDAVI_S001 | H21 | Scheme | 2022-09-14 11:25 | FRA_4605140920221010.pdf | fowlerb1 | 4605140920221010 | Retirement Housing | South West | North East Somerset Wilts and Avon | South | South Patch 2 | r5z9tvir1rl81gsb77 | Observation Only | Risk Closed | 44832.4496 | Obs10 | Fire Safety And Notices | NULL | N/A | Surveyor | Fire action notices for information only | Information only
4605 | Hedley Davis Court | HEDLEYDAVI_S001 | H21 | Scheme | 2022-09-14 11:25 | FRA_4605140920221010.pdf | fowlerb1 | 4605140920221010 | Retirement Housing | South West | North East Somerset Wilts and Avon | South | South Patch 2 | bweh5rd0qnl81fz1qj | Observation Only | Risk Closed | 44832.4498 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Surveyor | FFE for information only | Information only
4605 | Hedley Davis Court | HEDLEYDAVI_S001 | H21 | Scheme | 2022-09-14 11:25 | FRA_4605140920221010.pdf | fowlerb1 | 4605140920221010 | Retirement Housing | South West | North East Somerset Wilts and Avon | South | South Patch 2 | bmh3j3fpeu7l81fv64l | High Risk Closed | Risk Closed | 44820.4032 | Obs6 | Fire Hazards - Elimination & Control | 44909 | High | Court Manager | Resident in flat no.7 that has dementia and smokes and this is a Hugh risk situation. | We had a visit from the Safe & Well being Fire officer who met with myself, the resident and her son. They provided the resident with a fire resistant blanket to wrap around her when she smokes. They also sprayed her carpet around the areas where she tends to sit and smoke with a fire retardant spray.
4605 | Hedley Davis Court | HEDLEYDAVI_S001 | H21 | Scheme | 2022-09-14 11:25 | FRA_4605140920221010.pdf | fowlerb1 | 4605140920221010 | Retirement Housing | South West | North East Somerset Wilts and Avon | South | South Patch 2 | ww1t50sqaifl81gil6j | Observation Only | Risk Closed | 44832.4504 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Surveyor | AOV's to communal areas and upvc window panels removed. | Information only
4607 | Maple Court | MAPLE_S001 | H21 | Scheme | 2022-02-14 11:13 | FRA_4607140220221017.pdf | AhmadW | 4607140220221010 | Extra Care | Extra Care South | EC South 5 | South | South Patch 8 | rqxxmp4vrnkzmkfl0y | Medium Risk closed | Risk Closed | 44743.301 | Obs7 | Fire Protection Measures | 44971 | Medium | Court Manager | Kitchen to restaurant door needs adjustment and reconnecting to the closer. | Raised work order
4608 | Dairy View Court | DAIRYVIEW_S001 | H21 | Scheme | 2022-01-25 11:55 | FRA_4608250120221035.pdf | AhmadW | 4608250120221030 | Extra Care | Extra Care South | EC South 5 | South | South Patch 8 | qzjowlhucqfkyu0dyqv | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45316 | Low | Court Manager | 2 no. Ground floor corridor doors require minor repair | NULL
4608 | Dairy View Court | DAIRYVIEW_S001 | H21 | Scheme | 2022-01-25 11:55 | FRA_4608250120221035.pdf | AhmadW | 4608250120221030 | Extra Care | Extra Care South | EC South 5 | South | South Patch 8 | 4xkkc918ceykyu0fanq | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45316 | Low | Court Manager | The following Corridor doors require adjustment, By flat 41 | NULL
4608 | Dairy View Court | DAIRYVIEW_S001 | H21 | Scheme | 2022-01-25 11:55 | FRA_4608250120221035.pdf | AhmadW | 4608250120221030 | Extra Care | Extra Care South | EC South 5 | South | South Patch 8 | z1a9iy398ihkyu0xdtn | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45316 | Low | Court Manager | Chairs placed in corridors beside water coolers. Should be removed | NULL
4702 | Mitford Slade Court | MITFORDSLAD_S001 | H21 | Scheme | 2022-01-13 11:01 | FRA_4702130120220955.pdf | fowlerb1 | 4702130120220950 | Retirement Housing | South West | North East Somerset Wilts and Avon | South | South Patch 2 | 4rsdli1ruzikycunnkv | Observation Only | Risk Closed | 44649.3631 | Obs10 | Fire Safety And Notices | NULL | N/A | Surveyor | Fire action notice | This is information only
4702 | Mitford Slade Court | MITFORDSLAD_S001 | H21 | Scheme | 2022-01-13 11:01 | FRA_4702130120220955.pdf | fowlerb1 | 4702130120220950 | Retirement Housing | South West | North East Somerset Wilts and Avon | South | South Patch 2 | 2hyyz0fr753kyctcau9 | Observation Only | Risk Closed | 44649.3633 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel for information only | This is information only
4702 | Mitford Slade Court | MITFORDSLAD_S001 | H21 | Scheme | 2022-01-13 11:01 | FRA_4702130120220955.pdf | fowlerb1 | 4702130120220950 | Retirement Housing | South West | North East Somerset Wilts and Avon | South | South Patch 2 | 3bqvjg07gm4kycufhye | Observation Only | Risk Closed | 44649.3628 | Obs9 | Escape Lighting | NULL | N/A | Surveyor | Emergency lighting | This is information only
4702 | Mitford Slade Court | MITFORDSLAD_S001 | H21 | Scheme | 2022-01-13 11:01 | FRA_4702130120220955.pdf | fowlerb1 | 4702130120220950 | Retirement Housing | South West | North East Somerset Wilts and Avon | South | South Patch 2 | 1jvf0jmxelijkycu21eb | Observation Only | Risk Closed | 44649.3668 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Surveyor | Fire blanket | This is information only
4702 | Mitford Slade Court | MITFORDSLAD_S001 | H21 | Scheme | 2022-01-13 11:01 | FRA_4702130120220955.pdf | fowlerb1 | 4702130120220950 | Retirement Housing | South West | North East Somerset Wilts and Avon | South | South Patch 2 | t4w5mg6z6ykycu36pd | Observation Only | Risk Closed | 44649.3626 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Surveyor | Portable appliance test details | This is information only
4702 | Mitford Slade Court | MITFORDSLAD_S001 | H21 | Scheme | 2022-01-13 11:01 | FRA_4702130120220955.pdf | fowlerb1 | 4702130120220950 | Retirement Housing | South West | North East Somerset Wilts and Avon | South | South Patch 2 | t9dn0obmvxkycucop8 | Observation Only | Risk Closed | 44649.363 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Surveyor | Guest room and flat 5 above communal lounge | This is information only
4702 | Mitford Slade Court | MITFORDSLAD_S001 | H21 | Scheme | 2022-01-13 11:01 | FRA_4702130120220955.pdf | fowlerb1 | 4702130120220950 | Retirement Housing | South West | North East Somerset Wilts and Avon | South | South Patch 2 | gxpf530vnnnkyctz86e | Observation Only | Risk Closed | 44649.3635 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Surveyor | Bin store | This is information only
4704 | Hillside Court | HILLSIDE_S001 | H21 | Scheme | 2022-10-20 16:01 | FRA_4704201020221541.pdf | AhmadW | 4704201020221540 | Extra Care | Extra Care South | EC South 5 | South | South Patch 8 | ng0f471y0wal9h6uk1l | Medium Risk to be actioned | Risk Open | NULL | Obs16 | Testing And Maintenance | 45219 | Medium | Surveyor | AOV near flat 38 is not opening. Problem with switch gear and cabling. All other AOVs may require renewal. Contractors to attend | NULL
4706 | John James Court | JOHNJAME_S001 | H21 | Scheme | 2022-06-27 14:02 | FRA_4706270620221330.pdf | AhmadW | 4706270620221330 | Retirement Housing | South West | North East Somerset Wilts and Avon | South | South Patch 8 | ax44ec3tifdl4wq7zrb | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45470 | Low | Court Manager | Waste items to be cleared from plant room and electrical intake cupboard | NULL
4801 | Johnson Court | JOHNSON_S001 | H21 | Scheme | 2022-06-21 09:13 | FRA_4801210620220910.pdf | doerrd | 4801210620220910 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 1 | s7qudz5e6dl4nvzb86 | Low Risk closed | Risk Closed | 44740.6012 | Obs8 | Measures To Limit Fire Spread And Development | 45464 | Low | Court Manager | Fire door to under stairs cupboard in block 12-18 is missing the smoke seal from the top of the door. | replaced 28/6/22
4802 | Edward Arnold Court | EDWARDARNO_S001 | H21 | Scheme | 2022-01-10 09:47 | FRA_4802100120220922.pdf | doerrd | 4802100120220920 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 1 | opcqr5s2qjhky8h8mdn | Low Risk closed | Risk Closed | 44742.4035 | Obs15 | Management Of Fire Safety | 45301 | Low | Court Manager | List of FFE and locations details old appliances. List needs updating. | walked round the court checked positions of all FFE Logged missing one and replaced Court Plan in fire folder
4802 | Edward Arnold Court | EDWARDARNO_S001 | H21 | Scheme | 2022-01-10 09:47 | FRA_4802100120220922.pdf | doerrd | 4802100120220920 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 1 | gqrm1tiv5clky8h8maf | Medium Risk closed | Risk Closed | 44732.6761 | Obs1 | The Building | 44936 | Medium | Surveyor | Extractor fans from a number of internal bathrooms terminate in the communal corridor and shared escape route. These should have intumescent grills or barriers inside the ducts to ensure compartmentation. | Court Manager has had these fitted.
4802 | Edward Arnold Court | EDWARDARNO_S001 | H21 | Scheme | 2022-01-10 09:47 | FRA_4802100120220922.pdf | doerrd | 4802100120220920 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 1 | b4cqscxub8ky8hs1c8 | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44936 | Medium | Surveyor | There are no opening widows to the corridors and no ventilation system installed. | NULL
4802 | Edward Arnold Court | EDWARDARNO_S001 | H21 | Scheme | 2022-01-10 09:47 | FRA_4802100120220922.pdf | doerrd | 4802100120220920 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 1 | 2qtrl67jvu4ky8h8mbm | Medium Risk closed | Risk Closed | 44575.5712 | Obs2 | Means Of Giving Warning In Case Of Fire | 44936 | Medium | Court Manager | Zoning needs checking to ensure that flats are alerted when required. Flat 30 specifically needs investigating due to a known disconnection. | Flat 30 raised works order to get this rectified and arrange for openview to come out to check our zoning and reset if needed
4802 | Edward Arnold Court | EDWARDARNO_S001 | H21 | Scheme | 2022-01-10 09:47 | FRA_4802100120220922.pdf | doerrd | 4802100120220920 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 1 | 2v93eh0fdljky8h8mck | Observation Only | Risk Closed | 44575.3311 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | No PAT testing of scooters in scooter store. Not a housing 21 direct responsibility however clarification is being sought on the rules and records we keep on residents scooter insurance and maintenance. | Not obligation to record however encourage residents to have insurance and maintain the scooters for safety
4802 | Edward Arnold Court | EDWARDARNO_S001 | H21 | Scheme | 2022-01-10 09:47 | FRA_4802100120220922.pdf | doerrd | 4802100120220920 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 1 | wz533qk8lqky8h8m8z | Observation Only | Risk Closed | 44732.6757 | Obs1 | The Building | NULL | N/A | Surveyor | There are no roof voids accessible from the communal areas. | No action can be taken
4803 | Howard Court (Flitwick) | HOWARDFLIT_S001 | H21 | Scheme | 2022-06-22 09:41 | FRA_4803220620220925.pdf | doerrd | 4803220620220920 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 1 | ydlusd2z1ul4pbzefq | Low Risk closed | Risk Closed | 44749.5143 | Obs6 | Fire Hazards - Elimination & Control | 45096 | Low | Court Manager | Door mats in communal areas especially near exits and stairs. | Mentioned in the monthly newsletter thee importance of removing doormats as highlighted in the risk assessment.
4803 | Howard Court (Flitwick) | HOWARDFLIT_S001 | H21 | Scheme | 2022-06-22 09:41 | FRA_4803220620220925.pdf | doerrd | 4803220620220920 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 1 | 3h1gak70n0pl4pbzegy | Low Risk closed | Risk Closed | 44749.4185 | Obs10 | Fire Safety And Notices | 45465 | Low | Court Manager | Fire door keep shut sign is half worn away. This is on the communal door next to flat 15 | Purchased 2 new fire door keep shut signs to replace and 1 spare
4803 | Howard Court (Flitwick) | HOWARDFLIT_S001 | H21 | Scheme | 2022-06-22 09:41 | FRA_4803220620220925.pdf | doerrd | 4803220620220920 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 1 | ns49jrh243l4pc0j5v | Medium Risk closed | Risk Closed | 44735.372 | Obs6 | Fire Hazards - Elimination & Control | 44731 | Medium | Court Manager | Plug in air freshener in the communal areas is a fire hazard that cannot be allowed to continue. | Letter sent to residents plug in removed sign put up in block notice boards.
4804 | Handley Court | HANDLEY_S001 | H21 | Scheme | 2022-11-22 15:33 | FRA_4804221120221515.pdf | doerrd | 4804221120221510 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 1 | tvx1ydw5xwalasczys2 | Low Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45618 | Low | Court Manager | Update court fire folder documents. Fire plan, there are some out of date details around the extinguishers. | NULL
4804 | Handley Court | HANDLEY_S001 | H21 | Scheme | 2022-11-22 15:33 | FRA_4804221120221515.pdf | doerrd | 4804221120221510 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 1 | 4x39lm04gomlasczyol | Observation Only | Risk Closed | 44887.6601 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Surveyor | Although the electrical meter cupboards are metal and should provide suitable protection due to their age and the possibilty that residents may leave them open slightly there is a minor risk that remains | No action required, this is just a note.
4804 | Handley Court | HANDLEY_S001 | H21 | Scheme | 2022-11-22 15:33 | FRA_4804221120221515.pdf | doerrd | 4804221120221510 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 1 | 7wjnhrmthfolasczypi | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45252 | Medium | Court Manager | Walker, buggy and coffee table are stored on the communal hallway. These should be inside the flats. Corridor by flat 38 | NULL
4804 | Handley Court | HANDLEY_S001 | H21 | Scheme | 2022-11-22 15:33 | FRA_4804221120221515.pdf | doerrd | 4804221120221510 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 1 | asz03tog2uklasczyt4 | Low Risk to be actioned | Risk Open | NULL | Obs16 | Testing And Maintenance | 45618 | Low | M&E Team | The lightning protection system is now being added to the service contractors list of courts. And will be serviced going forwards. | NULL
4804 | Handley Court | HANDLEY_S001 | H21 | Scheme | 2022-11-22 15:33 | FRA_4804221120221515.pdf | doerrd | 4804221120221510 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 1 | a2uta5m850hlasd5uj0 | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45618 | Low | Court Manager | Under stairs store cupboard has combustible materials stored. There is detection but this should be cleared. | NULL
4804 | Handley Court | HANDLEY_S001 | H21 | Scheme | 2022-11-22 15:33 | FRA_4804221120221515.pdf | doerrd | 4804221120221510 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 1 | vg96xxzqgnklasczyqz | Low Risk closed | Risk Closed | 44897.5486 | Obs10 | Fire Safety And Notices | 45618 | Low | Court Manager | Fire safety notices in lounge and kitchen need the assembly point location written onto them. | completed signs in permanent ink to read evacuate to car park
4902 | Alice Bye Court | ALICEBYE_S001 | H21 | Scheme | 2022-09-20 11:47 | FRA_4902200920220946.pdf | pickfordj | 4902200920220940 | Extra Care | Extra Care South | EC South 5 | South | South Patch 8 | vswcj2e76nbl89z5qp0 | High Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44915 | High | Court Manager | Flat 44 breeches the building smoking policy and is careless especially with where he extinguished his cigarettes. It's been highlighted to me that the resident is also a high risk concern for fire safety within his flat. He extinguishes and in rubbish bins, on his floor, in doors and on bedding. This is a high risk concern due to a previous fire caused by the resident and smoking | NULL
4902 | Alice Bye Court | ALICEBYE_S001 | H21 | Scheme | 2022-09-20 11:47 | FRA_4902200920220946.pdf | pickfordj | 4902200920220940 | Extra Care | Extra Care South | EC South 5 | South | South Patch 8 | up5vkp8af1cl89ztp56 | Medium Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45189 | Medium | Court Manager | Put up signage to make clear to visitors what the fire Eva is in communal areas. | NULL
4902 | Alice Bye Court | ALICEBYE_S001 | H21 | Scheme | 2022-09-20 11:47 | FRA_4902200920220946.pdf | pickfordj | 4902200920220940 | Extra Care | Extra Care South | EC South 5 | South | South Patch 8 | yk4p9u6dhyfl8a25d6g | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45555 | Low | Court Manager | Flat 11, items need removing from communal hallway | NULL
4902 | Alice Bye Court | ALICEBYE_S001 | H21 | Scheme | 2022-09-20 11:47 | FRA_4902200920220946.pdf | pickfordj | 4902200920220940 | Extra Care | Extra Care South | EC South 5 | South | South Patch 8 | dbr9f9z7yail8a20cfv | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45189 | Medium | Court Manager | Refuse doors are floor 1 I do not believe are fire doors and they are missing the intu strips/cold smoke seals. Also door closer missing. | NULL
4902 | Alice Bye Court | ALICEBYE_S001 | H21 | Scheme | 2022-09-20 11:47 | FRA_4902200920220946.pdf | pickfordj | 4902200920220940 | Extra Care | Extra Care South | EC South 5 | South | South Patch 8 | d0kt7ttwm3pl8a2g5vn | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45555 | Low | Court Manager | Lower ground floor, needs items removing from elec cupboard | NULL
4902 | Alice Bye Court | ALICEBYE_S001 | H21 | Scheme | 2022-09-20 11:47 | FRA_4902200920220946.pdf | pickfordj | 4902200920220940 | Extra Care | Extra Care South | EC South 5 | South | South Patch 8 | dun1zreu1ltl8a26ztk | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45189 | Medium | Court Manager | Office inside communal kitchen area needs a fire door with vision panel as it's a room inside a room. | NULL
4902 | Alice Bye Court | ALICEBYE_S001 | H21 | Scheme | 2022-09-20 11:47 | FRA_4902200920220946.pdf | pickfordj | 4902200920220940 | Extra Care | Extra Care South | EC South 5 | South | South Patch 8 | 6qg7yv5brkl8a28zad | High Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44915 | High | Court Manager | Bin store, on entrance level, accessed externally and internally. Needs the missing ceiling replaced | NULL
4902 | Alice Bye Court | ALICEBYE_S001 | H21 | Scheme | 2022-09-20 11:47 | FRA_4902200920220946.pdf | pickfordj | 4902200920220940 | Extra Care | Extra Care South | EC South 5 | South | South Patch 8 | 3i6fnv3yyjpl8a2i7iv | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45189 | Medium | Court Manager | Top floor refuse area, hole in wall needs filling. | NULL
4902 | Alice Bye Court | ALICEBYE_S001 | H21 | Scheme | 2022-09-20 11:47 | FRA_4902200920220946.pdf | pickfordj | 4902200920220940 | Extra Care | Extra Care South | EC South 5 | South | South Patch 8 | 22ks4tdb0exl8a24t0g | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45189 | Medium | Court Manager | Hole in scooter store ceiling | NULL
4902 | Alice Bye Court | ALICEBYE_S001 | H21 | Scheme | 2022-09-20 11:47 | FRA_4902200920220946.pdf | pickfordj | 4902200920220940 | Extra Care | Extra Care South | EC South 5 | South | South Patch 8 | tcpim7nugf9l8a2873c | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45189 | Medium | Court Manager | Refuse room next to communal kitchen, requires door closer. | NULL
4904 | Gordon Palmer Court | JBGORDONPALMER_S001 | H21 | Scheme | 2022-10-07 10:25 | FRA_4904061020221938.pdf | pickfordj | 4904061020221930 | Retirement Housing | Mid South | Berks and Hampshire North | South | South Patch 8 | tbd9h491k1l8ya154d | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45572 | Low | Court Manager | 8 random doors tested, only two passed. I reccommend that all doors are fitted with overhead door closers as the perkos currently installed are not fit for purpose. | NULL
4905 | Orchard Court | JBORCHARD_S001 | H21 | Scheme | 2022-08-02 09:31 | FRA_4905020820220739.pdf | pickfordj | 4905020820220730 | Retirement Housing | Mid South | Berks and Hampshire North | South | South Patch 8 | scka5rm2ntsl6bw5rt3 | Observation Only | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Other | Smokes in flats and stairway,lobby. No need for a panel and detection system | NULL
4905 | Orchard Court | JBORCHARD_S001 | H21 | Scheme | 2022-08-02 09:31 | FRA_4905020820220739.pdf | pickfordj | 4905020820220730 | Retirement Housing | Mid South | Berks and Hampshire North | South | South Patch 8 | nuk6genj9wml6bwqqh8 | Low Risk closed | Risk Closed | 44777.5725 | Obs6 | Fire Hazards - Elimination & Control | 45506 | Low | Court Manager | Sign to be put up to tell residents to clean. Machine does also tell you to change. | Sign up in laundry remove items under stairs report door closure
4908 | Windsor Court | JBWINDSOR_S001 | H21 | Scheme | 2022-07-01 19:24 | FRA_4908010720221517.pdf | pickfordj | 4908010720221510 | Retirement Housing | Mid South | Berks and Hampshire North | South | South Patch 8 | t6j1jqjwbqbl52k10q9 | Medium Risk closed | Risk Closed | 44810.5384 | Obs6 | Fire Hazards - Elimination & Control | 45108 | Medium | Court Manager | Please ensure there is sufficient signage in laundry room detailing how and why tumble dryer filters need cleaning after each use | New Signage put up in Laundry and copy sent with September Newsletter
4909 | Willow Court | JBWILLOW_S001 | H21 | Scheme | 2022-07-26 11:32 | FRA_4909260720220945.pdf | pickfordj | 4909260720220940 | Retirement Housing | Mid South | Berks and Hampshire North | South | South Patch 8 | wnxox9alszl61yd6vg | Medium Risk closed | Risk Closed | 44824.4774 | Obs6 | Fire Hazards - Elimination & Control | 45133 | Medium | Court Manager | Mobility scooters to be pat tested to use communal charging points | PAT TEST COMPLETED ON MOBILITY SCOOTERS. CERTIFICATE STORED ON SHAREPOINT/ WILLOW/PUBLIC/FRA
4910 | Woodrow Court | JBWOODROW_S001 | H21 | Scheme | 2022-01-11 12:43 | FRA_4910110120221100.pdf | AhmadW | 4910110120221100 | Retirement Housing | Mid South | Berks and Hampshire North | South | South Patch 8 | 4panywqprfjkya1280h | Observation Only | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Other | Detection system in main block only. Resident blocks have hard wired smoke detectors in the landing area | NULL
4911 | Beeches Manor | BEECHESMANOR_S001 | H21 | Scheme | 2022-08-09 10:32 | FRA_4911080820221910.pdf | pickfordj | 4911080820221910 | Extra Care | Extra Care South | EC South 5 | South | South Patch 4 | cwimpkv53aal6lx30gk | Low Risk closed | Risk Closed | 44789.4028 | Obs4 | The Occupant - Information Provided By The Court Manager | 45513 | Low | Court Manager | Cm has completed person centered Eva plan but wants to speak to fire brigade about this | Meeting with Local authority fire service 31st August
4911 | Beeches Manor | BEECHESMANOR_S001 | H21 | Scheme | 2022-08-09 10:32 | FRA_4911080820221910.pdf | pickfordj | 4911080820221910 | Extra Care | Extra Care South | EC South 5 | South | South Patch 4 | 8i927h40sxtl6lxobv1 | Observation Only | Risk Closed | 44789.4033 | Obs13 | Other Relevant Fixed Systems | NULL | N/A | Court Manager | Dry riser | Certification scheduled for 17th August
4911 | Beeches Manor | BEECHESMANOR_S001 | H21 | Scheme | 2022-08-09 10:32 | FRA_4911080820221910.pdf | pickfordj | 4911080820221910 | Extra Care | Extra Care South | EC South 5 | South | South Patch 4 | osz14pk12zl6lxuzkw | Medium Risk to be actioned | Risk Open | NULL | Obs12 | Automatic Fire Systems i.e. Suppression System | 45147 | Medium | M&E Team | Appears that there is an unknown sprinkler system installed. Serviced annually by Compco, however sprinkler not wired up, but it is a system fed by cold water supply and it does send a signal to fire panel. CM to speak with contracts team to establish further details | NULL
4911 | Beeches Manor | BEECHESMANOR_S001 | H21 | Scheme | 2022-08-09 10:32 | FRA_4911080820221910.pdf | pickfordj | 4911080820221910 | Extra Care | Extra Care South | EC South 5 | South | South Patch 4 | q7jl60hkl6ly6ai7 | High Risk Overdue | Risk Open | NULL | Obs16 | Testing And Maintenance | 44874 | High | M&E Team | Dry riser appears to never have been tested. No certs available and nothing that i can find on our system | NULL
5001 | Jackson Court | JACKSON_S001 | H21 | Scheme | 2022-06-13 09:49 | FRA_5001110620220937.pdf | doerrd | 5001110620220930 | Retirement Housing | Mid South | Glos Oxford and South Bucks | Central | Central Patch 1 | 5uhje30dks8l49mkevy | Observation Only | Risk Closed | 44732.5448 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Court Manager needs to arrange for the installation of a smoking bin to the patio area. | New smoking bin installed
5001 | Jackson Court | JACKSON_S001 | H21 | Scheme | 2022-06-13 09:49 | FRA_5001110620220937.pdf | doerrd | 5001110620220930 | Retirement Housing | Mid South | Glos Oxford and South Bucks | Central | Central Patch 1 | 30g544pekd4l49mkeul | Medium Risk closed | Risk Closed | 44735.476 | Obs6 | Fire Hazards - Elimination & Control | 45088 | Medium | Court Manager | Court managers office has extension leads in use around the desk some are plugged into another extension lead. | Connected both extension leads directly to the socket.
5001 | Jackson Court | JACKSON_S001 | H21 | Scheme | 2022-06-13 09:49 | FRA_5001110620220937.pdf | doerrd | 5001110620220930 | Retirement Housing | Mid South | Glos Oxford and South Bucks | Central | Central Patch 1 | 0mqu3f22so9gl4chfje9 | Low Risk closed | Risk Closed | 44748.5769 | Obs1 | The Building | 45456 | Low | Court Manager | Under stairs cupboard in the communal lounge has a bundle if cables that is not sufficiently sealed. This needs to be treated from both sides to prevent smoke and fire spread. | Sealed from both sides
5001 | Jackson Court | JACKSON_S001 | H21 | Scheme | 2022-06-13 09:49 | FRA_5001110620220937.pdf | doerrd | 5001110620220930 | Retirement Housing | Mid South | Glos Oxford and South Bucks | Central | Central Patch 1 | xamsr6vavql4chpznw | Medium Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45090 | Medium | Surveyor | Following the renovation of the court managers property into two flats the fire zone plan needs updating to reflect the new layout. | NULL
5001 | Jackson Court | JACKSON_S001 | H21 | Scheme | 2022-06-13 09:49 | FRA_5001110620220937.pdf | doerrd | 5001110620220930 | Retirement Housing | Mid South | Glos Oxford and South Bucks | Central | Central Patch 1 | ztw28op59ql4chkoqi | Low Risk to be actioned | Risk Open | NULL | Obs1 | The Building | 45456 | Low | Court Manager | There are a couple if holes around cables in the communal hallway to the toilet, Apollo server cupboard and the guest bedroom cupboard that need sealing with intumescent sealant. | NULL
5002 | Frank Howe Court | FRANKHOWE_S001 | H21 | Scheme | 2022-01-26 19:39 | FRA_5002260120221420.pdf | doerrd | 5002260120221420 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | ysjlsrrjskokyvoh4u3 | Low Risk closed | Risk Closed | 44613.5075 | Obs6 | Fire Hazards - Elimination & Control | 45317 | Low | Court Manager | Pallets have been left to the side of the court. These need removing. | Removed by gardens 15.2.22
5002 | Frank Howe Court | FRANKHOWE_S001 | H21 | Scheme | 2022-01-26 19:39 | FRA_5002260120221420.pdf | doerrd | 5002260120221420 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | b9pqr5bez4pkyvxcbpz | Observation Only | Risk Closed | 44732.6788 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Surveyor | Roof spaces above the first floor corridors are open spaces without compartment separation along its length. This risk is mitigated by detection in the roof spaces. | Confirmed that the risk is mitigated by detection.
5002 | Frank Howe Court | FRANKHOWE_S001 | H21 | Scheme | 2022-01-26 19:39 | FRA_5002260120221420.pdf | doerrd | 5002260120221420 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | e4k4nqfm0zakyvnffxr | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45317 | Low | Surveyor | Court managers office has trailing leads and extension leads. | NULL
5002 | Frank Howe Court | FRANKHOWE_S001 | H21 | Scheme | 2022-01-26 19:39 | FRA_5002260120221420.pdf | doerrd | 5002260120221420 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | ortayzkxxadkyvxoq42 | Low Risk closed | Risk Closed | 44629.4352 | Obs8 | Measures To Limit Fire Spread And Development | 45317 | Low | Court Manager | Laundry room fire door closer requires adjustment as it doesn't close fully. This is the laundry near flat 21. | Contractor attended to ease and adjust fire doors
5002 | Frank Howe Court | FRANKHOWE_S001 | H21 | Scheme | 2022-01-26 19:39 | FRA_5002260120221420.pdf | doerrd | 5002260120221420 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | ndsyjspa6bpkyvmx9xq | Observation Only | Risk Closed | 44732.6784 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Surveyor | Hot works permits are not currently used, this should be looked into as part of the repairs and planned maintenance contracts | None to take
5003 | Scott Evans Court | SCOTTEVAN_S001 | H21 | Scheme | 2022-06-08 15:57 | FRA_5003080620220854.pdf | doerrd | 5003080620220850 | Retirement Housing | Mid South | Glos Oxford and South Bucks | Central | Central Patch 1 | j8qwn7hv5lrl45eg9si | Observation Only | Risk Closed | 44729.4833 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Hot works permits are not currently used | Hot works are avoided and very rarely used. We have full time court managers on site and Risk is minimal.
5003 | Scott Evans Court | SCOTTEVAN_S001 | H21 | Scheme | 2022-06-08 15:57 | FRA_5003080620220854.pdf | doerrd | 5003080620220850 | Retirement Housing | Mid South | Glos Oxford and South Bucks | Central | Central Patch 1 | ml2nmmjifkl45gti6b | Medium Risk closed | Risk Closed | 44729.5398 | Obs6 | Fire Hazards - Elimination & Control | 45085 | Medium | Court Manager | There is an accumulation of materials in the bin store area that poses an arson risk. These need to be removed. | Arranged for them to be removed and disposed of. This has now been completed.
5003 | Scott Evans Court | SCOTTEVAN_S001 | H21 | Scheme | 2022-06-08 15:57 | FRA_5003080620220854.pdf | doerrd | 5003080620220850 | Retirement Housing | Mid South | Glos Oxford and South Bucks | Central | Central Patch 1 | kyhq852kolfl45eahy3 | Observation Only | Risk Closed | 44732.6826 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Surveyor | Court managers office has extension leads in use around the desk area these are PAT tested but addition sockets will be needed in future. | IT are starting a project that will improve the office wiring.
5003 | Scott Evans Court | SCOTTEVAN_S001 | H21 | Scheme | 2022-06-08 15:57 | FRA_5003080620220854.pdf | doerrd | 5003080620220850 | Retirement Housing | Mid South | Glos Oxford and South Bucks | Central | Central Patch 1 | b40mzcek0el45e3i6c | Low Risk closed | Risk Closed | 44729.5408 | Obs4 | The Occupant - Information Provided By The Court Manager | 45451 | Low | Court Manager | Additional information needs collating to detail the high risk residents evacuation plan and to make this information available in the fire box. | Retirement living court. No evacuation plans needed for this court.
5003 | Scott Evans Court | SCOTTEVAN_S001 | H21 | Scheme | 2022-06-08 15:57 | FRA_5003080620220854.pdf | doerrd | 5003080620220850 | Retirement Housing | Mid South | Glos Oxford and South Bucks | Central | Central Patch 1 | 8075jisj10xl45gxm2k | Observation Only | Risk Closed | 44859.81 | Obs1 | The Building | NULL | N/A | Surveyor | Compartmentation is breached by cables and services in several positions within the roof spaces. Detection in all areas does mitigate this risk to an acceptable level however when future planned work is carried out it would be prudent to rectify this issue. | Confirmed that detection mitigates the risk suitably.
5004 | Frederick Smith Court | FREDERICKSMI_S001 | H21 | Scheme | 2022-01-11 17:15 | FRA_5004110120221150.pdf | doerrd | 5004110120221150 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | auup6i5h3aikya1yw8n | Medium Risk closed | Risk Closed | 44628.478 | Obs6 | Fire Hazards - Elimination & Control | 44937 | Medium | Court Manager | Extension lead has been used in the roof space outside flat 11 cable is under tension two more double sockets should be installed to provide enough power points. | Contractor attended 8.3.22.
5004 | Frederick Smith Court | FREDERICKSMI_S001 | H21 | Scheme | 2022-01-11 17:15 | FRA_5004110120221150.pdf | doerrd | 5004110120221150 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | c6emxps67i4kya1zcx5 | Low Risk closed | Risk Closed | 44573.4608 | Obs10 | Fire Safety And Notices | 45302 | Low | Court Manager | Fire safety notices need completing in the laundry room and by flat 19 | Updated 12.1.22
5004 | Frederick Smith Court | FREDERICKSMI_S001 | H21 | Scheme | 2022-01-11 17:15 | FRA_5004110120221150.pdf | doerrd | 5004110120221150 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | bybvx8zwwd9kya2qpez | Medium Risk closed | Risk Closed | 44721.4062 | Obs2 | Means Of Giving Warning In Case Of Fire | 44937 | Medium | Court Manager | The fire alarm call point to the boiler room has been removed with the cable left coiled. This needs reinstalling. | Quote requested, contractor attended to complete.
5004 | Frederick Smith Court | FREDERICKSMI_S001 | H21 | Scheme | 2022-01-11 17:15 | FRA_5004110120221150.pdf | doerrd | 5004110120221150 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | 3am0xgca8e4kya1yw9g | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44937 | Medium | Court Manager | Fire stopping to pipes and cables is required in communal roof space outside flat 11 | NULL
5004 | Frederick Smith Court | FREDERICKSMI_S001 | H21 | Scheme | 2022-01-11 17:15 | FRA_5004110120221150.pdf | doerrd | 5004110120221150 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | 6rdplkxwldkya1yw6p | Medium Risk closed | Risk Closed | 44732.6781 | Obs1 | The Building | 44937 | Medium | Surveyor | Compartment walls do not extend through the roof voids outside the lift. Detection is present across the whole roof. | Consulted with management and it is agreed that due to detection and zoning this mitigates the risk to an acceptable level. I would like to see some separation in future so will try to include thus in future planned maintenance.
5004 | Frederick Smith Court | FREDERICKSMI_S001 | H21 | Scheme | 2022-01-11 17:15 | FRA_5004110120221150.pdf | doerrd | 5004110120221150 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | jz1y08456bgkya21ex0 | Low Risk closed | Risk Closed | 44622.4907 | Obs11 | Fire Fighting Equipment | 45302 | Low | Court Manager | Fire extinguisher signage in the boiler room needs updating. | New signage purchased and installed.
5004 | Frederick Smith Court | FREDERICKSMI_S001 | H21 | Scheme | 2022-01-11 17:15 | FRA_5004110120221150.pdf | doerrd | 5004110120221150 | Retirement Housing | Mid West | Warwickshire and Northamptonshire | Central | Central Patch 1 | p9rst3stuu8kya1yw7q | Low Risk closed | Risk Closed | 44573.4581 | Obs4 | The Occupant - Information Provided By The Court Manager | 45302 | Low | Court Manager | The sheet detailing the high medium and low risk residents should be colour coded. Please use the newer template to make identification easier. | Updated on 11.1.22
5113 | Brown Edge Road | BROWNEDGERD_S001 | ODH | Scheme | 2022-01-12 17:48 | FRA_5113120120221738.pdf | mitchellj1 | 5113120120221730 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | puvnobgpdkkybttk3n | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45303 | Low | Court Manager | Ensure exit route to assembly point remains unobstructed at all times. | NULL
5113 | Brown Edge Road | BROWNEDGERD_S001 | ODH | Scheme | 2022-01-12 17:48 | FRA_5113120120221738.pdf | mitchellj1 | 5113120120221730 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | omqwapqijhikybttk08 | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | The scheme contains residents living independently. | NULL
5113 | Brown Edge Road | BROWNEDGERD_S001 | ODH | Scheme | 2022-01-12 17:48 | FRA_5113120120221738.pdf | mitchellj1 | 5113120120221730 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | jri7j7jlg4kybttk2c | Medium Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 44938 | Medium | Court Manager | Court Manager to book onto the fire safety manager course. | NULL
5113 | Brown Edge Road | BROWNEDGERD_S001 | ODH | Scheme | 2022-01-12 17:48 | FRA_5113120120221738.pdf | mitchellj1 | 5113120120221730 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | 6xu9x0iccthkybttk8s | Low Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45303 | Low | Court Manager | Include fire safety training records in folder to evidence training. | NULL
5113 | Brown Edge Road | BROWNEDGERD_S001 | ODH | Scheme | 2022-01-12 17:48 | FRA_5113120120221738.pdf | mitchellj1 | 5113120120221730 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | 5f7jqv6meu4kybttk67 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45303 | Low | Court Manager | No fire doors internally, these should be installed as part of the remodel,. | NULL
5113 | Brown Edge Road | BROWNEDGERD_S001 | ODH | Scheme | 2022-01-12 17:48 | FRA_5113120120221738.pdf | mitchellj1 | 5113120120221730 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | 1elr1wfdomckybttjz4 | Observation Only | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | The court manager office and communal space is covered by local detection linked to the warden call/helpline monitoring office, there is no fire panel in place, the helpline connection is tested every morning by the CM. Residents of the bungalows have a choice of the helpline service. | NULL
5113 | Brown Edge Road | BROWNEDGERD_S001 | ODH | Scheme | 2022-01-12 17:48 | FRA_5113120120221738.pdf | mitchellj1 | 5113120120221730 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | e3kcmnvuxmqkybttk7a | Low Risk to be actioned | Risk Open | NULL | Obs9 | Escape Lighting | 44959 | Low | Court Manager | It is recommended that emergency lighting be installed to common areas and externally. | NULL
5113 | Brown Edge Road | BROWNEDGERD_S001 | ODH | Scheme | 2022-01-12 17:48 | FRA_5113120120221738.pdf | mitchellj1 | 5113120120221730 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | 8bsej2hph56kybttk1e | Observation Only | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | NULL | N/A | Surveyor | No fire box as the bungalows have their own entrance and residents live independently. | NULL
5113 | Brown Edge Road | BROWNEDGERD_S001 | ODH | Scheme | 2022-01-12 17:48 | FRA_5113120120221738.pdf | mitchellj1 | 5113120120221730 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | zgi6lmso1gdkybttk56 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45303 | Low | Court Manager | Exit doors open inwards and are key barrel operated, these should be upgraded to push bar/pad doors, consider installing thumb turns in the interim. | NULL
5122 | Chew Vale | CHEWVALE_S001 | ODH | Scheme | 2022-01-18 08:01 | FRA_5122180120220711.pdf | mitchellj1 | 5122180120220710 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | xovnvwl8eukyjswqjz | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44953 | Low | Court Manager | Door from lounge to conservatory doesnt close properly, this will be addressed as part of the planned works, if these don't go ahead this should be addressed within the action timescale. | NULL
5122 | Chew Vale | CHEWVALE_S001 | ODH | Scheme | 2022-01-18 08:01 | FRA_5122180120220711.pdf | mitchellj1 | 5122180120220710 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | bfkafsplbpbkyjtmdcg | Observation Only | Risk Closed | 44904.4241 | Obs15 | Management Of Fire Safety | NULL | N/A | Surveyor | All tests are recorded electronically on excel. | NA
5122 | Chew Vale | CHEWVALE_S001 | ODH | Scheme | 2022-01-18 08:01 | FRA_5122180120220711.pdf | mitchellj1 | 5122180120220710 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | bhycvzvtz6kyjtq8t1 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45309 | Low | Court Manager | The conservatory exit doesn't have fire exit signage so it's assumed this is not a designated emergency exit, if the area is used frequently consider installing a thumb turn in place of the barrel to allow for fast exit. | NULL
5122 | Chew Vale | CHEWVALE_S001 | ODH | Scheme | 2022-01-18 08:01 | FRA_5122180120220711.pdf | mitchellj1 | 5122180120220710 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | a8ho7gn0ppfkyjsqqgl | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45309 | Low | Court Manager | Mobility scooter is being stored (not charging at time of survey) in lift lobby area at the time of survey. | NULL
5122 | Chew Vale | CHEWVALE_S001 | ODH | Scheme | 2022-01-18 08:01 | FRA_5122180120220711.pdf | mitchellj1 | 5122180120220710 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | d3wy6oppd89kyjt7knc | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45309 | Low | Court Manager | Upgrade 'do not use lift signs to more visible signs, required throughout Primrose and on the 1st floor of Coombes. | NULL
5122 | Chew Vale | CHEWVALE_S001 | ODH | Scheme | 2022-01-18 08:01 | FRA_5122180120220711.pdf | mitchellj1 | 5122180120220710 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 3uw5u5azs62kyjt9e98 | Low Risk to be actioned | Risk Open | NULL | Obs11 | Fire Fighting Equipment | 44953 | Low | M&E Team | Fire extinguishers aren't P50 as per h21 policy but are serviced as part of an an going maintenance contract. | NULL
5122 | Chew Vale | CHEWVALE_S001 | ODH | Scheme | 2022-01-18 08:01 | FRA_5122180120220711.pdf | mitchellj1 | 5122180120220710 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 539uuisugfbkyjt58f6 | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 44953 | Low | Surveyor | Fire action notices require upgrading to approved H21 signs, this will be done as part of re-zoning works. | NULL
5122 | Chew Vale | CHEWVALE_S001 | ODH | Scheme | 2022-01-18 08:01 | FRA_5122180120220711.pdf | mitchellj1 | 5122180120220710 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | merthm65h5rkyjsb7fa | Medium Risk to be actioned | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | 44944 | Medium | Court Manager | No detection visible in the conservatory area, works are planned to this area which will introduce detection. If these don't go ahead this should be addressed by fitting a device within the action timescale. | NULL
5122 | Chew Vale | CHEWVALE_S001 | ODH | Scheme | 2022-01-18 08:01 | FRA_5122180120220711.pdf | mitchellj1 | 5122180120220710 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | ofes55d69ekyjt3llg | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 44953 | Low | Court Manager | Action notices should be at every manual call point (second floor Primrose House is missing one). | NULL
5122 | Chew Vale | CHEWVALE_S001 | ODH | Scheme | 2022-01-18 08:01 | FRA_5122180120220711.pdf | mitchellj1 | 5122180120220710 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | r1j6kthjfikyjt1tl6 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44953 | Low | Court Manager | Gap in store door under stairs at Coombes house | NULL
5139 | Holland Close | HOLLANDCLOSE_S001 | ODH | Scheme | 2021-12-21 17:02 | FRA_5139211220210842.pdf | mitchellj1 | 5139211220210840 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | qyh81bn19rikxg461jz | Observation Only | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | NULL | N/A | Court Manager | Guest rooms fire exit door is operated by thumb turn and opens inwards. | NULL
5139 | Holland Close | HOLLANDCLOSE_S001 | ODH | Scheme | 2021-12-21 17:02 | FRA_5139211220210842.pdf | mitchellj1 | 5139211220210840 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | q5g1z81lb3kkxg1yqnx | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45281 | Low | Court Manager | Communal door between flats 17 and 18 has shrunk in the opening and so may be compromised. | NULL
5139 | Holland Close | HOLLANDCLOSE_S001 | ODH | Scheme | 2021-12-21 17:02 | FRA_5139211220210842.pdf | mitchellj1 | 5139211220210840 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | jnglt8iq8ikxg18fis | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44953 | Low | Court Manager | Gap in electric meter cupboard door adjacent flat 24 is too big. | NULL
5139 | Holland Close | HOLLANDCLOSE_S001 | ODH | Scheme | 2021-12-21 17:02 | FRA_5139211220210842.pdf | mitchellj1 | 5139211220210840 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | gj1mggdor19kxg2wras | Observation Only | Risk Open | NULL | Obs11 | Fire Fighting Equipment | NULL | N/A | Court Manager | Fire extinguishers aren't as per H21 policy but are covered by a servicing contract. | NULL
5139 | Holland Close | HOLLANDCLOSE_S001 | ODH | Scheme | 2021-12-21 17:02 | FRA_5139211220210842.pdf | mitchellj1 | 5139211220210840 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | h5fnxp95dubkxg2nlfk | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44953 | Low | Court Manager | Door near flat 12 doesn't close into rebate properly | NULL
5139 | Holland Close | HOLLANDCLOSE_S001 | ODH | Scheme | 2021-12-21 17:02 | FRA_5139211220210842.pdf | mitchellj1 | 5139211220210840 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 54yu0bmmm6hkxfz7bmm | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 44953 | Low | Court Manager | Do not use lift in the event of fire signs should be installed outside lifts. | NULL
5139 | Holland Close | HOLLANDCLOSE_S001 | ODH | Scheme | 2021-12-21 17:02 | FRA_5139211220210842.pdf | mitchellj1 | 5139211220210840 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 6i4lhznsgykkxg09vtv | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45281 | Low | Court Manager | Use of pink foam in external meter cupboard room to block housing flats 4, 5 & 6. Fire-stopping requires upgrading. | NULL
5139 | Holland Close | HOLLANDCLOSE_S001 | ODH | Scheme | 2021-12-21 17:02 | FRA_5139211220210842.pdf | mitchellj1 | 5139211220210840 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 3twtcbspcnhkxg1vm2k | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45281 | Low | Court Manager | Store cupboard door under stairs near flat 14 doesn't lock and is being held closed using cardboard, gaps around door also too big. | NULL
5139 | Holland Close | HOLLANDCLOSE_S001 | ODH | Scheme | 2021-12-21 17:02 | FRA_5139211220210842.pdf | mitchellj1 | 5139211220210840 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 3qvv6gd3rj4kxfzaeso | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 44953 | Low | Court Manager | Update fire action notices to company approved signage. | NULL
5139 | Holland Close | HOLLANDCLOSE_S001 | ODH | Scheme | 2021-12-21 17:02 | FRA_5139211220210842.pdf | mitchellj1 | 5139211220210840 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | cx3rawb3i4jkxg4bzdc | Observation Only | Risk Open | NULL | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | Court Manager to do fire safety manager refresher training which wasn't attended due to covid. | NULL
5139 | Holland Close | HOLLANDCLOSE_S001 | ODH | Scheme | 2021-12-21 17:02 | FRA_5139211220210842.pdf | mitchellj1 | 5139211220210840 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | c2s1b97lw39kxfzomvy | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45281 | Low | Court Manager | Items being stored outside flat 6 - this area should be sterile with no items on corridor. | NULL
5139 | Holland Close | HOLLANDCLOSE_S001 | ODH | Scheme | 2021-12-21 17:02 | FRA_5139211220210842.pdf | mitchellj1 | 5139211220210840 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | f6gbnyuiuqdkxg1d594 | Medium Risk to be actioned | Risk Open | NULL | Obs1 | The Building | 44916 | Medium | Court Manager | Void detection to communal loft space between flats 24 & 25 not in place - detector head has been removed and wiring cut. | NULL
5139 | Holland Close | HOLLANDCLOSE_S001 | ODH | Scheme | 2021-12-21 17:02 | FRA_5139211220210842.pdf | mitchellj1 | 5139211220210840 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | f3jtbfl7vinkxg2huyr | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45281 | Low | Court Manager | Items stored on the landing near flat 13 - this area should remain sterile. | NULL
5139 | Holland Close | HOLLANDCLOSE_S001 | ODH | Scheme | 2021-12-21 17:02 | FRA_5139211220210842.pdf | mitchellj1 | 5139211220210840 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | adfqephs3wkxg2cks5 | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45281 | Low | Court Manager | Consider additional signage externally on the external walkways and the outside area directing people to the fire exit and assembly point. | NULL
5139 | Holland Close | HOLLANDCLOSE_S001 | ODH | Scheme | 2021-12-21 17:02 | FRA_5139211220210842.pdf | mitchellj1 | 5139211220210840 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | y58r94c3cltkxg1unqa | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45281 | Low | Court Manager | Communal door between flats 14 and 15 doesn't close into rebate properly. | NULL
5139 | Holland Close | HOLLANDCLOSE_S001 | ODH | Scheme | 2021-12-21 17:02 | FRA_5139211220210842.pdf | mitchellj1 | 5139211220210840 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | vosdduvyowbkxg23gp9 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45281 | Low | Court Manager | Large gap to door outside flat 17 | NULL
5139 | Holland Close | HOLLANDCLOSE_S001 | ODH | Scheme | 2021-12-21 17:02 | FRA_5139211220210842.pdf | mitchellj1 | 5139211220210840 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | zzhhmgx5u8kxg351p1 | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45281 | Low | Court Manager | PAT test label suggests it was last done in 2018. | NULL
5154 | Lynmouth Avenue | LYNMOUTHAVE_S001 | ODH | Scheme | 2022-01-27 12:33 | FRA_5154260120221607.pdf | JohnsonD | 5154260120221600 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 8o20hc71x1kyvr1eod | Observation Only | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | NULL | N/A | Other | Note. Residents live independently in bungalows and therefore no requirement for red box and resident details. | NULL
5190 | Victoria Gardens | VICTORIAGDNS_S001 | ODH | Scheme | 2021-12-17 12:09 | FRA_5190171220211139.pdf | JohnsonD | 5190171220211130 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | dp2hf5c7ff4kxac16l0 | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45277 | Low | Court Manager | Pat and Hw testing expired. CM to arrange with M and E. | NULL
5195 | Walton House | WALTONHSE_S001 | ODH | Scheme | 2022-01-13 12:58 | FRA_5195130120221010.pdf | JohnsonD | 5195130120221010 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | 9iu2q286s84kycy4dfn | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45304 | Low | Court Manager | Some items not pat tested. Please arrange for this to be done. | NULL
5195 | Walton House | WALTONHSE_S001 | ODH | Scheme | 2022-01-13 12:58 | FRA_5195130120221010.pdf | JohnsonD | 5195130120221010 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | 7ad5ekhyngdkycy10y0 | Low Risk to be actioned | Risk Open | NULL | Obs16 | Testing And Maintenance | 45304 | Low | Court Manager | Service dates inspected for PV system. | NULL
5195 | Walton House | WALTONHSE_S001 | ODH | Scheme | 2022-01-13 12:58 | FRA_5195130120221010.pdf | JohnsonD | 5195130120221010 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | i6v7djln0mkycyfyjk | Medium Risk closed | Risk Closed | 44763.7581 | Obs6 | Fire Hazards - Elimination & Control | 44939 | Medium | Surveyor | Arrange for compartmentation survey to be carried out by specialist organization. | Type 4 works complete
5195 | Walton House | WALTONHSE_S001 | ODH | Scheme | 2022-01-13 12:58 | FRA_5195130120221010.pdf | JohnsonD | 5195130120221010 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | qbpcm69ztqrkycyw5fw | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44939 | Medium | Court Manager | Adjust Fire door outside flat 16 and 18. | NULL
5195 | Walton House | WALTONHSE_S001 | ODH | Scheme | 2022-01-13 12:58 | FRA_5195130120221010.pdf | JohnsonD | 5195130120221010 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | vnhn3tf2u8kycyteyx | Medium Risk closed | Risk Closed | 44630.3384 | Obs6 | Fire Hazards - Elimination & Control | 44939 | Medium | Surveyor | Check rising main duct as part of compartmentation survey. | Awaiting action from specialist contractor
5195 | Walton House | WALTONHSE_S001 | ODH | Scheme | 2022-01-13 12:58 | FRA_5195130120221010.pdf | JohnsonD | 5195130120221010 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | ysta1zjypifkycyk1ad | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44939 | Medium | Court Manager | Adjust Fire door adjacent to main entrance. And managers office. And near flat 6. | NULL
5201 | Lees House | LEES_S001 | ODH | Scheme | 2022-02-16 18:05 | FRA_5201160220221801.pdf | mitchellj1 | 5201160220221800 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | ybdgs80k1yjkzpv1mzq | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 44975 | Low | Court Manager | Full height blinds covering exit in Lounge, it has been arranged for the blinds to be removed however. | NULL
5201 | Lees House | LEES_S001 | ODH | Scheme | 2022-02-16 18:05 | FRA_5201160220221801.pdf | mitchellj1 | 5201160220221800 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | wnef7eip0tkzpv1mza | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45338 | Low | Surveyor | Laundry door doesn't close fully from an open position, please arrange for this to be addressed to ensure it closes fully. | NULL
5201 | Lees House | LEES_S001 | ODH | Scheme | 2022-02-16 18:05 | FRA_5201160220221801.pdf | mitchellj1 | 5201160220221800 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | zzftckzdrakzpv1mxc | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45338 | Low | Surveyor | Fire stopping around services leaving inner cleaning cupboard room wall, as well as outer cleaning cupboard room wall, above suspended ceiling tiles. | NULL
5201 | Lees House | LEES_S001 | ODH | Scheme | 2022-02-16 18:05 | FRA_5201160220221801.pdf | mitchellj1 | 5201160220221800 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | zkrrknn1xqbkzpv1myk | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 44975 | Low | Court Manager | The following fire exits are thumb-turn operated, consider suitability of this for residents and consider upgrading to a single motion opener such as a push bar: Bin store Laundry Lounge | NULL
5201 | Lees House | LEES_S001 | ODH | Scheme | 2022-02-16 18:05 | FRA_5201160220221801.pdf | mitchellj1 | 5201160220221800 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | z8ey0iw6jtokzpv1mwn | Observation Only | Risk Closed | 44904.4529 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Panel | N.a. note only.
5201 | Lees House | LEES_S001 | ODH | Scheme | 2022-02-16 18:05 | FRA_5201160220221801.pdf | mitchellj1 | 5201160220221800 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | ribrcwkeklikzpv1n2d | Observation Only | Risk Closed | 44904.4533 | Obs13 | Other Relevant Fixed Systems | NULL | N/A | Surveyor | AOV to stairwell. | N.a. photo only.
5201 | Lees House | LEES_S001 | ODH | Scheme | 2022-02-16 18:05 | FRA_5201160220221801.pdf | mitchellj1 | 5201160220221800 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | uehj9mttapqkzpv1n3j | Observation Only | Risk Open | NULL | Obs14 | Access By Emergency Services | NULL | N/A | Court Manager | Locks throughout service cupboards aren't on suited locks/keys. | NULL
5201 | Lees House | LEES_S001 | ODH | Scheme | 2022-02-16 18:05 | FRA_5201160220221801.pdf | mitchellj1 | 5201160220221800 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | kmwkuu56j2kzpv1mvs | Observation Only | Risk Open | NULL | Obs1 | The Building | NULL | N/A | Surveyor | No compartmentation between corridor roof space and the flats' roof space. Ensure this is in line with evacuation strategy. | NULL
5201 | Lees House | LEES_S001 | ODH | Scheme | 2022-02-16 18:05 | FRA_5201160220221801.pdf | mitchellj1 | 5201160220221800 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | 6aj3l128wlxkzpv1n2u | Low Risk to be actioned | Risk Open | NULL | Obs13 | Other Relevant Fixed Systems | 45338 | Low | Court Manager | No servicing records for AOV, testing/servicing should be arranged. | NULL
5201 | Lees House | LEES_S001 | ODH | Scheme | 2022-02-16 18:05 | FRA_5201160220221801.pdf | mitchellj1 | 5201160220221800 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | 1ve22fg0x4jkzpv1muy | Low Risk to be actioned | Risk Open | NULL | Obs1 | The Building | 45338 | Low | Surveyor | Cedral cladding to bays. | NULL
5201 | Lees House | LEES_S001 | ODH | Scheme | 2022-02-16 18:05 | FRA_5201160220221801.pdf | mitchellj1 | 5201160220221800 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | aqydfzezm6mkzpv1mxw | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44973 | Medium | Court Manager | Excess service cables in pile in meter cupboard, area is fire stopped but please can the responsible service contractor be informed of this and arrange to remove/fix safe. | NULL
5201 | Lees House | LEES_S001 | ODH | Scheme | 2022-02-16 18:05 | FRA_5201160220221801.pdf | mitchellj1 | 5201160220221800 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | a1dpyi431gwkzpv1n1f | Observation Only | Risk Open | NULL | Obs11 | Fire Fighting Equipment | NULL | N/A | Court Manager | Fire extinguishers aren't P50 as per H21 policy, but are serviced as part of an on going servicing contract. | NULL
5202 | Trinity House | TRINITY_S001 | ODH | Scheme | 2022-01-19 18:12 | FRA_5202190120221806.pdf | mitchellj1 | 5202190120221800 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | bjiosovqin4kyluw71v | Low Risk to be actioned | Risk Open | NULL | Obs11 | Fire Fighting Equipment | 44955 | Low | Court Manager | Fire extinguishers aren't P50 as per h21 policy but are covered by a servicing contract. | NULL
5202 | Trinity House | TRINITY_S001 | ODH | Scheme | 2022-01-19 18:12 | FRA_5202190120221806.pdf | mitchellj1 | 5202190120221800 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | 9g6vdjtix7kyluw6ym | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45310 | Low | Court Manager | No evidence of PAT testing to some mobility scooters, please ensure all scooters have been PAT tested. | NULL
5202 | Trinity House | TRINITY_S001 | ODH | Scheme | 2022-01-19 18:12 | FRA_5202190120221806.pdf | mitchellj1 | 5202190120221800 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | ej0hln4yvljkyluw6wt | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45310 | Low | Court Manager | Refuse door opposite flat 44 doesn't close properly. | NULL
5202 | Trinity House | TRINITY_S001 | ODH | Scheme | 2022-01-19 18:12 | FRA_5202190120221806.pdf | mitchellj1 | 5202190120221800 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | 23eziresn9akyluw6zr | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 44955 | Low | Court Manager | Fire action notices require updating to new h21 branded signs as per policy, these should be upgraded as part of re-zoning works. | NULL
5202 | Trinity House | TRINITY_S001 | ODH | Scheme | 2022-01-19 18:12 | FRA_5202190120221806.pdf | mitchellj1 | 5202190120221800 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | 1lwmjmsh14kyluw70o | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 44955 | Low | Court Manager | Change signs on old lift motor room/plant room to store cupboards. | NULL
5202 | Trinity House | TRINITY_S001 | ODH | Scheme | 2022-01-19 18:12 | FRA_5202190120221806.pdf | mitchellj1 | 5202190120221800 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | 7fa4b9dnmo4kyluw6tg | Medium Risk Overdue | Risk Open | NULL | Obs1 | The Building | 44590 | Medium | Court Manager | Breaches and expanding foam visible to partition walls in roof space. Survey to establish fire stopping requirements being done by third party. | NULL
5202 | Trinity House | TRINITY_S001 | ODH | Scheme | 2022-01-19 18:12 | FRA_5202190120221806.pdf | mitchellj1 | 5202190120221800 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | i7sagy0ynkikyluw6vr | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44955 | Low | Court Manager | Use of pink foam in boiler cupboard opposite library, next to guest flat. | NULL
5202 | Trinity House | TRINITY_S001 | ODH | Scheme | 2022-01-19 18:12 | FRA_5202190120221806.pdf | mitchellj1 | 5202190120221800 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | hbd9q89hl6kyluw6uv | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45310 | Low | Court Manager | Service cables and mains supply cables above suspended ceiling and in meter rooms are clipped to cable trays with plastic cable ties, these should be upgraded to metal ties. | NULL
5202 | Trinity House | TRINITY_S001 | ODH | Scheme | 2022-01-19 18:12 | FRA_5202190120221806.pdf | mitchellj1 | 5202190120221800 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | gn6ksdphtdvkyluw6xo | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45310 | Low | Court Manager | Boiler cupboard door in drying room opposite flat 43 has excessive gap. | NULL
5203 | Tandle View Court | TANDLE_S001 | ODH | Scheme | 2021-12-10 18:53 | FRA_5203101220211540.pdf | mitchellj1 | 5203101220211540 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | fyqe8s2s0dckx0k34dh | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 44945 | Low | Court Manager | Please udate the fire action notices with the standard H21 signage. | NULL
5203 | Tandle View Court | TANDLE_S001 | ODH | Scheme | 2021-12-10 18:53 | FRA_5203101220211540.pdf | mitchellj1 | 5203101220211540 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | iekslahajhakx0l9lr8 | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45270 | Low | Court Manager | Introduce additional signage to exit at the WC opposite the 1st floor lounge directing people to exit. Also fill in assembly point on fire action sign. | NULL
5203 | Tandle View Court | TANDLE_S001 | ODH | Scheme | 2021-12-10 18:53 | FRA_5203101220211540.pdf | mitchellj1 | 5203101220211540 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | j3y0a5kozckx0k34g8 | Low Risk to be actioned | Risk Open | NULL | Obs11 | Fire Fighting Equipment | 44945 | Low | M&E Team | Extinguishers aren't P50 as per H21 policy, however they are covered by a servicing contract. | NULL
5203 | Tandle View Court | TANDLE_S001 | ODH | Scheme | 2021-12-10 18:53 | FRA_5203101220211540.pdf | mitchellj1 | 5203101220211540 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | krnfdz3y69pkx0k5t4q | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45270 | Low | Court Manager | Corridor doors between flats 3 and 1 don't close properly. | NULL
5203 | Tandle View Court | TANDLE_S001 | ODH | Scheme | 2021-12-10 18:53 | FRA_5203101220211540.pdf | mitchellj1 | 5203101220211540 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | jo4x606eeakx0k3430 | Low Risk to be actioned | Risk Open | NULL | Obs1 | The Building | 44945 | Low | Surveyor | Determine the construction of the cedar cladding. | NULL
5203 | Tandle View Court | TANDLE_S001 | ODH | Scheme | 2021-12-10 18:53 | FRA_5203101220211540.pdf | mitchellj1 | 5203101220211540 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | m8wmij8dtjkx0mjojr | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45270 | Low | Court Manager | Can't see evidence of PAT tests on scooters however chargers are missing, please arrange for PAT testing where scooters haven't received it. | NULL
5203 | Tandle View Court | TANDLE_S001 | ODH | Scheme | 2021-12-10 18:53 | FRA_5203101220211540.pdf | mitchellj1 | 5203101220211540 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | tmvtbxc1tgdkx0k34a8 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44945 | Low | Court Manager | Excessive gaps in corridor doors adjacent hair salon. | NULL
5203 | Tandle View Court | TANDLE_S001 | ODH | Scheme | 2021-12-10 18:53 | FRA_5203101220211540.pdf | mitchellj1 | 5203101220211540 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | re8sviycmakx0k3477 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44945 | Low | Court Manager | Excessive gaps in corridor doors and flat 24 | NULL
5203 | Tandle View Court | TANDLE_S001 | ODH | Scheme | 2021-12-10 18:53 | FRA_5203101220211540.pdf | mitchellj1 | 5203101220211540 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | qkpd5falozkkx0k3487 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44945 | Low | Court Manager | Excessive gaps in the lounge doors adjacent flat 36 | NULL
5203 | Tandle View Court | TANDLE_S001 | ODH | Scheme | 2021-12-10 18:53 | FRA_5203101220211540.pdf | mitchellj1 | 5203101220211540 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | ph7o978nahkx0k346g | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44945 | Low | Court Manager | Excessive gaps in the refuse room door adjacent flats 31, 45 and 52. | NULL
5203 | Tandle View Court | TANDLE_S001 | ODH | Scheme | 2021-12-10 18:53 | FRA_5203101220211540.pdf | mitchellj1 | 5203101220211540 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | 7dsh37wpf47kx0k34hc | Low Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45270 | Low | Court Manager | Replace fire strategy and fire plan documents with updated H21documents which are available on WILMA. | NULL
5203 | Tandle View Court | TANDLE_S001 | ODH | Scheme | 2021-12-10 18:53 | FRA_5203101220211540.pdf | mitchellj1 | 5203101220211540 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | 67s120wv2bdkx0l6joh | Low Risk closed | Risk Closed | 44904.4179 | Obs8 | Measures To Limit Fire Spread And Development | 44945 | Low | Surveyor | Use of pink foam to service risers. | Action passed to Link Fire Safety who addressed as part of their style 4 works.
5203 | Tandle View Court | TANDLE_S001 | ODH | Scheme | 2021-12-10 18:53 | FRA_5203101220211540.pdf | mitchellj1 | 5203101220211540 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | 5ii231d9x08kx0lutlo | Observation Only | Risk Closed | 44904.3968 | Obs13 | Other Relevant Fixed Systems | NULL | N/A | Surveyor | Photo of call point for AOV | No action required
5203 | Tandle View Court | TANDLE_S001 | ODH | Scheme | 2021-12-10 18:53 | FRA_5203101220211540.pdf | mitchellj1 | 5203101220211540 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | 5y3h6tw6d5wkx0nazq4 | Medium Risk closed | Risk Closed | 44904.3985 | Obs1 | The Building | 44905 | Medium | Surveyor | Survey to be done by third party to roof voids and compartmentation . | Link Fire Safety undertook survey.
5203 | Tandle View Court | TANDLE_S001 | ODH | Scheme | 2021-12-10 18:53 | FRA_5203101220211540.pdf | mitchellj1 | 5203101220211540 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | 4ndq222pvnlkx0kx3up | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45270 | Low | Court Manager | Flat 20's door is catching on the carpet and not closing, please arrange for this to be eased. | NULL
5203 | Tandle View Court | TANDLE_S001 | ODH | Scheme | 2021-12-10 18:53 | FRA_5203101220211540.pdf | mitchellj1 | 5203101220211540 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | dsd01j66mcqkx0k345f | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44945 | Low | Court Manager | Holes in doors where previous closers removed adjacent flat 56 & 21. | NULL
5203 | Tandle View Court | TANDLE_S001 | ODH | Scheme | 2021-12-10 18:53 | FRA_5203101220211540.pdf | mitchellj1 | 5203101220211540 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | dnbjleds36jkx0k3495 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44945 | Low | Court Manager | Doors in corridor adjacent flat 36 dont close properly. | NULL
5203 | Tandle View Court | TANDLE_S001 | ODH | Scheme | 2021-12-10 18:53 | FRA_5203101220211540.pdf | mitchellj1 | 5203101220211540 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | 9d3jp8t9cgkx0k34bm | Medium Risk closed | Risk Closed | 44904.3978 | Obs8 | Measures To Limit Fire Spread And Development | 44580 | Medium | Surveyor | Compartmentation survey by third party has been arranged to identify sufficiency of compartmentation. | Link Fire Safety have undertaken type 4 fire stopping works and have identified additional risks which h21 are considering.
5203 | Tandle View Court | TANDLE_S001 | ODH | Scheme | 2021-12-10 18:53 | FRA_5203101220211540.pdf | mitchellj1 | 5203101220211540 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | 9a5pi57zjjskx0lfa8u | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45270 | Low | Court Manager | Please arrange for intumescent strip to be installed top side of flat 29 flat door/frame. | NULL
5203 | Tandle View Court | TANDLE_S001 | ODH | Scheme | 2021-12-10 18:53 | FRA_5203101220211540.pdf | mitchellj1 | 5203101220211540 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | arvj9hbhr5okx0k344a | Observation Only | Risk Closed | 44904.4176 | Obs5 | Evacuation Strategy And Training | NULL | N/A | Surveyor | Photo of person centered risk assessment. | No action required.
5203 | Tandle View Court | TANDLE_S001 | ODH | Scheme | 2021-12-10 18:53 | FRA_5203101220211540.pdf | mitchellj1 | 5203101220211540 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | w900z7e2korkx0k34ez | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45270 | Low | Court Manager | Introduce fire exit signage to direct people to the communal door serving the entrance lobby, near flat 1. | NULL
5204 | Wood Square | WOODSQUARE_S001 | ODH | Scheme | 2022-02-03 17:45 | FRA_5204030220221728.pdf | mitchellj1 | 5204030220221720 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 9t5t9f1islekz795rgi | Observation Only | Risk Closed | 44904.4363 | Obs11 | Fire Fighting Equipment | NULL | N/A | Surveyor | Fire extinguishers aren't P50 in accordance with H21 policy but are covered by a servicing contract. | N.A - note only.
5204 | Wood Square | WOODSQUARE_S001 | ODH | Scheme | 2022-02-03 17:45 | FRA_5204030220221728.pdf | mitchellj1 | 5204030220221720 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 8g7ln0hz2ylkz795rhv | Observation Only | Risk Closed | 44904.4364 | Obs13 | Other Relevant Fixed Systems | NULL | N/A | Surveyor | Smoke vent at end of corridor | N.A - note only
5204 | Wood Square | WOODSQUARE_S001 | ODH | Scheme | 2022-02-03 17:45 | FRA_5204030220221728.pdf | mitchellj1 | 5204030220221720 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | dr3yqjoaeebkz795r9l | Low Risk to be actioned | Risk Open | NULL | Obs1 | The Building | 44961 | Low | Surveyor | Check construction of cedar cladding to external bays. | NULL
5204 | Wood Square | WOODSQUARE_S001 | ODH | Scheme | 2022-02-03 17:45 | FRA_5204030220221728.pdf | mitchellj1 | 5204030220221720 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 6nhbrf8jxndkz795rap | Medium Risk to be actioned | Risk Open | NULL | Obs1 | The Building | 44960 | Medium | Surveyor | No compartmentation between the flats and corridors in the roof space. | NULL
5204 | Wood Square | WOODSQUARE_S001 | ODH | Scheme | 2022-02-03 17:45 | FRA_5204030220221728.pdf | mitchellj1 | 5204030220221720 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 7dvzoxxlmuskz795ree | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44961 | Low | Court Manager | Gap between the communal fire doors adjacent flat 10 | NULL
5204 | Wood Square | WOODSQUARE_S001 | ODH | Scheme | 2022-02-03 17:45 | FRA_5204030220221728.pdf | mitchellj1 | 5204030220221720 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 7ixhpxxdxyokz795rdh | Low Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45325 | Low | Court Manager | Gate providing shortest route of exit to assembly point from lounge exit and back stairwell is locked with key operated lock, this should be removed as it prevents access to the assembly point. | NULL
5204 | Wood Square | WOODSQUARE_S001 | ODH | Scheme | 2022-02-03 17:45 | FRA_5204030220221728.pdf | mitchellj1 | 5204030220221720 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | pp7v07nnufkz795rfh | Observation Only | Risk Closed | 44904.4377 | Obs10 | Fire Safety And Notices | NULL | N/A | Surveyor | Fire action notices require updating to new signage as per h21 policy. | Following rezoning works the correct signage to suit the evacuation strategy will be installed.
5204 | Wood Square | WOODSQUARE_S001 | ODH | Scheme | 2022-02-03 17:45 | FRA_5204030220221728.pdf | mitchellj1 | 5204030220221720 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | rfpebfa34qokz795rlm | Observation Only | Risk Open | NULL | Obs16 | Testing And Maintenance | NULL | N/A | Court Manager | Please record fire alarms (false and genuine) in fire safety folder. | NULL
5204 | Wood Square | WOODSQUARE_S001 | ODH | Scheme | 2022-02-03 17:45 | FRA_5204030220221728.pdf | mitchellj1 | 5204030220221720 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | tvqd33oj7gkz795rkg | Low Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45325 | Low | Surveyor | Weekly tests and recording of activations are being done on computer and not in the fire risk folder. Surveyor to confirm that CM's are to record tests, activations etc in the folder. Tests are being recorded on Excel document in shared drive. Activations/false alarms are being reported via ERICA only. | NULL
5204 | Wood Square | WOODSQUARE_S001 | ODH | Scheme | 2022-02-03 17:45 | FRA_5204030220221728.pdf | mitchellj1 | 5204030220221720 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | im3r2msv4kekz795rbr | Observation Only | Risk Closed | 44904.437 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel | N.A - note only
5204 | Wood Square | WOODSQUARE_S001 | ODH | Scheme | 2022-02-03 17:45 | FRA_5204030220221728.pdf | mitchellj1 | 5204030220221720 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | hd6xjo9ghp7kz795rci | Low Risk to be actioned | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | 44961 | Low | Court Manager | Call point not visible in Lounge due to cabinets being in place, please arrange for cabinets to be removed. | NULL
5205 | School House Flats | SCHOOLHSE_S001 | ODH | Scheme | 2022-07-12 20:27 | FRA_5205120720220839.pdf | mitchellj1 | 5205120720220830 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | j56fdvmmw5el5i1vbgu | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45122 | Low | Court Manager | The external egress path isn't 900mm all the way around the building. | NULL
5205 | School House Flats | SCHOOLHSE_S001 | ODH | Scheme | 2022-07-12 20:27 | FRA_5205120720220839.pdf | mitchellj1 | 5205120720220830 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | i38qljqud6bl5i9znmr | Medium Risk to be actioned | Risk Open | NULL | Obs16 | Testing And Maintenance | 45119 | Medium | M&E Team | No test certificate for the lightning protection, please arrange for this to be tested. | NULL
5205 | School House Flats | SCHOOLHSE_S001 | ODH | Scheme | 2022-07-12 20:27 | FRA_5205120720220839.pdf | mitchellj1 | 5205120720220830 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | u1cbka9hfll5hz370s | Observation Only | Risk Open | NULL | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | Fire service have attended to consult the Court Manager regarding the 2nr high risk residents. | NULL
5205 | School House Flats | SCHOOLHSE_S001 | ODH | Scheme | 2022-07-12 20:27 | FRA_5205120720220839.pdf | mitchellj1 | 5205120720220830 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | njb8sxiwzthl5hzthfu | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45122 | Low | Court Manager | Fire stopping required to cables leaving the electric meter room ceiling & wall to RHS as you walk in. | NULL
5205 | School House Flats | SCHOOLHSE_S001 | ODH | Scheme | 2022-07-12 20:27 | FRA_5205120720220839.pdf | mitchellj1 | 5205120720220830 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 0144upttjs9hml5i1si79 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45485 | Low | Court Manager | There is a step down from one of the fire exits which could pose a hazard. | NULL
5205 | School House Flats | SCHOOLHSE_S001 | ODH | Scheme | 2022-07-12 20:27 | FRA_5205120720220839.pdf | mitchellj1 | 5205120720220830 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | f0hlplnynal5i2a886 | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45122 | Low | Court Manager | Cables near riser in communal lounge require fire stopping. | NULL
5205 | School House Flats | SCHOOLHSE_S001 | ODH | Scheme | 2022-07-12 20:27 | FRA_5205120720220839.pdf | mitchellj1 | 5205120720220830 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 86ukmu580hel5i0f290 | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45485 | Low | Court Manager | Only 1 scooter in EV store but no charge lead with it, please confirm the scooter has been PAT tested. | NULL
5205 | School House Flats | SCHOOLHSE_S001 | ODH | Scheme | 2022-07-12 20:27 | FRA_5205120720220839.pdf | mitchellj1 | 5205120720220830 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | ynxkpquhpjl5hv5qh2 | Observation Only | Risk Open | NULL | Obs11 | Fire Fighting Equipment | NULL | N/A | M&E Team | Fire extinguishers are not P50 as per company policy, but are covered by a servicing contract. | NULL
5207 | Lido House | LIDO_S001 | ODH | Scheme | 2022-02-08 18:45 | FRA_5207080220221844.pdf | mitchellj1 | 5207080220221840 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | wkn0wogxcxhkzeh263j | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45330 | Low | Surveyor | Introduce 'in the event of fire do not use lift' signage outside each lift. | NULL
5207 | Lido House | LIDO_S001 | ODH | Scheme | 2022-02-08 18:45 | FRA_5207080220221844.pdf | mitchellj1 | 5207080220221840 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | dxmk6zt7bwkzeh2602 | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44959 | Low | Surveyor | Fire stopping to meter cupboards: expanding foam around service cables in meter room. | NULL
5207 | Lido House | LIDO_S001 | ODH | Scheme | 2022-02-08 18:45 | FRA_5207080220221844.pdf | mitchellj1 | 5207080220221840 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | cej79u439mgkzeh262p | Low Risk closed | Risk Closed | 44904.4404 | Obs10 | Fire Safety And Notices | 44959 | Low | Surveyor | Fire action notices require updating to new signs as per h21 policy. | Re-zoning works are planned, appropriate signage will be installed following these works.
5207 | Lido House | LIDO_S001 | ODH | Scheme | 2022-02-08 18:45 | FRA_5207080220221844.pdf | mitchellj1 | 5207080220221840 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | 1r5tj37mbuikzeh25yi | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44959 | Low | Court Manager | Quite a few items (walkers etc) being stored in EV store. Residents should be told to remove items they don't use frequently so area can be cleared of stored items. | NULL
5207 | Lido House | LIDO_S001 | ODH | Scheme | 2022-02-08 18:45 | FRA_5207080220221844.pdf | mitchellj1 | 5207080220221840 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | 1rxji8pm4l9ikzeh25x7 | Low Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 44959 | Low | Court Manager | Additional signage directing people to the assembly point should be introduced. | NULL
5207 | Lido House | LIDO_S001 | ODH | Scheme | 2022-02-08 18:45 | FRA_5207080220221844.pdf | mitchellj1 | 5207080220221840 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | 72p6tdsio4ckzeh25vy | Observation Only | Risk Closed | 44904.4388 | Obs1 | The Building | NULL | N/A | Surveyor | Some breaches to roof space identified as part of high risk resident survey in 2021 | N.A - note only
5207 | Lido House | LIDO_S001 | ODH | Scheme | 2022-02-08 18:45 | FRA_5207080220221844.pdf | mitchellj1 | 5207080220221840 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | 5kc88q93lxikzeh264f | Observation Only | Risk Closed | 44904.4383 | Obs11 | Fire Fighting Equipment | NULL | N/A | Surveyor | Extinguishers aren't P50 as per policy, but are covered by a servicing contract. | N.A - note only
5207 | Lido House | LIDO_S001 | ODH | Scheme | 2022-02-08 18:45 | FRA_5207080220221844.pdf | mitchellj1 | 5207080220221840 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | o5gfk3pj0ndkzeh25ze | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45330 | Low | Court Manager | No evidence of PAT tests to scooters/vehicles in store, please ensure this is in place. | NULL
5207 | Lido House | LIDO_S001 | ODH | Scheme | 2022-02-08 18:45 | FRA_5207080220221844.pdf | mitchellj1 | 5207080220221840 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | jgteacdjkskzeh260z | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 44959 | Low | Surveyor | Both secondary block fire exit doors and fire exit in communal lounge are thumb turn operated consider suitability of these and consider upgrading to a single motion operated exit door. | NULL
5208 | Aster House | ASTER_S001 | ODH | Scheme | 2021-12-14 12:56 | FRA_5208141220211201.pdf | JohnsonD | 5208141220211200 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | jxryadi081hkx62ixk3 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45274 | Low | Court Manager | Riser cupboard door near kitchen and adjacent store door requires adjustments as gaps are excessive. | NULL
5208 | Aster House | ASTER_S001 | ODH | Scheme | 2021-12-14 12:56 | FRA_5208141220211201.pdf | JohnsonD | 5208141220211200 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | mbtt6gcziskx622nq0 | Medium Risk closed | Risk Closed | 44811.6602 | Obs1 | The Building | 44568 | Medium | Surveyor | It is recommended that a full compartmentation survey is carried out by a competent and certified assessor. | Assessment completed
5208 | Aster House | ASTER_S001 | ODH | Scheme | 2021-12-14 12:56 | FRA_5208141220211201.pdf | JohnsonD | 5208141220211200 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | ow8475pqifkx625q9f | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45274 | Low | Court Manager | A sign to guide residents to a suitable Assembly point is required. | NULL
5208 | Aster House | ASTER_S001 | ODH | Scheme | 2021-12-14 12:56 | FRA_5208141220211201.pdf | JohnsonD | 5208141220211200 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | oy0f1lvi15kkx62174u | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | There are 9 high risk residents. This is mainly due to mobility issues. | NULL
5208 | Aster House | ASTER_S001 | ODH | Scheme | 2021-12-14 12:56 | FRA_5208141220211201.pdf | JohnsonD | 5208141220211200 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | u2fdlgrumikx63426y | Observation Only | Risk Open | NULL | Obs14 | Access By Emergency Services | NULL | N/A | Other | Access is available for emergency services on all elevations. However, the rear of the scheme is shared with an adjacent housing estate. | NULL
5208 | Aster House | ASTER_S001 | ODH | Scheme | 2021-12-14 12:56 | FRA_5208141220211201.pdf | JohnsonD | 5208141220211200 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | u59jp3rdxwokx630wy0 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45274 | Low | Court Manager | Fire door to laundry requires adjustments as gaps are excessive. | NULL
5208 | Aster House | ASTER_S001 | ODH | Scheme | 2021-12-14 12:56 | FRA_5208141220211201.pdf | JohnsonD | 5208141220211200 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | ub7x6m234fpkx62eid9 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45274 | Low | Court Manager | Door to communal lounge requires adjustments as gaps are excessive. | NULL
5208 | Aster House | ASTER_S001 | ODH | Scheme | 2021-12-14 12:56 | FRA_5208141220211201.pdf | JohnsonD | 5208141220211200 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | sfjcq948d4fkx62v7de | Medium Risk Overdue | Risk Open | NULL | Obs7 | Fire Protection Measures | 44909 | Medium | Court Manager | Fire door closer adjacent to flat 30 inoperative. Requires immediate attention. | NULL
5208 | Aster House | ASTER_S001 | ODH | Scheme | 2021-12-14 12:56 | FRA_5208141220211201.pdf | JohnsonD | 5208141220211200 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | 68xj3zp0uodkx62176o | Medium Risk Overdue | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44568 | Medium | Court Manager | No evidence to confirm if HW testing has been completed. | NULL
5208 | Aster House | ASTER_S001 | ODH | Scheme | 2021-12-14 12:56 | FRA_5208141220211201.pdf | JohnsonD | 5208141220211200 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | bs5z5qgbcaukx62175t | Observation Only | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Filters checked weekly. | NULL
5209 | Hopwood Court | HOPWOOD_S001 | ODH | Scheme | 2022-04-29 16:47 | FRA_5209290420220750.pdf | mitchellj1 | 5209290420220750 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | ds4uwmsbxvql2k3zbbc | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45309 | Low | Court Manager | Introduce additional signage after gate to LHS of garden area to direct people to footpath which leads to assemnly point. | NULL
5209 | Hopwood Court | HOPWOOD_S001 | ODH | Scheme | 2022-04-29 16:47 | FRA_5209290420220750.pdf | mitchellj1 | 5209290420220750 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | 82r5b9uhp4l2kbowyc | Observation Only | Risk Open | NULL | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | Oldham court managers have been instructed to record weekly and monthly checks on a central spreadsheet stored on the Y drive. | NULL
5209 | Hopwood Court | HOPWOOD_S001 | ODH | Scheme | 2022-04-29 16:47 | FRA_5209290420220750.pdf | mitchellj1 | 5209290420220750 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | 9w6uufev82el2kc6sag | Observation Only | Risk Closed | 44904.4449 | Obs5 | Evacuation Strategy And Training | NULL | N/A | Surveyor | Third party care staff don't receive training from H21. | N.a. note only - advice has been sought from Alicia wheeler and circulated to Oldham OM's
5209 | Hopwood Court | HOPWOOD_S001 | ODH | Scheme | 2022-04-29 16:47 | FRA_5209290420220750.pdf | mitchellj1 | 5209290420220750 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | 6bqa54885kxl2k3r6ix | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45309 | Low | Court Manager | Flat 19 door catching on frame and preventing door closing fully. | NULL
5209 | Hopwood Court | HOPWOOD_S001 | ODH | Scheme | 2022-04-29 16:47 | FRA_5209290420220750.pdf | mitchellj1 | 5209290420220750 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | 6ie3uon5rhyl2kei99l | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45411 | Low | Court Manager | Flat 28 door not closing due to recently fitted carpet, arrange for door to be eased. | NULL
5209 | Hopwood Court | HOPWOOD_S001 | ODH | Scheme | 2022-04-29 16:47 | FRA_5209290420220750.pdf | mitchellj1 | 5209290420220750 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | 73psh950uqrl2k3ite4 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 44945 | Low | Court Manager | The following Fire exit doors are thumb turn operated: - lounge (near kitchen) - between flats 1 & 2 - Next to flat 8 - Next to flat 19 - Next to flat 14 Consider residents' abilities and suitability of thumb turn operation and consider installing a single motion egress door (push bar etc). | NULL
5209 | Hopwood Court | HOPWOOD_S001 | ODH | Scheme | 2022-04-29 16:47 | FRA_5209290420220750.pdf | mitchellj1 | 5209290420220750 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | q21qa8451msl2kdetb3 | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45411 | Low | Court Manager | Fire blanket in Hopwood suite and communal lounge requires servicing, please arrange for all blankets on site to be serviced. | NULL
5209 | Hopwood Court | HOPWOOD_S001 | ODH | Scheme | 2022-04-29 16:47 | FRA_5209290420220750.pdf | mitchellj1 | 5209290420220750 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | ou4uo1qci8l2kcy4af | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45411 | Low | Court Manager | Gap between door and jamb to ground floor BT/comms room cupboard is excessive, please arrange for a a certified joiner to attend and rectify. | NULL
5209 | Hopwood Court | HOPWOOD_S001 | ODH | Scheme | 2022-04-29 16:47 | FRA_5209290420220750.pdf | mitchellj1 | 5209290420220750 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | n019a10byfpl2kbx8wn | Observation Only | Risk Open | NULL | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | Fires and false alarms to be recorded in the fire safety file as well as Erica. | NULL
5209 | Hopwood Court | HOPWOOD_S001 | ODH | Scheme | 2022-04-29 16:47 | FRA_5209290420220750.pdf | mitchellj1 | 5209290420220750 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | l4sn0doandl2k3pmm2 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45309 | Low | Court Manager | Gaps around first floor cleaners cupboard door are excessive, these should be addressed by a joiner. | NULL
5209 | Hopwood Court | HOPWOOD_S001 | ODH | Scheme | 2022-04-29 16:47 | FRA_5209290420220750.pdf | mitchellj1 | 5209290420220750 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | hwrzh0lkgijl2k411gl | Low Risk to be actioned | Risk Open | NULL | Obs11 | Fire Fighting Equipment | 44945 | Low | M&E Team | Extinguishers aren't P50 but are serviced as part of a maintenance contract. | NULL
5209 | Hopwood Court | HOPWOOD_S001 | ODH | Scheme | 2022-04-29 16:47 | FRA_5209290420220750.pdf | mitchellj1 | 5209290420220750 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | hxxrduzg66gl2k3aldx | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45309 | Low | Court Manager | No evidence of PAT testing to mobility scooters in EV store, please ensure this has been done. | NULL
5209 | Hopwood Court | HOPWOOD_S001 | ODH | Scheme | 2022-04-29 16:47 | FRA_5209290420220750.pdf | mitchellj1 | 5209290420220750 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | hasv7v9ceoml2keb3xr | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45411 | Low | Court Manager | Resident at flat 25 reports his door isn't closing properly when the Windows are shut, the closer may need adjusting. | NULL
5209 | Hopwood Court | HOPWOOD_S001 | ODH | Scheme | 2022-04-29 16:47 | FRA_5209290420220750.pdf | mitchellj1 | 5209290420220750 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | whlbt5ey2dgl2k37ogu | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44945 | Low | Court Manager | Service cables above suspended ceiling in corridor near entrance lobby are clipped to the cable tray using plastic cable ties, these should be removed and clipped with metal ties throughout. Cables and wiring throughout meter room also clipped with plastic cable ties. | NULL
5209 | Hopwood Court | HOPWOOD_S001 | ODH | Scheme | 2022-04-29 16:47 | FRA_5209290420220750.pdf | mitchellj1 | 5209290420220750 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | xy62ujrnszhl2k3t7zv | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45309 | Low | Court Manager | There's two doors in the restaurant area leading to corridors in either direction, there's no fire exit signage directing people to either of the doors, this should be installed. | NULL
5209 | Hopwood Court | HOPWOOD_S001 | ODH | Scheme | 2022-04-29 16:47 | FRA_5209290420220750.pdf | mitchellj1 | 5209290420220750 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | wvvneuv9vakl2kbunvw | Low Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45411 | Low | Surveyor | Care staff don't receive training from housing 21. Ask H&S team about this. | NULL
5210 | Charles Morris House | CHARLESMORRIS_S001 | ODH | Scheme | 2022-07-05 17:07 | FRA_5210040720220649.pdf | mitchellj1 | 5210040720220640 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | q98blvfk08nl58d1o8z | Medium Risk Overdue | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44904 | Medium | Surveyor | Containment cover in first floor refuse room shows lack of fire stopping around service cables passing through floor. | NULL
5210 | Charles Morris House | CHARLESMORRIS_S001 | ODH | Scheme | 2022-07-05 17:07 | FRA_5210040720220649.pdf | mitchellj1 | 5210040720220640 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | tse1ewm6zuel56bylf1 | Observation Only | Risk Open | NULL | Obs11 | Fire Fighting Equipment | NULL | N/A | M&E Team | Fire extinguishers aren't all P50 as per H21 policy, they are however covered by an existing servicing contract. | NULL
5210 | Charles Morris House | CHARLESMORRIS_S001 | ODH | Scheme | 2022-07-05 17:07 | FRA_5210040720220649.pdf | mitchellj1 | 5210040720220640 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | 70tz7qmckl5l56bva65 | Observation Only | Risk Open | NULL | Obs1 | The Building | NULL | N/A | Court Manager | Link fire safety have recently completed fire-stopping and compartmentation works and are due to return to undertake additional fire stopping following the installation of the warden call system. | NULL
5210 | Charles Morris House | CHARLESMORRIS_S001 | ODH | Scheme | 2022-07-05 17:07 | FRA_5210040720220649.pdf | mitchellj1 | 5210040720220640 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | 63uo7sja8qql56oqg6c | Low Risk to be actioned | Risk Open | NULL | Obs1 | The Building | 45269 | Low | Surveyor | Fire stopping required between levels in refuse room adjacent flat 27 | NULL
5210 | Charles Morris House | CHARLESMORRIS_S001 | ODH | Scheme | 2022-07-05 17:07 | FRA_5210040720220649.pdf | mitchellj1 | 5210040720220640 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | 2fzasj01oxol56oko2e | Low Risk to be actioned | Risk Open | NULL | Obs1 | The Building | 45477 | Low | Surveyor | Penetration caused by data cables to wall in first floor lift lobby required fire-stopping. | NULL
5210 | Charles Morris House | CHARLESMORRIS_S001 | ODH | Scheme | 2022-07-05 17:07 | FRA_5210040720220649.pdf | mitchellj1 | 5210040720220640 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | admmlmn6709l58czkqy | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44951 | Low | Court Manager | Gap to corridor door near flat 18 is large. | NULL
5210 | Charles Morris House | CHARLESMORRIS_S001 | ODH | Scheme | 2022-07-05 17:07 | FRA_5210040720220649.pdf | mitchellj1 | 5210040720220640 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | cyq11xnlhe5l58cygix | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44951 | Low | Court Manager | Gap to Laundry door is large and a section of the architrave has been cut out near the closer. | NULL
5211 | Throstle Court | THROSTLE_S001 | ODH | Scheme | 2022-01-10 16:38 | FRA_5211100120220954.pdf | JohnsonD | 5211100120220950 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | 9b5vz2qbom4ky8kytza | Low Risk to be actioned | Risk Open | NULL | Obs16 | Testing And Maintenance | 45301 | Low | Court Manager | Ensure lightning protection is checked with compliance certification. | NULL
5211 | Throstle Court | THROSTLE_S001 | ODH | Scheme | 2022-01-10 16:38 | FRA_5211100120220954.pdf | JohnsonD | 5211100120220950 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | 3fd5tov04j2ky8j96x4 | Low Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45301 | Low | Court Manager | There is a temporary Court Manager in post covering long term sickness. Please confirm medium and long term management cover in due course. | NULL
5211 | Throstle Court | THROSTLE_S001 | ODH | Scheme | 2022-01-10 16:38 | FRA_5211100120220954.pdf | JohnsonD | 5211100120220950 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | 1ru779kt7ohky8wqg0w | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45301 | Low | Surveyor | Carry out compartment survey as detailed above. | NULL
5211 | Throstle Court | THROSTLE_S001 | ODH | Scheme | 2022-01-10 16:38 | FRA_5211100120220954.pdf | JohnsonD | 5211100120220950 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | i2sivb923zcky8k884h | Low Risk to be actioned | Risk Open | NULL | Obs11 | Fire Fighting Equipment | 44938 | Low | M&E Team | Upgrade fire fighting equipment to P50 type, in accordance with Housing 21 policy. | NULL
5212 | Old Mill House | OLDMILL_S001 | ODH | Scheme | 2022-02-09 18:42 | FRA_5212090220221310.pdf | mitchellj1 | 5212090220221310 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | iqhw3qnusmkzfkkf6p | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44969 | Low | Surveyor | Ground floor meter cupboard near refuse area near flat 17: incoming service cable has green expanding foam around it, this should be confirmed adequate by fire stopping contractor. | NULL
5212 | Old Mill House | OLDMILL_S001 | ODH | Scheme | 2022-02-09 18:42 | FRA_5212090220221310.pdf | mitchellj1 | 5212090220221310 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | im0c1umamfkzfkkf0j | Observation Only | Risk Closed | 44904.4416 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel | N.a - note only.
5212 | Old Mill House | OLDMILL_S001 | ODH | Scheme | 2022-02-09 18:42 | FRA_5212090220221310.pdf | mitchellj1 | 5212090220221310 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | ije1txws93qkzfkkf22 | Observation Only | Risk Closed | 44904.4391 | Obs5 | Evacuation Strategy And Training | NULL | N/A | Surveyor | Care staff are an external company but have all completed the fire safety awareness, only senior carers have completed the fire warden learning. | N.A - note only
5212 | Old Mill House | OLDMILL_S001 | ODH | Scheme | 2022-02-09 18:42 | FRA_5212090220221310.pdf | mitchellj1 | 5212090220221310 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | mfzxr54xeljkzfkkf2w | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45331 | Low | Surveyor | Doors between lounge and conservatory show large gaps and are out of line when closed. | NULL
5212 | Old Mill House | OLDMILL_S001 | ODH | Scheme | 2022-02-09 18:42 | FRA_5212090220221310.pdf | mitchellj1 | 5212090220221310 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | pwsyxxc3y1kzfkkfa7 | Observation Only | Risk Open | NULL | Obs11 | Fire Fighting Equipment | NULL | N/A | Court Manager | Fire extinguishers are not P50 type as per Housing 21 policy, however they are covered by a servicing contract. | NULL
5212 | Old Mill House | OLDMILL_S001 | ODH | Scheme | 2022-02-09 18:42 | FRA_5212090220221310.pdf | mitchellj1 | 5212090220221310 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | ppkc2ks0qsckzfkkf7l | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45331 | Low | Court Manager | Fire action notices aren't in accordance with Housing 21's policy. | NULL
5212 | Old Mill House | OLDMILL_S001 | ODH | Scheme | 2022-02-09 18:42 | FRA_5212090220221310.pdf | mitchellj1 | 5212090220221310 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | 1v15lctuwl3kzfkkf46 | Observation Only | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Surveyor | Ground floor, front elevation: Unable to determine adequacy of upvc cladding to ceiling and service cables fed above it. | NULL
5212 | Old Mill House | OLDMILL_S001 | ODH | Scheme | 2022-02-09 18:42 | FRA_5212090220221310.pdf | mitchellj1 | 5212090220221310 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | 1596zj9jimbkzfkkf1b | Observation Only | Risk Closed | 44904.4538 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire alarm zone plan | N.a. note only.
5212 | Old Mill House | OLDMILL_S001 | ODH | Scheme | 2022-02-09 18:42 | FRA_5212090220221310.pdf | mitchellj1 | 5212090220221310 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | 0lqt1r3vpvefkzfkkf95 | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45331 | Low | Court Manager | Do not use lift in the event of fire missing from ground floor lift entrance near flat 18, these should be in place outside each lift. | NULL
5212 | Old Mill House | OLDMILL_S001 | ODH | Scheme | 2022-02-09 18:42 | FRA_5212090220221310.pdf | mitchellj1 | 5212090220221310 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | 0fbqjtns9x5gkzfkkf5o | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45331 | Low | Surveyor | Ground floor meter room accessed via refuse area near flat 18: Service cable entering from floor has expanding foam around it, this should be fire stopped appropriately. | NULL
5212 | Old Mill House | OLDMILL_S001 | ODH | Scheme | 2022-02-09 18:42 | FRA_5212090220221310.pdf | mitchellj1 | 5212090220221310 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | 6kbold5fcg6kzfkkf4u | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44969 | Low | Surveyor | Ground floor meter cupboard accessed via refuse area near flat 18: service cables leaving through ceiling aren't fire stopped. | NULL
5212 | Old Mill House | OLDMILL_S001 | ODH | Scheme | 2022-02-09 18:42 | FRA_5212090220221310.pdf | mitchellj1 | 5212090220221310 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | aacmxmjinlikzfkkf8i | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45331 | Low | Court Manager | Neither door in the first floor communal lounge has a fire exit sign indicating which is to be used in the event of a fire, this should be installed. | NULL
5212 | Old Mill House | OLDMILL_S001 | ODH | Scheme | 2022-02-09 18:42 | FRA_5212090220221310.pdf | mitchellj1 | 5212090220221310 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | bmwj4z70adkzfkkezk | Observation Only | Risk Closed | 44904.4413 | Obs1 | The Building | NULL | N/A | Surveyor | 2nd floor loft space above flat 29 wing: survey to establish fire stopping requirements planned. | Link Fire Safety have undertaken fire stopping and compartmentation works to the court.
5212 | Old Mill House | OLDMILL_S001 | ODH | Scheme | 2022-02-09 18:42 | FRA_5212090220221310.pdf | mitchellj1 | 5212090220221310 | PPP-PFI | Oldham Management Service | Neighbourhood 3 | North | North Patch 7 | ykll9ezjvpkzfkkf3k | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45331 | Low | Surveyor | Ground floor meter cupboard RHS after exiting court: service cables pass through slab and there is no fire stopping visible. | NULL
5214 | Cloughgate House | CLOUGHGATE_S001 | ODH | Scheme | 2021-12-07 17:38 | FRA_5214071220211722.pdf | mitchellj1 | 5214071220211720 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | xn2eyz357dkwwdf713 | Observation Only | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | NULL | N/A | Other | 1 resident in each block is nominated to walk the block in the event if the fire alarm going off, check to ensure there is no fire, then silence the panel, the nominated resident then waits for the response team to attend who then reset the panel. The nominated residents have been asked to reset the recently installed EV store doors at Highgate and Westgate also. | NULL
5214 | Cloughgate House | CLOUGHGATE_S001 | ODH | Scheme | 2021-12-07 17:38 | FRA_5214071220211722.pdf | mitchellj1 | 5214071220211720 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 91bs8xsqcyokwwdf703 | Observation Only | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Other | Fire panel | NULL
5214 | Cloughgate House | CLOUGHGATE_S001 | ODH | Scheme | 2021-12-07 17:38 | FRA_5214071220211722.pdf | mitchellj1 | 5214071220211720 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | cd34dm9h5ikkwwdf72v | Medium Risk Overdue | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44902 | Medium | Court Manager | Residents items stored in mobility scooter store should be removed. This area should be sterile. | NULL
5214 | Cloughgate House | CLOUGHGATE_S001 | ODH | Scheme | 2021-12-07 17:38 | FRA_5214071220211722.pdf | mitchellj1 | 5214071220211720 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 721gsceo2drkwwdf724 | Medium Risk Overdue | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44902 | Medium | Court Manager | PAT testing to mobility scooter expired in October 2021, please arrange for this to be renewed. | NULL
5214 | Cloughgate House | CLOUGHGATE_S001 | ODH | Scheme | 2021-12-07 17:38 | FRA_5214071220211722.pdf | mitchellj1 | 5214071220211720 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 0oy32kecgq6kwwdf78z | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45267 | Low | Court Manager | Updated Housing 21 fire action notice sign isn't in place throughout. | NULL
5214 | Cloughgate House | CLOUGHGATE_S001 | ODH | Scheme | 2021-12-07 17:38 | FRA_5214071220211722.pdf | mitchellj1 | 5214071220211720 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 118x4bevooalkwwdf7cg | Observation Only | Risk Open | NULL | Obs14 | Access By Emergency Services | NULL | N/A | Other | Consider discussing clearance of litter/fly-tipped clothes and items with car park operator to reduce likelihood of ASB and potential arson. | NULL
5214 | Cloughgate House | CLOUGHGATE_S001 | ODH | Scheme | 2021-12-07 17:38 | FRA_5214071220211722.pdf | mitchellj1 | 5214071220211720 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 0tah15b1md1ikwwdf79z | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45072 | Low | Court Manager | Consider introducing additional double-sided signage to make the assembly point more identifiable. | NULL
5214 | Cloughgate House | CLOUGHGATE_S001 | ODH | Scheme | 2021-12-07 17:38 | FRA_5214071220211722.pdf | mitchellj1 | 5214071220211720 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | pd65trga2ykwwdf75i | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45072 | Low | Court Manager | Vents to meter room door require upgrading to intumescent. | NULL
5214 | Cloughgate House | CLOUGHGATE_S001 | ODH | Scheme | 2021-12-07 17:38 | FRA_5214071220211722.pdf | mitchellj1 | 5214071220211720 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | pz57nrxzpmgkwwdf77k | Low Risk closed | Risk Closed | 44904.387 | Obs8 | Measures To Limit Fire Spread And Development | 45072 | Low | Court Manager | Fire stopping to communal ground floor area required, to wall and ceiling as well as partition wall between entrance lobby and lounge entrance lobby space. | Fire stopping was undertaken by TF Jones.
5214 | Cloughgate House | CLOUGHGATE_S001 | ODH | Scheme | 2021-12-07 17:38 | FRA_5214071220211722.pdf | mitchellj1 | 5214071220211720 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | u2onxazcnvfkwwdf7be | Observation Only | Risk Open | NULL | Obs11 | Fire Fighting Equipment | NULL | N/A | Other | Extinguishers aren't P50 as per h21 policy but a servicing contract is in place | NULL
5214 | Cloughgate House | CLOUGHGATE_S001 | ODH | Scheme | 2021-12-07 17:38 | FRA_5214071220211722.pdf | mitchellj1 | 5214071220211720 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | mds6jarornkwwdf73r | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45267 | Low | Court Manager | No fire exit sign to door in EV store. | NULL
5214 | Cloughgate House | CLOUGHGATE_S001 | ODH | Scheme | 2021-12-07 17:38 | FRA_5214071220211722.pdf | mitchellj1 | 5214071220211720 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | kairoc3qyykwwdf7ei | Observation Only | Risk Open | NULL | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | Fire Risk management documents will be split out and separate for each individual court (not captured under one block) moving forward. | NULL
5214 | Cloughgate House | CLOUGHGATE_S001 | ODH | Scheme | 2021-12-07 17:38 | FRA_5214071220211722.pdf | mitchellj1 | 5214071220211720 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | jal795uozlakwwdf74p | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45072 | Low | Court Manager | Fire exit door in kitchen has thumb turn lock on it and opens inwards. | NULL
5215 | Highgate House | HIGHGATE_S001 | ODH | Scheme | 2021-12-07 17:42 | FRA_5215071220211739.pdf | mitchellj1 | 5215071220211730 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | gpjmgtf4yvkwwe04ih | Observation Only | Risk Open | NULL | Obs11 | Fire Fighting Equipment | NULL | N/A | Other | Extinguishers aren't P50 but are covered by a servicing contract | NULL
5215 | Highgate House | HIGHGATE_S001 | ODH | Scheme | 2021-12-07 17:42 | FRA_5215071220211739.pdf | mitchellj1 | 5215071220211730 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | fkanxz6sr3rkwwe04ch | Medium Risk closed | Risk Closed | 44904.3872 | Obs8 | Measures To Limit Fire Spread And Development | 44902 | Medium | Court Manager | Damaged ceiling section exposes ceiling joists, surface is compromised, please arrange a repair. | Repair undertaken
5215 | Highgate House | HIGHGATE_S001 | ODH | Scheme | 2021-12-07 17:42 | FRA_5215071220211739.pdf | mitchellj1 | 5215071220211730 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | m3ga91f7hrkwwe04ae | Observation Only | Risk Open | NULL | Obs7 | Fire Protection Measures | NULL | N/A | Other | Mobility scooters stored behind 60 minute fire wall served by 2 double doors connected to the fire panel by EM closers. | NULL
5215 | Highgate House | HIGHGATE_S001 | ODH | Scheme | 2021-12-07 17:42 | FRA_5215071220211739.pdf | mitchellj1 | 5215071220211730 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | lwias8vk5crkwwe048t | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45072 | Low | Court Manager | Gate to place of safety outside the grounds is operated by button/fob and requires pulling. Change to push pad or bar to allow for easy egress. | NULL
5215 | Highgate House | HIGHGATE_S001 | ODH | Scheme | 2021-12-07 17:42 | FRA_5215071220211739.pdf | mitchellj1 | 5215071220211730 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | ua689w28n98kwwe045v | Observation Only | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Rear bin store door accessed by blocks 10-12 requires repairing. | NULL
5215 | Highgate House | HIGHGATE_S001 | ODH | Scheme | 2021-12-07 17:42 | FRA_5215071220211739.pdf | mitchellj1 | 5215071220211730 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | ramyp06vvvkwwe047m | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45267 | Low | Court Manager | Door adjacent flat 10 has key barrel lock, we would recommend upgrading this to a push pad or bar as this serves as a fire exit, the alternative exit in this space is operated by thumb turn however isn't designed as a fire exit as it doesn't provide unobstructed access to the assembly point | NULL
5215 | Highgate House | HIGHGATE_S001 | ODH | Scheme | 2021-12-07 17:42 | FRA_5215071220211739.pdf | mitchellj1 | 5215071220211730 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | ohseuhammakwwe046r | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45267 | Low | Court Manager | Fire exit door adjacent flat 1 is lockable and the handle feels loose, we would recommend upgrading this to a push bar or pad in the future and repairing the handle in the interim. | NULL
5215 | Highgate House | HIGHGATE_S001 | ODH | Scheme | 2021-12-07 17:42 | FRA_5215071220211739.pdf | mitchellj1 | 5215071220211730 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 7lfp3w4d6s7kwwe044s | Medium Risk Overdue | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44902 | Medium | Court Manager | PAT testing of scooter chargers expired in October 2021, please arrange for this to be done. | NULL
5215 | Highgate House | HIGHGATE_S001 | ODH | Scheme | 2021-12-07 17:42 | FRA_5215071220211739.pdf | mitchellj1 | 5215071220211730 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 5xhew9wu9c3kwwe043u | Observation Only | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | NULL | N/A | Other | 1 resident in each block is nominated to walk the block in the event if the fire alarm going off, check to ensure there is no fire, then silence the panel, the nominated resident then waits for the response team to attend who then reset the panel. The nominated residents have been asked to reset the recently installed EV store doors at Highgate and Westgate also. | NULL
5215 | Highgate House | HIGHGATE_S001 | ODH | Scheme | 2021-12-07 17:42 | FRA_5215071220211739.pdf | mitchellj1 | 5215071220211730 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | dmbp0n5gc7ekwwe04gd | Observation Only | Risk Closed | 44540.4228 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Other | Door closer | Having spoke to the surveyor this task and photograph was purely to show that the door met the measures to limit the spread of flame and was observation only
5215 | Highgate House | HIGHGATE_S001 | ODH | Scheme | 2021-12-07 17:42 | FRA_5215071220211739.pdf | mitchellj1 | 5215071220211730 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | e10bi4s74w7kwwe04dr | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45267 | Low | Surveyor | Openable upvc window to flat 6 on escape route, seek guidance to consider appropriate action for upgrading. | NULL
5215 | Highgate House | HIGHGATE_S001 | ODH | Scheme | 2021-12-07 17:42 | FRA_5215071220211739.pdf | mitchellj1 | 5215071220211730 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | ae60ofps23kwwe042y | Observation Only | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Other | Fire panel | NULL
5215 | Highgate House | HIGHGATE_S001 | ODH | Scheme | 2021-12-07 17:42 | FRA_5215071220211739.pdf | mitchellj1 | 5215071220211730 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | an0jpkawymqkwwe04he | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45267 | Low | Court Manager | Update fire action notices to New H21 sign. | NULL
5215 | Highgate House | HIGHGATE_S001 | ODH | Scheme | 2021-12-07 17:42 | FRA_5215071220211739.pdf | mitchellj1 | 5215071220211730 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | v66ccug03bkwwe04be | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45267 | Low | Court Manager | Trolley and power lead in corridor outside EV store. This area should be sterile. | NULL
5215 | Highgate House | HIGHGATE_S001 | ODH | Scheme | 2021-12-07 17:42 | FRA_5215071220211739.pdf | mitchellj1 | 5215071220211730 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | z57v7q37cbikwwe04f6 | Observation Only | Risk Closed | 44540.4229 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Other | Inside of flat 6's door. | Having spoke to the surveyor this task and photograph was purely to show that the door met the measures to limit the spread of flame and was observation only
5216 | Westgate House | WESTGATE_S001 | ODH | Scheme | 2021-12-07 17:23 | FRA_5216071220211600.pdf | mitchellj1 | 5216071220211600 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | b4p03k17xlfkwwagwp4 | Observation Only | Risk Closed | 44540.423 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Other | Door check | Having spoke to the surveyor this task and photograph was purely to show that the door met the measures to limit the spread of flame and was observation only
5216 | Westgate House | WESTGATE_S001 | ODH | Scheme | 2021-12-07 17:23 | FRA_5216071220211600.pdf | mitchellj1 | 5216071220211600 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 80h0adsn1gqkwwagwqt | Observation Only | Risk Open | NULL | Obs9 | Escape Lighting | NULL | N/A | Court Manager | Light fitting (not emergency) in EV store not working. | NULL
5216 | Westgate House | WESTGATE_S001 | ODH | Scheme | 2021-12-07 17:23 | FRA_5216071220211600.pdf | mitchellj1 | 5216071220211600 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | fat5vxe68vhkwwagwel | Observation Only | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Other | Fire alarm panel | NULL
5216 | Westgate House | WESTGATE_S001 | ODH | Scheme | 2021-12-07 17:23 | FRA_5216071220211600.pdf | mitchellj1 | 5216071220211600 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | cascwsr8t6wkwwagwin | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45267 | Low | Court Manager | Items being stored behind door to EV store. This area should remain sterile. | NULL
5216 | Westgate House | WESTGATE_S001 | ODH | Scheme | 2021-12-07 17:23 | FRA_5216071220211600.pdf | mitchellj1 | 5216071220211600 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 754tqag7xkokwwagwhw | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45267 | Low | Court Manager | Bin store space abutts the building and is less than 6m away and unlocked, consider installing a lock to the gate to improve security and prevent ASB/arson. | NULL
5216 | Westgate House | WESTGATE_S001 | ODH | Scheme | 2021-12-07 17:23 | FRA_5216071220211600.pdf | mitchellj1 | 5216071220211600 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 6rryyu17fd3kwway2g5 | Medium Risk Overdue | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44707 | Medium | Court Manager | One exit door on stairwells 4-6, 7-9 & 10-11 is operated by key barrel, the door adjacent flat 7 was locked. We would recommend upgrading those which are designated fire exit doors to a push pad or bar door, and installing a thumb turn to them in the interim to avoid people locking them. | NULL
5216 | Westgate House | WESTGATE_S001 | ODH | Scheme | 2021-12-07 17:23 | FRA_5216071220211600.pdf | mitchellj1 | 5216071220211600 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 13wr9kv5usemkwwagwfp | Observation Only | Risk Open | NULL | Obs3 | Details Of Fire Loss | NULL | N/A | Other | Flat 4 had a minor fire caused by portable vacuum cleaner, however no damage to building, occurred on 5th August 2021. | NULL
5216 | Westgate House | WESTGATE_S001 | ODH | Scheme | 2021-12-07 17:23 | FRA_5216071220211600.pdf | mitchellj1 | 5216071220211600 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 1lhati4vtntkwwagwjk | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45072 | Low | Court Manager | Boiler at top of central fire exit stairs exposed, requires additional compartmentation. | NULL
5216 | Westgate House | WESTGATE_S001 | ODH | Scheme | 2021-12-07 17:23 | FRA_5216071220211600.pdf | mitchellj1 | 5216071220211600 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 0r0bywdfk70pkwwagwm2 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45267 | Low | Court Manager | Exit adjacent flat 4 has a call point, signs don't indicate it's a fire exit and direct people to the other side, door is lockable with key/barrel, last FRA identified it as being an exit. Ensure local residents are aware this isn't a fire exit (as there are no signs), consider removing lock and installing push pad/bar. | NULL
5216 | Westgate House | WESTGATE_S001 | ODH | Scheme | 2021-12-07 17:23 | FRA_5216071220211600.pdf | mitchellj1 | 5216071220211600 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | 03f44ncasvqekwwagwsg | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45072 | Low | Court Manager | Additional signage outside to direct people to the assembly point. | NULL
5216 | Westgate House | WESTGATE_S001 | ODH | Scheme | 2021-12-07 17:23 | FRA_5216071220211600.pdf | mitchellj1 | 5216071220211600 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | t7dnl0wu5ghkwwagwgi | Observation Only | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | NULL | N/A | Other | 1 resident in each block is nominated to walk the block in the event if the fire alarm going off, check to ensure there is no fire, then silence the panel, the nominated resident then waits for the response team to attend who then reset the panel. The nominated residents have been asked to reset the recently installed EV store doors at Highgate and Westgate also. | NULL
5216 | Westgate House | WESTGATE_S001 | ODH | Scheme | 2021-12-07 17:23 | FRA_5216071220211600.pdf | mitchellj1 | 5216071220211600 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | t5pz8qrtaojkwwagwrr | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45267 | Low | Court Manager | Fire action notices not the updated Housing21 signs. | NULL
5216 | Westgate House | WESTGATE_S001 | ODH | Scheme | 2021-12-07 17:23 | FRA_5216071220211600.pdf | mitchellj1 | 5216071220211600 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | jfkmdx27roqkwwagwnn | Observation Only | Risk Open | NULL | Obs7 | Fire Protection Measures | NULL | N/A | Other | Mobility scooter storage space has now been separated from circulation area by introduction of a 60 minute wall with 2 double doors and AM closers linked to fire panel. | NULL
5216 | Westgate House | WESTGATE_S001 | ODH | Scheme | 2021-12-07 17:23 | FRA_5216071220211600.pdf | mitchellj1 | 5216071220211600 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | fwrbp47al39kwwagwtg | Observation Only | Risk Open | NULL | Obs11 | Fire Fighting Equipment | NULL | N/A | Court Manager | Fire fighting equipment in place is not P50 as per H21 policy as there is a servicing agreement in place. | NULL
5216 | Westgate House | WESTGATE_S001 | ODH | Scheme | 2021-12-07 17:23 | FRA_5216071220211600.pdf | mitchellj1 | 5216071220211600 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | j809gfqtr7rkwwagwkk | Medium Risk Overdue | Risk Open | NULL | Obs7 | Fire Protection Measures | 44707 | Medium | Court Manager | Fire exit adjacent flat 7 is locked. We would recommend that a push pad or bar is installed. | NULL
5216 | Westgate House | WESTGATE_S001 | ODH | Scheme | 2021-12-07 17:23 | FRA_5216071220211600.pdf | mitchellj1 | 5216071220211600 | PPP-PFI | Oldham Management Service | Neighbourhood 2 | North | North Patch 7 | j5rtdgcjiilkwwagwh9 | Medium Risk Overdue | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44902 | Medium | Court Manager | PAT testing to mobility scooters expired in (October 2021, it is recommended that they are re-tested. | NULL
5218 | Violet Hill Court | VIOLETHILL_S001 | ODH | Scheme | 2021-12-14 17:59 | FRA_5218141220211752.pdf | mitchellj1 | 5218141220211750 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | fyb9mav5zg9kx6ekfd6 | Observation Only | Risk Open | NULL | Obs11 | Fire Fighting Equipment | NULL | N/A | Court Manager | Fire extinguishers are not a P50 type as per company policy, but are maintained as part of a servicing contract. | NULL
5218 | Violet Hill Court | VIOLETHILL_S001 | ODH | Scheme | 2021-12-14 17:59 | FRA_5218141220211752.pdf | mitchellj1 | 5218141220211750 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | g4h05o2sinlkx6ekf46 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45274 | Low | Court Manager | Flat 54 door closer is not in place. | NULL
5218 | Violet Hill Court | VIOLETHILL_S001 | ODH | Scheme | 2021-12-14 17:59 | FRA_5218141220211752.pdf | mitchellj1 | 5218141220211750 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | mrq8lwgi1vlkx6ekf6d | Low Risk closed | Risk Closed | 44904.4216 | Obs8 | Measures To Limit Fire Spread And Development | 45274 | Low | Court Manager | Store near flat 28 had aerosols and items stored in It, resident of flat 28 removed them during survey, regular checks may be required to ensure no flammable items are stored in space. Walkway outside flat 28 also has plants and items storing It, area should be sterile as it serves as an emergency exit route. | Cm action.
5218 | Violet Hill Court | VIOLETHILL_S001 | ODH | Scheme | 2021-12-14 17:59 | FRA_5218141220211752.pdf | mitchellj1 | 5218141220211750 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | ofi4dw3a9hpkx6ekf77 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45274 | Low | Court Manager | Panel to service room near guest room has dropped and compartmentation to edges is no longer in place. | NULL
5218 | Violet Hill Court | VIOLETHILL_S001 | ODH | Scheme | 2021-12-14 17:59 | FRA_5218141220211752.pdf | mitchellj1 | 5218141220211750 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | ndmahgnhu2jkx6ekez6 | Low Risk to be actioned | Risk Open | NULL | Obs1 | The Building | 45274 | Low | Surveyor | Establish suitability of cladding material. | NULL
5218 | Violet Hill Court | VIOLETHILL_S001 | ODH | Scheme | 2021-12-14 17:59 | FRA_5218141220211752.pdf | mitchellj1 | 5218141220211750 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | qsqi4vx4c8ckx6ekfbe | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45274 | Low | Court Manager | Introduce fire exit signage to walls in yard area outside flat 1. | NULL
5218 | Violet Hill Court | VIOLETHILL_S001 | ODH | Scheme | 2021-12-14 17:59 | FRA_5218141220211752.pdf | mitchellj1 | 5218141220211750 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | poj4sosbqsrkx6ekf9l | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45274 | Low | Court Manager | It's recommended that 'do not use lift in the event of a Fire signage is installed in lift lobbies. | NULL
5218 | Violet Hill Court | VIOLETHILL_S001 | ODH | Scheme | 2021-12-14 17:59 | FRA_5218141220211752.pdf | mitchellj1 | 5218141220211750 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | 4s7fj3ehoeykx6ekfag | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45274 | Low | Court Manager | Install fire exit sign to central fire exit gate. | NULL
5218 | Violet Hill Court | VIOLETHILL_S001 | ODH | Scheme | 2021-12-14 17:59 | FRA_5218141220211752.pdf | mitchellj1 | 5218141220211750 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | 4z79glb25xdkx6emqdw | Low Risk closed | Risk Closed | 44904.419 | Obs8 | Measures To Limit Fire Spread And Development | 45274 | Low | Court Manager | Flat 52 - closer not in place | Link fire safety have installed closers to doors requiring them.
5218 | Violet Hill Court | VIOLETHILL_S001 | ODH | Scheme | 2021-12-14 17:59 | FRA_5218141220211752.pdf | mitchellj1 | 5218141220211750 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | chy2v9uldckx6ekf8l | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45274 | Low | Court Manager | It is recommended that the fire action notices are upgraded to the Housing 21 standard signage. | NULL
5218 | Violet Hill Court | VIOLETHILL_S001 | ODH | Scheme | 2021-12-14 17:59 | FRA_5218141220211752.pdf | mitchellj1 | 5218141220211750 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | df1kothnlj4kx6ekf1t | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 44959 | Low | Court Manager | Additional fire stopping required to service risers on ground floor adjacent staircase 3. | NULL
5218 | Violet Hill Court | VIOLETHILL_S001 | ODH | Scheme | 2021-12-14 17:59 | FRA_5218141220211752.pdf | mitchellj1 | 5218141220211750 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | dgmbyqbhabikx6em8uj | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45274 | Low | Court Manager | Flat 50 - closer not in place. | NULL
5218 | Violet Hill Court | VIOLETHILL_S001 | ODH | Scheme | 2021-12-14 17:59 | FRA_5218141220211752.pdf | mitchellj1 | 5218141220211750 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | 831pzjmmu78kx6ekfew | Observation Only | Risk Open | NULL | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | Complete fire safety responsibility matrix. | NULL
5218 | Violet Hill Court | VIOLETHILL_S001 | ODH | Scheme | 2021-12-14 17:59 | FRA_5218141220211752.pdf | mitchellj1 | 5218141220211750 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | 92k1ng3edakx6ekf2z | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 44959 | Low | Court Manager | Service riser no.1 - additional fire stopping required in place of expanding foam. | NULL
5218 | Violet Hill Court | VIOLETHILL_S001 | ODH | Scheme | 2021-12-14 17:59 | FRA_5218141220211752.pdf | mitchellj1 | 5218141220211750 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | vhwvuqz48hpkx6ekf5s | Low Risk closed | Risk Closed | 44904.4195 | Obs8 | Measures To Limit Fire Spread And Development | 45274 | Low | Court Manager | Flat 27 - door doesn't close into the frame fully, closer force requires adjusting. | Link Fire Safety adjusted as part of closer installations.
5218 | Violet Hill Court | VIOLETHILL_S001 | ODH | Scheme | 2021-12-14 17:59 | FRA_5218141220211752.pdf | mitchellj1 | 5218141220211750 | PPP-PFI | Oldham Management Service | Neighbourhood 1 | North | North Patch 7 | yqlh4mhac2kx6ekf0d | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44959 | Low | Court Manager | Fire alarm cable in warden call cupboard in EV store needs fire stopping | NULL
5301 | Earl Spencer Court | EARLSPEN_S001 | H21 | Scheme | 2022-11-11 12:09 | FRA_5301101120221626.pdf | colej | 5301101120221620 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | z0i2vqjq38lacbzrmb | High Risk Closed | Risk Closed | 44880.3415 | Obs6 | Fire Hazards - Elimination & Control | 44968 | High | Court Manager | The main block electrical intake cupboard has a riser within. Some remedial work has commenced to the compartmentation. This requires completing to ensure there is no risk of flame and smoke spread. | added to handyman list
5301 | Earl Spencer Court | EARLSPEN_S001 | H21 | Scheme | 2022-11-11 12:09 | FRA_5301101120221626.pdf | colej | 5301101120221620 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | zsdi34f8fslacd3mtt | Observation Only | Risk Open | NULL | Obs9 | Escape Lighting | NULL | N/A | Surveyor | The communal and emergency lighting has recently been upgraded as part of the upcoming court makeover. At the time of the inspection some elements required finishing but were scheduled for the comings weeks. | NULL
5301 | Earl Spencer Court | EARLSPEN_S001 | H21 | Scheme | 2022-11-11 12:09 | FRA_5301101120221626.pdf | colej | 5301101120221620 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | znh9off5ixslacf2emn | High Risk Closed | Risk Closed | 44880.3414 | Obs8 | Measures To Limit Fire Spread And Development | 44968 | High | Court Manager | Although the door discharges to fresh air it is located directly by the escape route stairwell. The internal chain door closer has been disconnected and requires reconnecting to ensure the door self closes unaided. | added to handyman list
5301 | Earl Spencer Court | EARLSPEN_S001 | H21 | Scheme | 2022-11-11 12:09 | FRA_5301101120221626.pdf | colej | 5301101120221620 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | 9zreqh0xsjlaccx9l1 | Observation Only | Risk Closed | 44880.3407 | Obs7 | Fire Protection Measures | NULL | N/A | Court Manager | Of the 3 final exits within the main block, only one exit opens in the direction of travel. This is considered acceptable but should be considered when any upgrade replacement takes place in the future. | Works to be considered when upgrade replacement takes place
5301 | Earl Spencer Court | EARLSPEN_S001 | H21 | Scheme | 2022-11-11 12:09 | FRA_5301101120221626.pdf | colej | 5301101120221620 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | f9tz3a0qlholaceiykd | Medium Risk closed | Risk Closed | 44880.342 | Obs8 | Measures To Limit Fire Spread And Development | 45241 | Medium | Court Manager | It was noted at the time of inspection there was no door closer on the court mangers office door. It is recommended one is fitted to ensure the door closes into the frame unaided on exitng the room. The inclusion of a hold back device could be added to retain the door in an open position until triggered by the fire alarm. | added to handyman list
5301 | Earl Spencer Court | EARLSPEN_S001 | H21 | Scheme | 2022-11-11 12:09 | FRA_5301101120221626.pdf | colej | 5301101120221620 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | 0cdnbiuydebslaccqlbx | Observation Only | Risk Closed | 44879.5278 | Obs7 | Fire Protection Measures | NULL | N/A | Court Manager | It was noted that the upper walkways have a number of personal belongings located along the escape routes. This requires constant monitoring to ensure the walkways are clear of obstructions. At the time of the inspection it was deemed acceptable but noted one area to monitor. | constant monitoring of the walkways to ensure they stay clear
5301 | Earl Spencer Court | EARLSPEN_S001 | H21 | Scheme | 2022-11-11 12:09 | FRA_5301101120221626.pdf | colej | 5301101120221620 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | 3mykomsl0jxlacfpbzm | Medium Risk closed | Risk Closed | 44880.3392 | Obs10 | Fire Safety And Notices | 45241 | Medium | Court Manager | It was noted that the central staircase by flats 75-63 has no fire exit signage. It is recommended this is added to provide clear indication of the escape stairwells. | Works added to makeover
5301 | Earl Spencer Court | EARLSPEN_S001 | H21 | Scheme | 2022-11-11 12:09 | FRA_5301101120221626.pdf | colej | 5301101120221620 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | q0tgw6mvuwlaceshl6 | High Risk Closed | Risk Closed | 44880.3401 | Obs8 | Measures To Limit Fire Spread And Development | 44968 | High | Court Manager | Flat 43. The door is not closing fully into the frame unaided. The door requires adjustment to be able to self close. The external draft excluder strip is also loose and needs refitting at low level. | Added to WO1576036
5301 | Earl Spencer Court | EARLSPEN_S001 | H21 | Scheme | 2022-11-11 12:09 | FRA_5301101120221626.pdf | colej | 5301101120221620 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | r5oltdrw2qblacf69bb | High Risk Closed | Risk Closed | 44880.3419 | Obs8 | Measures To Limit Fire Spread And Development | 44968 | High | Court Manager | It was noted during the inspection that flats 71, 67, 63 & 21 only have a single direction of travel to escape. The above doors require closers to be working to ensure the doors closes fully into the frame unaided. This is to ensure the escape route is not compromised in the event of a fire. The internal door closers have been disconnected and require refitting. | Added to handyman list
5301 | Earl Spencer Court | EARLSPEN_S001 | H21 | Scheme | 2022-11-11 12:09 | FRA_5301101120221626.pdf | colej | 5301101120221620 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | gkvfwr91i8nlacfxv57 | Observation Only | Risk Open | NULL | Obs10 | Fire Safety And Notices | NULL | N/A | Surveyor | Any additional escape signage will be reviewed and replaced where required during the court makeover works currently planned for 2023/24. | NULL
5302 | Harry Scott Court | HARRYSCOT_S001 | H21 | Scheme | 2022-08-16 11:14 | FRA_5302160820221102.pdf | colej | 5302160820221100 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | ipgsvu4j68l6w0ni38 | Low Risk closed | Risk Closed | 44795.5634 | Obs7 | Fire Protection Measures | 45520 | Low | Court Manager | It is recommended that a fire exit sign is fitted above the cross corridor door by flat 7. | Fire exit sign installed
5302 | Harry Scott Court | HARRYSCOT_S001 | H21 | Scheme | 2022-08-16 11:14 | FRA_5302160820221102.pdf | colej | 5302160820221100 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | hib1mjymsil6w0ni6h | Medium Risk closed | Risk Closed | 44834.5143 | Obs8 | Measures To Limit Fire Spread And Development | 45154 | Medium | Court Manager | Quiet room (temporary office) It was noted the temporary office door is held open with a door wedge whilst occupied. In the event of A fire the door needs to close unaided. It is recommended that the door is fitted with a "Dorguard" device to allow the door to be held open and would operate at the sound of the fire alarm. | Dorguard fitted
5302 | Harry Scott Court | HARRYSCOT_S001 | H21 | Scheme | 2022-08-16 11:14 | FRA_5302160820221102.pdf | colej | 5302160820221100 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | uc7yu0iiwtl6w0ni57 | Medium Risk closed | Risk Closed | 44832.5167 | Obs8 | Measures To Limit Fire Spread And Development | 45154 | Medium | Court Manager | Flat 18 Internal door closer (perko) type is disconnected and requires reinstating. | Perko installed
5302 | Harry Scott Court | HARRYSCOT_S001 | H21 | Scheme | 2022-08-16 11:14 | FRA_5302160820221102.pdf | colej | 5302160820221100 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | ou5uduxui4l6w0ni5u | Medium Risk closed | Risk Closed | 44797.5346 | Obs8 | Measures To Limit Fire Spread And Development | 45154 | Medium | Court Manager | Flat 16b. The door doesn't close fully into the frame unaided. The door brush strip on the rear of the door needs to be raised allowing the door to clear the door mat. | Brush strip raised
5302 | Harry Scott Court | HARRYSCOT_S001 | H21 | Scheme | 2022-08-16 11:14 | FRA_5302160820221102.pdf | colej | 5302160820221100 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | zc6t3al4fb9l6w0ni4k | Medium Risk closed | Risk Closed | 44818.4441 | Obs8 | Measures To Limit Fire Spread And Development | 45154 | Medium | Court Manager | Flat 11 Internal door closer (perko) type is disconnected and requires reinstating or replacing. | Perko has been reconnected
5302 | Harry Scott Court | HARRYSCOT_S001 | H21 | Scheme | 2022-08-16 11:14 | FRA_5302160820221102.pdf | colej | 5302160820221100 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | wt3vxp0q36l6w0ni78 | Low Risk closed | Risk Closed | 44790.5817 | Obs10 | Fire Safety And Notices | 45520 | Low | Court Manager | The fire action notices on the landing by flat 8 & 15 requires the assembly point to be added. | Location of assembly point added to signage by flats 8 & 15
5303 | Palmer Close | PALMERCLOS_S001 | H21 | Scheme | 2022-11-08 13:57 | FRA_5303081120220851.pdf | colej | 5303081120220850 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | x8vzp6l147rla88olie | High Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44965 | High | Court Manager | The door does not close unaided due to the draft excluded strip fitted to the inside of the door which is dragging on the thick carpet. It is recommended that it is removed and a drop seal is fitted to the external face to stop the spread of potential smoke and fire along with preventing drafts for the resident. | NULL
5303 | Palmer Close | PALMERCLOS_S001 | H21 | Scheme | 2022-11-08 13:57 | FRA_5303081120220851.pdf | colej | 5303081120220850 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | xoep7jnj59ola87yb8u | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45238 | Medium | Court Manager | It was noted there are door mats located outside of some flat entrance doors. These can pose a trip hazard in the event of reduced visibility caused from smoke. It is recommended these are removed or replaced with non trip mats. The court has recessed mats provided at the front and rear exits of the blocks. | NULL
5303 | Palmer Close | PALMERCLOS_S001 | H21 | Scheme | 2022-11-08 13:57 | FRA_5303081120220851.pdf | colej | 5303081120220850 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | rx4xl4t61vhla89ie3q | High Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44965 | High | Court Manager | The door doesn't fully close into the frame unaided. The keep and door closer requires minor adjustment. | NULL
5303 | Palmer Close | PALMERCLOS_S001 | H21 | Scheme | 2022-11-08 13:57 | FRA_5303081120220851.pdf | colej | 5303081120220850 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | g6bq8ye3dv9la89dkhh | High Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44965 | High | Court Manager | The door doesn't fully close into the frame unaided. The keep and door closer requires minor adjustment. | NULL
5303 | Palmer Close | PALMERCLOS_S001 | H21 | Scheme | 2022-11-08 13:57 | FRA_5303081120220851.pdf | colej | 5303081120220850 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | jwi6bnmz9la84clx0 | High Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44965 | High | Court Manager | It was noted at the time of inspection, the fire blanket in the communal kitchen is missing and requires replacing. | NULL
5303 | Palmer Close | PALMERCLOS_S001 | H21 | Scheme | 2022-11-08 13:57 | FRA_5303081120220851.pdf | colej | 5303081120220850 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | 2w14bepxts5la83me1l | Low Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45604 | Low | Court Manager | Completion of online fire training required. The court manager is temporary at present. | NULL
5303 | Palmer Close | PALMERCLOS_S001 | H21 | Scheme | 2022-11-08 13:57 | FRA_5303081120220851.pdf | colej | 5303081120220850 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | 0iuktzfbhd67la87qcu3 | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45604 | Low | Court Manager | It was noted there are some old fire action notices in place. To avoid any confusion it is recommended to remove these so there is a consistent approach on the court. | NULL
5303 | Palmer Close | PALMERCLOS_S001 | H21 | Scheme | 2022-11-08 13:57 | FRA_5303081120220851.pdf | colej | 5303081120220850 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | 1rvip8arxmula84su48 | High Risk Overdue | Risk Open | NULL | Obs10 | Fire Safety And Notices | 44611 | High | Court Manager | The fire action notices at the call points are in place but are missing the assembly point information. This needs to be added for clarity to residents and visitors. | NULL
5303 | Palmer Close | PALMERCLOS_S001 | H21 | Scheme | 2022-11-08 13:57 | FRA_5303081120220851.pdf | colej | 5303081120220850 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | 5e824pki53gla899r2n | High Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44965 | High | Court Manager | The door closer requires adjustment as it does not close into the frame in an acceptable time frame. | NULL
5303 | Palmer Close | PALMERCLOS_S001 | H21 | Scheme | 2022-11-08 13:57 | FRA_5303081120220851.pdf | colej | 5303081120220850 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | c6e5va8casdla86xdxn | High Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44965 | High | Court Manager | The court managers office door when tested would not self close. The Fireco door closer battery requires replacing. | NULL
5303 | Palmer Close | PALMERCLOS_S001 | H21 | Scheme | 2022-11-08 13:57 | FRA_5303081120220851.pdf | colej | 5303081120220850 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | 94jfvw064fnla87w278 | High Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44965 | High | Court Manager | The cross corridor fire door leading to the stairs of flats 3&5 would not fully close into the frame when operated. The door closer requires adjustment. | NULL
5304 | Legge-Bourke Court | LEGGEBOURKE_S001 | H21 | Scheme | 2022-08-03 14:41 | FRA_5304030820221053.pdf | colej | 5304030820221050 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | 8xpiyippzp4l6dnekcb | Medium Risk closed | Risk Closed | 44777.522 | Obs8 | Measures To Limit Fire Spread And Development | 45141 | Medium | Court Manager | The chain door closer to the flat 18 has been disconnected. This either needs reinstating or an overhead door closer installed. There is an additional fire door from the flat lobby to the main escape route making this acceptable in the short term. | Overhead closer fitted 4th August
5304 | Legge-Bourke Court | LEGGEBOURKE_S001 | H21 | Scheme | 2022-08-03 14:41 | FRA_5304030820221053.pdf | colej | 5304030820221050 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | 6dylpoas77bl6dnipws | Medium Risk closed | Risk Closed | 44851.5059 | Obs8 | Measures To Limit Fire Spread And Development | 45141 | Medium | Court Manager | The door closer to flat 34 requires adjustment to the last 15 degree setting as it doesn't close fully into the frame. Minor adjustment necessary. | Contractor corrected the problem
5304 | Legge-Bourke Court | LEGGEBOURKE_S001 | H21 | Scheme | 2022-08-03 14:41 | FRA_5304030820221053.pdf | colej | 5304030820221050 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | mqfo0tvjovl6dngxn4 | Medium Risk closed | Risk Closed | 44795.5402 | Obs8 | Measures To Limit Fire Spread And Development | 45141 | Medium | Court Manager | Flat 12. This property is currently void and not in use. There is a Fireco door closer that will require a new battery upon re occupation of the property. | New battery fitted
5304 | Legge-Bourke Court | LEGGEBOURKE_S001 | H21 | Scheme | 2022-08-03 14:41 | FRA_5304030820221053.pdf | colej | 5304030820221050 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | ip6woeyt3hal6dhgrjt | Medium Risk closed | Risk Closed | 44795.5406 | Obs10 | Fire Safety And Notices | 45141 | Medium | Court Manager | It was noted the lack of a signage to the lift. Please install signage indicating. "In the event of a fire do not use the lift" | Signs now in place
5305 | Skeels Court | SKEELS_S001 | H21 | Scheme | 2022-01-07 13:29 | FRA_5305060120221709.pdf | colej | 5305060120221700 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | on1a21l4e1ky4ep7cr | Medium Risk closed | Risk Closed | 44588.4952 | Obs7 | Fire Protection Measures | 44933 | Medium | Court Manager | It was noted at the time of the inspection the balcony walkways had lots of personal items outside the properties that could become a trip hazard in the event of incident requiring urgent escape. It is recommended that this is reviewed by the court manager and housing manager with a view to minimise the amount of items on the escape route. | Trevor Lyndsay from Cambs Fire and rescue visited and said that the balcony walkways were ok as they were if managed A report was emailed to Jason Cole
5305 | Skeels Court | SKEELS_S001 | H21 | Scheme | 2022-01-07 13:29 | FRA_5305060120221709.pdf | colej | 5305060120221700 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | nbvkb0jpycky4evyz7 | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45298 | Low | Court Manager | At the time of inspection it was noted that the electrical meter boxes on the walkways externally to the properties did not appear to have adequate fire stopping to the cable routes entering the building. It is recommended that these are addressed by a suitable competent contractor using a putty based intumescent fire stopping compound and specifically not pink fire foam. | NULL
5305 | Skeels Court | SKEELS_S001 | H21 | Scheme | 2022-01-07 13:29 | FRA_5305060120221709.pdf | colej | 5305060120221700 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | 1cq9sgxn9jaky48b8e9 | Observation Only | Risk Closed | 44601.4096 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | Currently there no high risk residents on the court | I have completed all my PCFRA and I have no high risk residents on court. I will continue to monitor my medium risk and any other circumstances that may change
5305 | Skeels Court | SKEELS_S001 | H21 | Scheme | 2022-01-07 13:29 | FRA_5305060120221709.pdf | colej | 5305060120221700 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | 3b4t18n4oj5ky491asm | Low Risk closed | Risk Closed | 44747.5946 | Obs7 | Fire Protection Measures | 45298 | Low | Surveyor | It was noted that the fire exits have a combination of doors that require more than a single action to operate and not all doors open in the direction of travel. It is recommended that they are changed at the next replacement upgrade programme. | Surveys have been carried out and are to be implemented in the coming years investment works.
5306 | St Edmunds Court | STEDMUND_S001 | H21 | Scheme | 2022-07-05 14:06 | FRA_5306040720221702.pdf | colej | 5306040720221700 | Extra Care | Extra Care South | EC South 2 | Central | Central Patch 3 | rhktg75td4l586bp3j | Observation Only | Risk Closed | 44748.4131 | Obs7 | Fire Protection Measures | NULL | N/A | Court Manager | It was noted that there are the use of door mats outside a tiny amount of properties. These were not considered a hazard as they are kept within the reveals of the door entrances and with minimal thickness to cause a trip hazard. It is suggested that this is monitored in the event there is an issue with the size or type of Matt used in future. | N/A
5307 | De Ramsey Court | DERAMSEY_S001 | H21 | Scheme | 2022-01-05 11:50 | FRA_5307050120221106.pdf | colej | 5307050120221100 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | t92io0hrpleky1fr97r | Low Risk closed | Risk Closed | 44586.702 | Obs7 | Fire Protection Measures | 45296 | Low | Court Manager | Not all doors are considered as escape exits and some doors have thumbturn operations and are key operated. It is worth considering having these changed at the next upgrade opportunity to allow for easier escape if alternative escape routes and comprised. | This is to be dealt with by asset management in the future as part of a SIPP program, so no further action is required by myself as the court manager.
5307 | De Ramsey Court | DERAMSEY_S001 | H21 | Scheme | 2022-01-05 11:50 | FRA_5307050120221106.pdf | colej | 5307050120221100 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | oh2sfksuarky1fr98e | Observation Only | Risk Closed | 44586.7022 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Court Manager | It is assumed that the doors are FD30 as there are no clear markings to identify them. All doors have intumescent smoke seals and door closers. A list of all doors inspected and their findings are listed within the document. | No further action required.
5307 | De Ramsey Court | DERAMSEY_S001 | H21 | Scheme | 2022-01-05 11:50 | FRA_5307050120221106.pdf | colej | 5307050120221100 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | 1zi210c3gz3ky1fr970 | Medium Risk closed | Risk Closed | 44595.6956 | Obs6 | Fire Hazards - Elimination & Control | 44931 | Medium | Surveyor | It was noted that there are electrical meter boxes serving each property located in the communal corridors. There is no evidence of intumescent fire stopping at cable routes entering the flats following the recent heating upgrade works. These need to be addressed by the surveyor with the installation contractor prior to sign off of works. | The fire stopping works have now been completed by SSE following the planned works upgrade of the storage heaters. This was concluded on the 13th January 2022.
5309 | Bishopsfield Court | BISHOPSFIELD_S001 | H21 | Scheme | 2022-03-07 14:08 | FRA_5309070320221342.pdf | colej | 5309070320221340 | Extra Care | Extra Care South | EC South 2 | Central | Central Patch 3 | 0bo3nice5cdsl0gr5up0 | Low Risk closed | Risk Closed | 44763.612 | Obs6 | Fire Hazards - Elimination & Control | 45358 | Low | Court Manager | It was noted at the time of inspection a build up of waste materials beside the separate house (no50) and refuse room. A works order has been requested for the removal by CGM and will be done shortly. | Had some one come in to remove rubbish
5309 | Bishopsfield Court | BISHOPSFIELD_S001 | H21 | Scheme | 2022-03-07 14:08 | FRA_5309070320221342.pdf | colej | 5309070320221340 | Extra Care | Extra Care South | EC South 2 | Central | Central Patch 3 | kiqpc2ik58l0gr5uo5 | Observation Only | Risk Closed | 44628.665 | Obs5 | Evacuation Strategy And Training | NULL | N/A | Court Manager | Although there is a stay put policy for the court, the current assembly point for the place of ultimate safety is within the main car park and is documented within the court fire plan. For clarity, It was noted and agreed with the court managers that the 2 main communal lounges on both the ground and first floors offer a place of relative safety to residents who may be outside of their flats and within the communal areas in the event of a fire alarm activation and not in immediate proximity of a fire. It is been deemed unsafe nor practical to move all residents to a single place of relative safety when there are multiple options available For those with less mobility can take refuge within the pod areas located between fires doors on each corridor. Each pod area on the ground floor offers a means of escape from the building to ultimate safety. | It has been agreed if residents out of there flat they can go in pod lounge or main lounge up stairs or down stairs
5312 | Denis Wilson Court | DENISWILS_S001 | H21 | Scheme | 2022-05-12 12:21 | FRA_5312120520221038.pdf | colej | 5312120520221030 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 3 | 8434axu15uhl32uzqzs | Observation Only | Risk Closed | 44778.7486 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Other | Only flats 27-30 share a single escape route and therefore have specific fire doors with self closing devices. | n/a observation only
5313 | McNish Court | MCNISH_S001 | H21 | Scheme | 2022-11-02 15:22 | FRA_5313021120221114.pdf | doerrd | 5313021120221110 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 1 | d7zomn1wtxel9zjkttx | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45598 | Low | Surveyor | Lift motor room hole remains from lift replacement | NULL
5313 | McNish Court | MCNISH_S001 | H21 | Scheme | 2022-11-02 15:22 | FRA_5313021120221114.pdf | doerrd | 5313021120221110 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 1 | du0ni8lm9fwl9zjktuk | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45598 | Low | Surveyor | Store cupboard by CM office needs sealing around penetrations. | NULL
5313 | McNish Court | MCNISH_S001 | H21 | Scheme | 2022-11-02 15:22 | FRA_5313021120221114.pdf | doerrd | 5313021120221110 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 1 | 3dstkxxcbwsl9zjktsu | Observation Only | Risk Closed | 44868.5857 | Obs6 | Fire Hazards - Elimination & Control | NULL | N/A | Court Manager | Metal meter cupboard doors will provide nominal protection however some are left slightly open and the protection cannot be guaranteed. | Check all meter boxes every week on walk around, some are warped
5313 | McNish Court | MCNISH_S001 | H21 | Scheme | 2022-11-02 15:22 | FRA_5313021120221114.pdf | doerrd | 5313021120221110 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 1 | 3jm66o3j3xbl9zrx4t1 | Medium Risk to be actioned | Risk Open | NULL | Obs1 | The Building | 45232 | Medium | Surveyor | Redundant milkman panels through to each flat have been blocked off however the structure may not provide 30mins fire protection. These should be blocked off with 15mm plaster board and skimmed removing the compartment breach. | NULL
5313 | McNish Court | MCNISH_S001 | H21 | Scheme | 2022-11-02 15:22 | FRA_5313021120221114.pdf | doerrd | 5313021120221110 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 1 | t15esvfgzfql9zsb8e6 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45598 | Low | Court Manager | Guest room door closer requires adjustment or replacement to ensure that the door closes fully. | NULL
5313 | McNish Court | MCNISH_S001 | H21 | Scheme | 2022-11-02 15:22 | FRA_5313021120221114.pdf | doerrd | 5313021120221110 | Retirement Housing | East Anglia | Cambridgeshire and Bedfordshire | Central | Central Patch 1 | u0f13j6062gl9zjktta | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45598 | Low | Surveyor | Court managers office has extension leads in use, these will be done away with during planned makeover. | NULL
5401 | George Culmer Court | GEORGECULMER_S001 | H21 | Scheme | 2022-04-27 14:53 | FRA_5401270420221440.pdf | LingF | 5401270420221440 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | npcra2px6ll2hmjzj4 | Observation Only | Risk Closed | 44763.4681 | Obs16 | Testing And Maintenance | NULL | N/A | Surveyor | Sprinklers _ 10/2021. Lightening _ 6/2021 | Info
5401 | George Culmer Court | GEORGECULMER_S001 | H21 | Scheme | 2022-04-27 14:53 | FRA_5401270420221440.pdf | LingF | 5401270420221440 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | p5qgf2c30col2hmjzi9 | Low Risk closed | Risk Closed | 44684.4729 | Obs6 | Fire Hazards - Elimination & Control | 45409 | Low | Court Manager | Clear flammable Items from comms cupboard | Paper etc removed on 28.04.22. See photo attached.
5401 | George Culmer Court | GEORGECULMER_S001 | H21 | Scheme | 2022-04-27 14:53 | FRA_5401270420221440.pdf | LingF | 5401270420221440 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | j7oyv1kbhpl2hmjzhe | Observation Only | Risk Closed | 44763.468 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Surveyor | Residents are supported by care staff on site, this would be over a 24hr period. | Info
5401 | George Culmer Court | GEORGECULMER_S001 | H21 | Scheme | 2022-04-27 14:53 | FRA_5401270420221440.pdf | LingF | 5401270420221440 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | h6nllclecml2hmjzgg | Observation Only | Risk Closed | 44763.4682 | Obs1 | The Building | NULL | N/A | Surveyor | General facade view | Info
5402 | Alfred Deller Court | ALFREDDELLER_S001 | H21 | Scheme | 2021-12-15 15:26 | FRA_5402151220211146.pdf | LingF | 5402151220211140 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | hmw51gmi9xbkx7gxdj3 | Observation Only | Risk Closed | 44546.3176 | Obs13 | Other Relevant Fixed Systems | NULL | N/A | Surveyor | MOV | Info only
5402 | Alfred Deller Court | ALFREDDELLER_S001 | H21 | Scheme | 2021-12-15 15:26 | FRA_5402151220211146.pdf | LingF | 5402151220211140 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | hy656ijjwrekx7gxdeg | Observation Only | Risk Closed | 44593.3624 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Court Manager | Example of MOV on corridor and stairwell | N/A
5402 | Alfred Deller Court | ALFREDDELLER_S001 | H21 | Scheme | 2021-12-15 15:26 | FRA_5402151220211146.pdf | LingF | 5402151220211140 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | kp4y0kklethkx7gxdgi | Observation Only | Risk Closed | 44546.3178 | Obs9 | Escape Lighting | NULL | N/A | Surveyor | System meets requirements of BS :5266 | Info only
5402 | Alfred Deller Court | ALFREDDELLER_S001 | H21 | Scheme | 2021-12-15 15:26 | FRA_5402151220211146.pdf | LingF | 5402151220211140 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | jwyl80wr25kx7gxdjw | Observation Only | Risk Closed | 44593.3626 | Obs16 | Testing And Maintenance | NULL | N/A | Court Manager | Sprinklers _ 15/10/21 Gas safety _ 2/2020 FAT/PAT _ 5/2021 FFE _ 11.2021 Evac drill _ 10.2021 | N/A
5402 | Alfred Deller Court | ALFREDDELLER_S001 | H21 | Scheme | 2021-12-15 15:26 | FRA_5402151220211146.pdf | LingF | 5402151220211140 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | jn0l8xwf8xnkx7gxddi | Observation Only | Risk Closed | 44546.318 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel and call point | Info only
5402 | Alfred Deller Court | ALFREDDELLER_S001 | H21 | Scheme | 2021-12-15 15:26 | FRA_5402151220211146.pdf | LingF | 5402151220211140 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | qq9id6hjiajkx7gy1o0 | Observation Only | Risk Closed | 44546.3177 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Surveyor | A number of residents present as high risk, these risks are mitigated by the 24/7 Care support on site. Thevstaffing levels range from 1 night shift up to 7 during the day. | Info only
5402 | Alfred Deller Court | ALFREDDELLER_S001 | H21 | Scheme | 2021-12-15 15:26 | FRA_5402151220211146.pdf | LingF | 5402151220211140 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | r1sy52ny90pkx7ooywa | Low Risk closed | Risk Closed | 44593.3638 | Obs4 | The Occupant - Information Provided By The Court Manager | 45275 | Low | Court Manager | F8 _ Has mobility issues and tendency to board belongings. | On going monitoring by onsite support staff and myself 're hoarding; advice on storage and review PCFRA as necessary.
5402 | Alfred Deller Court | ALFREDDELLER_S001 | H21 | Scheme | 2021-12-15 15:26 | FRA_5402151220211146.pdf | LingF | 5402151220211140 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | 2di0ccy5o5mkx7gxdcl | Observation Only | Risk Closed | 44546.3174 | Obs1 | The Building | NULL | N/A | Surveyor | General elevation view showing extent of cladding panels and balcony structures | Info only
5402 | Alfred Deller Court | ALFREDDELLER_S001 | H21 | Scheme | 2021-12-15 15:26 | FRA_5402151220211146.pdf | LingF | 5402151220211140 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | xo4zmx1siykkx7gxdhc | Observation Only | Risk Closed | 44546.3175 | Obs10 | Fire Safety And Notices | NULL | N/A | Surveyor | Signage appears to meet requirements of BS:5499 | Info only
5402 | Alfred Deller Court | ALFREDDELLER_S001 | H21 | Scheme | 2021-12-15 15:26 | FRA_5402151220211146.pdf | LingF | 5402151220211140 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | xrqntcnqiy9kx7gxdf2 | Medium Risk closed | Risk Closed | 44901.5293 | Obs8 | Measures To Limit Fire Spread And Development | 44910 | Medium | Court Manager | Remove pink foam from elec riser cupboards door frame, Replace with suitable intumescent putty | DMA completed works.
5402 | Alfred Deller Court | ALFREDDELLER_S001 | H21 | Scheme | 2021-12-15 15:26 | FRA_5402151220211146.pdf | LingF | 5402151220211140 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | zn3huqsddockx7gxdft | Observation Only | Risk Closed | 44593.3622 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Court Manager | Damage to smoke seal F3 to be monitored | N/A
5402 | Alfred Deller Court | ALFREDDELLER_S001 | H21 | Scheme | 2021-12-15 15:26 | FRA_5402151220211146.pdf | LingF | 5402151220211140 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | zutd8zgbj5kx7gxdi9 | Observation Only | Risk Closed | 44593.362 | Obs11 | Fire Fighting Equipment | NULL | N/A | Court Manager | Sprinkler system dis room | N/A
5403 | Emily Court | EMILY_S001 | H21 | Scheme | 2022-07-27 21:29 | FRA_5403270720222118.pdf | BhopalP | 5403270720222110 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood1 | South | South Patch 6 | 6w1dl060c3rl64239x3 | Observation Only | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Court Manager | CM to check final exit doors on monthly basis to ensure that they open easily. | NULL
5406 | Summer Court | SUMMER_S001 | H21 | Scheme | 2022-08-23 13:31 | FRA_5406230820220956.pdf | LingF | 5406230820220950 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | 6vxhkmzo266l764htxv | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45527 | Low | Court Manager | Broken fire door mag holder, grd floor corridor unable to test door closing | NULL
5406 | Summer Court | SUMMER_S001 | H21 | Scheme | 2022-08-23 13:31 | FRA_5406230820220956.pdf | LingF | 5406230820220950 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | 7vesgyl2adml7617hx5 | Observation Only | Risk Closed | 44813.4458 | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | KFRS are due to undertake a scheme residents meeting 9/2022. | N/A
5406 | Summer Court | SUMMER_S001 | H21 | Scheme | 2022-08-23 13:31 | FRA_5406230820220956.pdf | LingF | 5406230820220950 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | 2odgrndxannl761eidt | Low Risk closed | Risk Closed | 44809.4213 | Obs2 | Means Of Giving Warning In Case Of Fire | 45527 | Low | Court Manager | Zone chart is faded and hard to read | Freshed writing and new frame
5406 | Summer Court | SUMMER_S001 | H21 | Scheme | 2022-08-23 13:31 | FRA_5406230820220956.pdf | LingF | 5406230820220950 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | 09syugdydv2l765k4wa | Observation Only | Risk Closed | 44854.7689 | Obs1 | The Building | NULL | N/A | Surveyor | General elevation view showing example of cladding panels forming bay windows. | Info
5406 | Summer Court | SUMMER_S001 | H21 | Scheme | 2022-08-23 13:31 | FRA_5406230820220956.pdf | LingF | 5406230820220950 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | jk6hykfv0ql763mivu | Medium Risk closed | Risk Closed | 44858.3669 | Obs8 | Measures To Limit Fire Spread And Development | 45161 | Medium | Court Manager | Damaged fire compartment ceiling, top floor in front of lift | Checkmate attened site and completed task 19/10/2022
5406 | Summer Court | SUMMER_S001 | H21 | Scheme | 2022-08-23 13:31 | FRA_5406230820220956.pdf | LingF | 5406230820220950 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | jxll0769vl75yi5rn | Observation Only | Risk Closed | 44813.4456 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | F8 _ reduced mobility, heavy smoker, FRS aware ahve provided safe smoking aids, would require assistance to evacuate. Understands risk of smoking with poor mobility. F11 _ Bed bound not able weight bear, non smoker, wife is main carer. F20 _ not able to transfer without assistance to wheelchair. F24 _ mental impairment wouldn't respond to alarms, poor mobility, non cooker, non smoker. F31 _ reduced mobility, non smoker, occasional cooker,. F32 _ reduced mobility would require assistance, non smoker, non cooker, F38 _ reduced mobility, smoker, FRS aware and have provided safe smoke aids. | N/A
5406 | Summer Court | SUMMER_S001 | H21 | Scheme | 2022-08-23 13:31 | FRA_5406230820220956.pdf | LingF | 5406230820220950 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | ka11oudr4al761tduw | Low Risk closed | Risk Closed | 44812.6014 | Obs8 | Measures To Limit Fire Spread And Development | 45527 | Low | Court Manager | Missing intu strip behind auto door into buggy room area | Dma has fitted block of timber into the door where hinge cut out previously and fitted a new section of intumescent smoke seal
5406 | Summer Court | SUMMER_S001 | H21 | Scheme | 2022-08-23 13:31 | FRA_5406230820220956.pdf | LingF | 5406230820220950 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | lu0b4zd8inrl761l1u8 | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45527 | Low | Court Manager | Trailing lead and extension cable within kitchen office, allow to ad additional wired sockets to remove the need for an extension block. | NULL
5406 | Summer Court | SUMMER_S001 | H21 | Scheme | 2022-08-23 13:31 | FRA_5406230820220956.pdf | LingF | 5406230820220950 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | m6t3crhun3l761fvct | Observation Only | Risk Closed | 44854.7688 | Obs5 | Evacuation Strategy And Training | NULL | N/A | Surveyor | CM undertakes an annual fire drill with the care team | Info
5406 | Summer Court | SUMMER_S001 | H21 | Scheme | 2022-08-23 13:31 | FRA_5406230820220956.pdf | LingF | 5406230820220950 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | i3uyasj3qvl763q0at | Medium Risk closed | Risk Closed | 44847.6363 | Obs8 | Measures To Limit Fire Spread And Development | 44796 | Medium | Court Manager | Flat doors infill panels fail to meet FD30 fire rated construction. Panels to be removed and replaced with suitable fire rated infill. The remaining screen complies to FD30 design standards | DMA ave confirmed that during survey it was found that the door panels were made of cut down 60 minute fire doors
5406 | Summer Court | SUMMER_S001 | H21 | Scheme | 2022-08-23 13:31 | FRA_5406230820220956.pdf | LingF | 5406230820220950 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | zhbg9uqckzl761d32h | Observation Only | Risk Closed | 44813.4453 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Court Manager | Fire panel and zone chart | All up to date
5407 | Dolphin Court | DOLPHIN_S001 | H21 | Scheme | 2022-08-25 12:59 | FRA_5407250820221154.pdf | LingF | 5407250820221150 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | wbr9pge4usl78ygd3r | Observation Only | Risk Closed | 44854.7691 | Obs16 | Testing And Maintenance | NULL | N/A | Surveyor | Alarm test undertaken by CM, this is a simple push button test of hardwired domestic detection. | Info
5407 | Dolphin Court | DOLPHIN_S001 | H21 | Scheme | 2022-08-25 12:59 | FRA_5407250820221154.pdf | LingF | 5407250820221150 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | iv1mhueizkl78y8uj8 | Observation Only | Risk Closed | 44854.7691 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Surveyor | Travel distance kept below the 7m BREG requirements for AOV's, first floor corridor does have opening Windows. | Info
5407 | Dolphin Court | DOLPHIN_S001 | H21 | Scheme | 2022-08-25 12:59 | FRA_5407250820221154.pdf | LingF | 5407250820221150 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | fam374u8iqcl78xx0ch | Observation Only | Risk Closed | 44803.6146 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | No high risk residents recorded, customers who have greater needs have 24hr 1_2_1 support | No action required, two residents support by a 121 carer staff 24/7 peep in place and tenants staff would assist with evacuation.
5407 | Dolphin Court | DOLPHIN_S001 | H21 | Scheme | 2022-08-25 12:59 | FRA_5407250820221154.pdf | LingF | 5407250820221150 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | mu0euz2ihukl78ysvwn | Observation Only | Risk Closed | 44854.769 | Obs1 | The Building | NULL | N/A | Surveyor | General elevation view showing extent of cladding panels forming bay windows less than Metal balcony structures | Info
5407 | Dolphin Court | DOLPHIN_S001 | H21 | Scheme | 2022-08-25 12:59 | FRA_5407250820221154.pdf | LingF | 5407250820221150 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | sx2kjsmqz6nl78y0eja | Observation Only | Risk Closed | 44803.6134 | Obs5 | Evacuation Strategy And Training | NULL | N/A | Court Manager | NHSM undertakes training where appropriate for all staff, 2 sleeping care support. Care team employed by the customers have induction at time of tenancy sign up. | No action required. All staff have a building safety induction and on completion of tenancy sign up with new residents care/family support.
5407 | Dolphin Court | DOLPHIN_S001 | H21 | Scheme | 2022-08-25 12:59 | FRA_5407250820221154.pdf | LingF | 5407250820221150 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | qfvssag8sul78z7gdw | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45529 | Low | Court Manager | Missing intumescent strip 1st floor service riser cupboard. | NULL
5407 | Dolphin Court | DOLPHIN_S001 | H21 | Scheme | 2022-08-25 12:59 | FRA_5407250820221154.pdf | LingF | 5407250820221150 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | op2p379kijhl78ywo80 | Observation Only | Risk Closed | 44803.6122 | Obs5 | Evacuation Strategy And Training | NULL | N/A | Court Manager | Fire evac drill _ 1/2022 | Record of fire evacuation drills within fire folder log.
5407 | Dolphin Court | DOLPHIN_S001 | H21 | Scheme | 2022-08-25 12:59 | FRA_5407250820221154.pdf | LingF | 5407250820221150 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | 8lftcqaknwpl78z3ae9 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45529 | Low | Court Manager | Repair damage to fire stopping bed floor service riser ceiling. Missing intu strip on same cupboard door. | NULL
5407 | Dolphin Court | DOLPHIN_S001 | H21 | Scheme | 2022-08-25 12:59 | FRA_5407250820221154.pdf | LingF | 5407250820221150 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | 9uudiig9vdl78ye8me | Observation Only | Risk Closed | 44803.6138 | Obs16 | Testing And Maintenance | NULL | N/A | Court Manager | Sprinkler _ 6/2022 Lightening _ 5/2022 GAS _ 5/2022 | No action required
5408 | Tiger Court | TIGER_S001 | H21 | Scheme | 2022-02-14 13:22 | FRA_5408140220221221.pdf | LingF | 5408140220221220 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | 8mcrq62t6shkzmo0xf5 | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45336 | Low | Court Manager | Additional fire escape signage required on stairwell directing to ground floor escape areas | NULL
5408 | Tiger Court | TIGER_S001 | H21 | Scheme | 2022-02-14 13:22 | FRA_5408140220221221.pdf | LingF | 5408140220221220 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | fdxgymvaoekkzmo0xdl | Low Risk closed | Risk Closed | 44887.6791 | Obs5 | Evacuation Strategy And Training | 45336 | Low | Court Manager | Carers training records not within fire folder | It was in the fire folder but must've missed it.
5408 | Tiger Court | TIGER_S001 | H21 | Scheme | 2022-02-14 13:22 | FRA_5408140220221221.pdf | LingF | 5408140220221220 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | d1lryxxn4rvkzmo0xcs | Medium Risk to be actioned | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | 44971 | Medium | Court Manager | Missing fire detection to meet L2 requirements on all landing levels as noted with fire strategy document within fire folder Extended detection to upper corridors and individual compartments. | NULL
5408 | Tiger Court | TIGER_S001 | H21 | Scheme | 2022-02-14 13:22 | FRA_5408140220221221.pdf | LingF | 5408140220221220 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | dn17uiqaelgkzmo0xem | Low Risk closed | Risk Closed | 44901.5239 | Obs8 | Measures To Limit Fire Spread And Development | 45336 | Low | Court Manager | Evidence of missing or unsuitable fire stopping within the loft space. Undertake stopping up of gaps passing through fire break walls and compartments. | DMA contractors completed works 4/5/22
5408 | Tiger Court | TIGER_S001 | H21 | Scheme | 2022-02-14 13:22 | FRA_5408140220221221.pdf | LingF | 5408140220221220 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | 0i97lz6f35cskzmo0xga | Observation Only | Risk Closed | 44630.4197 | Obs16 | Testing And Maintenance | NULL | N/A | Court Manager | Evac drills undertaken _ 12/2021 | N/A
5408 | Tiger Court | TIGER_S001 | H21 | Scheme | 2022-02-14 13:22 | FRA_5408140220221221.pdf | LingF | 5408140220221220 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | 6foyad16o4jkzmo0xc8 | Observation Only | Risk Closed | 44742.602 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel | Info only
5408 | Tiger Court | TIGER_S001 | H21 | Scheme | 2022-02-14 13:22 | FRA_5408140220221221.pdf | LingF | 5408140220221220 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | rvgkpx9g2p9kzmo0xfq | Low Risk closed | Risk Closed | 44887.6817 | Obs15 | Management Of Fire Safety | 45336 | Low | Court Manager | Missing fire procedure training/refresher training within the fire folder | H21 DVD provided for staff to view and sign as seen.
5408 | Tiger Court | TIGER_S001 | H21 | Scheme | 2022-02-14 13:22 | FRA_5408140220221221.pdf | LingF | 5408140220221220 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | mx6m58csqskzmpwq9i | Medium Risk closed | Risk Closed | 44887.6806 | Obs6 | Fire Hazards - Elimination & Control | 44971 | Medium | Court Manager | No record of 5yr HARDr wire testing. Date noted above is construction date. | DMA completed this 8/03/2022
5408 | Tiger Court | TIGER_S001 | H21 | Scheme | 2022-02-14 13:22 | FRA_5408140220221221.pdf | LingF | 5408140220221220 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | hqayk74p27jkzmo0xe8 | Low Risk closed | Risk Closed | 44901.5224 | Obs8 | Measures To Limit Fire Spread And Development | 45336 | Low | Court Manager | Flat doors general note: excessive gapping around door seal, allow to close down with extended intumescent brush strip | DMA contractors completed works
5408 | Tiger Court | TIGER_S001 | H21 | Scheme | 2022-02-14 13:22 | FRA_5408140220221221.pdf | LingF | 5408140220221220 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | zkg4mnytjtkzmo0xbg | Observation Only | Risk Closed | 44742.6019 | Obs1 | The Building | NULL | N/A | Surveyor | General elevation view showing extent of cladding panels and balcony structures | Info only
5411 | John Goldfinch Court | JOHNGOLDFINCH_S001 | H21 | Scheme | 2022-11-02 22:09 | FRA_5411011120220847.pdf | BhopalP | 5411011120220840 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 6 | 2un9zo7047yla06gvwc | Observation Only | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | Residents have varying individual care packages. The scheme has a sleeping care staff member. | NULL
5412 | Watercress Court | WATERCRESS_S001 | H21 | Scheme | 2022-07-01 22:17 | FRA_5412010720222148.pdf | BhopalP | 5412010720222140 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood1 | South | South Patch 6 | fdj6m1t2oj8l52xgwb3 | Observation Only | Risk Closed | 44746.4253 | Obs1 | The Building | NULL | N/A | Court Manager | BBQs are prohibited. | No outstanding risks are due to be actioned.
5413 | Bradstow Court | BRADSTOW_S001 | H21 | Scheme | 2021-12-23 09:25 | FRA_5413231220210913.pdf | LingF | 5413231220210910 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | b46gcaq7uedkxiqzrmn | Observation Only | Risk Closed | 44578.6551 | Obs5 | Evacuation Strategy And Training | NULL | N/A | Surveyor | Stairwell landings are designated as refuge points. | Info only
5413 | Bradstow Court | BRADSTOW_S001 | H21 | Scheme | 2021-12-23 09:25 | FRA_5413231220210913.pdf | LingF | 5413231220210910 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | arlva4qb4ckkxiqzeal | Medium Risk closed | Risk Closed | 44567.6102 | Obs8 | Measures To Limit Fire Spread And Development | 44918 | Medium | Court Manager | Bin room door closer not operational when door fully open | DMA have fixed the door and it is now operational when fully open.
5413 | Bradstow Court | BRADSTOW_S001 | H21 | Scheme | 2021-12-23 09:25 | FRA_5413231220210913.pdf | LingF | 5413231220210910 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | 681t2znfmnbkxiqze4h | Medium Risk closed | Risk Closed | 44614.6452 | Obs2 | Means Of Giving Warning In Case Of Fire | 44918 | Medium | Court Manager | Extend smoke alarm system into the staff sleeping room used by consultant for beauty treatments | DMA have actioned this with Tunstall to connect to fire alarm to smoke alarm.
5413 | Bradstow Court | BRADSTOW_S001 | H21 | Scheme | 2021-12-23 09:25 | FRA_5413231220210913.pdf | LingF | 5413231220210910 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | 7l6qkmpk7x8kxiqzebi | Medium Risk closed | Risk Closed | 44573.6511 | Obs8 | Measures To Limit Fire Spread And Development | 44918 | Medium | Court Manager | Door to elec intake requires realignment | DMA have now realignd the door.
5413 | Bradstow Court | BRADSTOW_S001 | H21 | Scheme | 2021-12-23 09:25 | FRA_5413231220210913.pdf | LingF | 5413231220210910 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | 4tnni3311jlkxiqze7z | Low Risk closed | Risk Closed | 44573.4207 | Obs6 | Fire Hazards - Elimination & Control | 45283 | Low | Court Manager | Items stored within corridors including buggy these areas should be kept sterile as far as practically possible. | Spoke with resident, his visitor only stays a short period of time and has poor mobility. Explained the risk of electric buggy being stored in the corridor.
5413 | Bradstow Court | BRADSTOW_S001 | H21 | Scheme | 2021-12-23 09:25 | FRA_5413231220210913.pdf | LingF | 5413231220210910 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | fkxevzixjhckxiqzeb3 | Low Risk closed | Risk Closed | 44593.4592 | Obs8 | Measures To Limit Fire Spread And Development | 45283 | Low | Court Manager | Old cooking oil stored in bin room, when is this collected can it be stored externally and away from the building | Contacted compass who have arranged and ordered oil containers to store the oil so it rejuces the risk from the fire risk assessment.
5413 | Bradstow Court | BRADSTOW_S001 | H21 | Scheme | 2021-12-23 09:25 | FRA_5413231220210913.pdf | LingF | 5413231220210910 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | n46c51ry7iikxiqze73 | Observation Only | Risk Closed | 44567.6116 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | Flats noted as high risk within resident profile. In the event of a fire evacuation from the flat for non weight bearing occupants the procedure would be to use bedding as an evac slide. F4 _ does not pose a higher risk of causing fire risk within their flat does not cook or smoke etc. F5 _ as above F6 _ as above F18 _ ablè to live independently risk high profile due to non weight bearing. F19 _ as above, does not cook. F20 _ as F4 F23 _ support form full time care whilst awake, non weight bearing. F37 _ as F18 F38 _ visual impairment, able to mobilise and wpuld be able to evac property unaided. F39 _ Double occupancy, smoker within property does not pose a risk due to to smoking, FRS aware of occupants and manage with home safety visits. | Occupant Information up dated every 6 months or when required.
5413 | Bradstow Court | BRADSTOW_S001 | H21 | Scheme | 2021-12-23 09:25 | FRA_5413231220210913.pdf | LingF | 5413231220210910 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | r3d7hwblowkxiqzebz | Medium Risk closed | Risk Closed | 44601.4648 | Obs8 | Measures To Limit Fire Spread And Development | 44918 | Medium | Court Manager | Rake out pink foam from fire batts elec intake cupboard | Reported to DMA and this has been passed to Checkmate fire to complete.
5413 | Bradstow Court | BRADSTOW_S001 | H21 | Scheme | 2021-12-23 09:25 | FRA_5413231220210913.pdf | LingF | 5413231220210910 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | nt7sg5r0wutkxiqze9w | Medium Risk closed | Risk Closed | 44601.4661 | Obs8 | Measures To Limit Fire Spread And Development | 44918 | Medium | Court Manager | Poorly fitting door from kitchen to escape stairs, close down perimter gapping. Check operation of door guard device | This job has been completed by DMA.
5413 | Bradstow Court | BRADSTOW_S001 | H21 | Scheme | 2021-12-23 09:25 | FRA_5413231220210913.pdf | LingF | 5413231220210910 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | yv399drh8dkxiqze8r | Medium Risk closed | Risk Closed | 44601.4654 | Obs8 | Measures To Limit Fire Spread And Development | 44918 | Medium | Court Manager | Holes passing through fire rated ceiling in front of lift top floor | This has been reported to DMA and passed on to Checkmate fire to complete.
5413 | Bradstow Court | BRADSTOW_S001 | H21 | Scheme | 2021-12-23 09:25 | FRA_5413231220210913.pdf | LingF | 5413231220210910 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | ve0burc26gdkxiqze3u | Observation Only | Risk Closed | 44578.6552 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel and zone chart | Info only
5413 | Bradstow Court | BRADSTOW_S001 | H21 | Scheme | 2021-12-23 09:25 | FRA_5413231220210913.pdf | LingF | 5413231220210910 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | uy042p3vkbikxiqze2v | Observation Only | Risk Closed | 44578.655 | Obs1 | The Building | NULL | N/A | Surveyor | External view showing extent of cladding panels | Info only
5413 | Bradstow Court | BRADSTOW_S001 | H21 | Scheme | 2021-12-23 09:25 | FRA_5413231220210913.pdf | LingF | 5413231220210910 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 2 | South | South Patch 3 | uyg314ky2rkxiqze9c | Low Risk closed | Risk Closed | 44593.4642 | Obs8 | Measures To Limit Fire Spread And Development | 45283 | Low | Court Manager | Gaps to corridor doors adj F31 | Doors have been checked and there are no longer gaps.
5414 | Buckland Court | BUCKLAND_S001 | H21 | Scheme | 2022-09-16 13:36 | FRA_5414160920221325.pdf | LingF | 5414160920221320 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | uv0n003bmnl84ge97j | Observation Only | Risk Closed | 44854.7702 | Obs1 | The Building | NULL | N/A | Surveyor | General elevation view showing extent of cladding panels forming bay windows less than. Timber fitted to masonry substrate | Info
5414 | Buckland Court | BUCKLAND_S001 | H21 | Scheme | 2022-09-16 13:36 | FRA_5414160920221325.pdf | LingF | 5414160920221320 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | xkx8brtd3nnl84ge9gw | Observation Only | Risk Closed | 44854.7701 | Obs16 | Testing And Maintenance | NULL | N/A | Surveyor | Sprinkler _ 1/2022 Catering equipment _ 8/2022 AOV _ 6/2022 Lightening _ 8/2022 Dry riser _ 7/2022 | Info
5414 | Buckland Court | BUCKLAND_S001 | H21 | Scheme | 2022-09-16 13:36 | FRA_5414160920221325.pdf | LingF | 5414160920221320 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | nmxbz5kcjil84ge9cz | Observation Only | Risk Closed | 44826.4312 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Court Manager | Door guard devices fitted to Stairwell doors, ensure testing regime in place to check full operation when alarm sounds. | these have been disabled as they do not close when a;atm activates
5414 | Buckland Court | BUCKLAND_S001 | H21 | Scheme | 2022-09-16 13:36 | FRA_5414160920221325.pdf | LingF | 5414160920221320 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | ozghxsdixfsl84ge98i | Observation Only | Risk Closed | 44854.7699 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | System links to onsite care team for the full 24hr period | Info
5414 | Buckland Court | BUCKLAND_S001 | H21 | Scheme | 2022-09-16 13:36 | FRA_5414160920221325.pdf | LingF | 5414160920221320 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | sghdui47nnl84ge9br | Observation Only | Risk Closed | 44826.4309 | Obs5 | Evacuation Strategy And Training | NULL | N/A | Court Manager | Fire drill _ 10/2021 | fire drill booked in
5414 | Buckland Court | BUCKLAND_S001 | H21 | Scheme | 2022-09-16 13:36 | FRA_5414160920221325.pdf | LingF | 5414160920221320 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | lvahgjqxhvsl84ge99y | Observation Only | Risk Closed | 44854.77 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Surveyor | Whiteoaks _ catering and cleaning _ 6 employees Nurse+ _ care team _ 3 during day period _ 1 waking night shift staff member. Given the staffing numbers and building design/Construction this supports a 'stay put' strategy | Info
5414 | Buckland Court | BUCKLAND_S001 | H21 | Scheme | 2022-09-16 13:36 | FRA_5414160920221325.pdf | LingF | 5414160920221320 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | kjyy6y9xw4rl84ge9as | Observation Only | Risk Closed | 44826.4315 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | F9 _ blind and smoker evidence of burns on carpet, past history of fire, KFRS are aware and visit frequently, KFRS have provided aids including support from care team. | ongoing review kent FRS six monthly visits in place
5414 | Buckland Court | BUCKLAND_S001 | H21 | Scheme | 2022-09-16 13:36 | FRA_5414160920221325.pdf | LingF | 5414160920221320 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | 0disdfjkig8jl84ge9e0 | Low Risk closed | Risk Closed | 44854.7703 | Obs8 | Measures To Limit Fire Spread And Development | 45551 | Low | Surveyor | Ceiling on top floor has been constructed to 60mins fire rated construction comprising of double layer plaster board, this design was approved by building control authority as a measure to compensate for the roof void compartments aligning with 8 flats in a compartment. The roof void is managed as a sterile area with detection in each zone. | Info
5414 | Buckland Court | BUCKLAND_S001 | H21 | Scheme | 2022-09-16 13:36 | FRA_5414160920221325.pdf | LingF | 5414160920221320 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | acsi21ot3hkl84ge994 | Observation Only | Risk Closed | 44854.7701 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Panel and zone chart | Info
5414 | Buckland Court | BUCKLAND_S001 | H21 | Scheme | 2022-09-16 13:36 | FRA_5414160920221325.pdf | LingF | 5414160920221320 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | fggyhqmkugql84ge9ev | Low Risk closed | Risk Closed | 44854.7698 | Obs8 | Measures To Limit Fire Spread And Development | 44820 | Low | Surveyor | DMA aware of deficiencies with infill panels works are programmed to upgrade to comply with FD30s designation. Scheme sprinkler system reduces risk to a tolerable level. | Info
5415 | Bleriot Court | BLERIOT_S001 | H21 | Scheme | 2022-09-16 13:24 | FRA_5415160920221224.pdf | LingF | 5415160920221220 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | drk2p33mrc5l84fw50q | Observation Only | Risk Closed | 44854.7697 | Obs1 | The Building | NULL | N/A | Surveyor | Typical elevation view showing extent of cladding panels and balcony structures | Info
5415 | Bleriot Court | BLERIOT_S001 | H21 | Scheme | 2022-09-16 13:24 | FRA_5415160920221224.pdf | LingF | 5415160920221220 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | dpqujsjthmsl84emc4x | Observation Only | Risk Closed | 44854.7698 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Surveyor | Scheme has MOV on each corridor, travel distance within tolerable levels of building regs | Info
5415 | Bleriot Court | BLERIOT_S001 | H21 | Scheme | 2022-09-16 13:24 | FRA_5415160920221224.pdf | LingF | 5415160920221220 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | a2qmx7tn6x9l84ew2xy | Observation Only | Risk Closed | 44854.7696 | Obs15 | Management Of Fire Safety | NULL | N/A | Surveyor | Fire evac drill _ 2/2021 | Info
5415 | Bleriot Court | BLERIOT_S001 | H21 | Scheme | 2022-09-16 13:24 | FRA_5415160920221224.pdf | LingF | 5415160920221220 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | oepgo5sx9p8l84erbch | Observation Only | Risk Closed | 44831.4793 | Obs16 | Testing And Maintenance | NULL | N/A | Court Manager | Sprinkler _ 1/2022 Lightening _ 6/2022 Gas _ 9/2022 | No action required
5415 | Bleriot Court | BLERIOT_S001 | H21 | Scheme | 2022-09-16 13:24 | FRA_5415160920221224.pdf | LingF | 5415160920221220 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | vrv70gf7ri9l84f1bwf | Observation Only | Risk Closed | 44831.4795 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Court Manager | Residents live with a high level of independence with occasional support from care team if required. Scheme has a night shift staff member on duty. | No action required
5416 | Joseph Hadlum Court | JOSEPHHADLUM_S001 | H21 | Scheme | 2021-12-20 16:53 | FRA_5416201220211632.pdf | LingF | 5416201220211630 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | qijnfhtxgrgkxewc4s9 | Low Risk closed | Risk Closed | 44676.4561 | Obs8 | Measures To Limit Fire Spread And Development | 45280 | Low | Court Manager | Elec cupboard _ infill cavity to prevent smoke propagation | Job raised to DMA Job complete 08/04/2022
5416 | Joseph Hadlum Court | JOSEPHHADLUM_S001 | H21 | Scheme | 2021-12-20 16:53 | FRA_5416201220211632.pdf | LingF | 5416201220211630 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | qyjc87cj3wkxewc4pt | Medium Risk closed | Risk Closed | 44578.6543 | Obs4 | The Occupant - Information Provided By The Court Manager | 44915 | Medium | Surveyor | Significant residents risk profile: F31 _ would require double handed support, present level of care support would allow thìs, residents do not pose any significant risk of causing a fire within their flat. F34 _ bed bound, has 24/7 personal care support, oxygen usage. Can be evacuated by on site care team. F5 _ present challenging mental health issues due to alcohol dependency, on site care team have increased in numbers to support living, local FRS aware, safe guarding measures in place with police. On site care team able to access flat to clean and remove rubbish. Resident has a history of arson and poses a considerable risk to the welbeing of the occupants of the scheme. | Info only
5416 | Joseph Hadlum Court | JOSEPHHADLUM_S001 | H21 | Scheme | 2021-12-20 16:53 | FRA_5416201220211632.pdf | LingF | 5416201220211630 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | mitspm4g578kxewc4t6 | Observation Only | Risk Closed | 44578.6549 | Obs12 | Automatic Fire Systems i.e. Suppression System | NULL | N/A | Surveyor | Water mist system | Info only
5416 | Joseph Hadlum Court | JOSEPHHADLUM_S001 | H21 | Scheme | 2021-12-20 16:53 | FRA_5416201220211632.pdf | LingF | 5416201220211630 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | bft8sqie2eqkxewc4oa | Observation Only | Risk Closed | 44578.6544 | Obs1 | The Building | NULL | N/A | Surveyor | General elevation view showing extent of cladding panels forming bay windows less than | Info only
5416 | Joseph Hadlum Court | JOSEPHHADLUM_S001 | H21 | Scheme | 2021-12-20 16:53 | FRA_5416201220211632.pdf | LingF | 5416201220211630 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | fexuidrvrhkxewc4rj | Medium Risk closed | Risk Closed | 44676.4554 | Obs8 | Measures To Limit Fire Spread And Development | 44915 | Medium | Court Manager | Holes passing through 1st floor fire ceiling adj lights to lift area. | Job raised to DMA Job completed 08/04/2022
5416 | Joseph Hadlum Court | JOSEPHHADLUM_S001 | H21 | Scheme | 2021-12-20 16:53 | FRA_5416201220211632.pdf | LingF | 5416201220211630 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | faj2pmogockkxewx7tn | Observation Only | Risk Closed | 44578.6548 | Obs4 | The Occupant - Information Provided By The Court Manager | NULL | N/A | Surveyor | Care team staffing numbers. Day shift_ 7 (max) Night shift _ 1 (waking) | Info only
5416 | Joseph Hadlum Court | JOSEPHHADLUM_S001 | H21 | Scheme | 2021-12-20 16:53 | FRA_5416201220211632.pdf | LingF | 5416201220211630 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | 1451jq5hcq9kxewc4qt | Observation Only | Risk Closed | 44578.6545 | Obs5 | Evacuation Strategy And Training | NULL | N/A | Surveyor | Stairwell landings noted as refuge points | Info only
5416 | Joseph Hadlum Court | JOSEPHHADLUM_S001 | H21 | Scheme | 2021-12-20 16:53 | FRA_5416201220211632.pdf | LingF | 5416201220211630 | PPP-PFI | Kent PFI Services | Kent PFI Neighbourhood 3 | South | South Patch 3 | 6x6ru6dkg73kxewc4p2 | Observation Only | Risk Closed | 44578.6546 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire panel and zone chart | Info only
5602 | Hancock Court | HANCOCK_S001 | H21 | Scheme | 2022-06-10 17:30 | FRA_5602100620220800.pdf | mitchellj1 | 5602100620220800 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 7 | 4szmzwflrtnl48encwm | Low Risk closed | Risk Closed | 44747.4911 | Obs6 | Fire Hazards - Elimination & Control | 45453 | Low | Court Manager | Couldn't see evidence that the mobility scooters in the external store have been PAT tested, please confirm this has been done. | the pat testing is due in November 2022 so will be covered at this time however 3 of the scooters are new so will be covered
5602 | Hancock Court | HANCOCK_S001 | H21 | Scheme | 2022-06-10 17:30 | FRA_5602100620220800.pdf | mitchellj1 | 5602100620220800 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 7 | 4zrff4bi5c5l48em9xx | Medium Risk closed | Risk Closed | 44747.4925 | Obs7 | Fire Protection Measures | 45087 | Medium | Court Manager | Door in communal lounge leading outside is sticking and is difficult to open, please arrange for this to be addressed by a contractor. | discussed with RHM may need to change the frame completely and make more accessible for disability So will look at any funding available, in the mean time the door has been shaved to ease the stickyness
5602 | Hancock Court | HANCOCK_S001 | H21 | Scheme | 2022-06-10 17:30 | FRA_5602100620220800.pdf | mitchellj1 | 5602100620220800 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 7 | 5pwxqbpghmil48d94dr | Low Risk closed | Risk Closed | 44747.4904 | Obs6 | Fire Hazards - Elimination & Control | 45453 | Low | Court Manager | Use of pink foam around service cables to door head near flat 31, these should be suitably fire stopped by a certified contractor. | fire stopping job been put through to all build
5602 | Hancock Court | HANCOCK_S001 | H21 | Scheme | 2022-06-10 17:30 | FRA_5602100620220800.pdf | mitchellj1 | 5602100620220800 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 7 | mm1d4xgbzbkl48ev371 | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45087 | Medium | M&E Team | PAT testing pre-populating as being done in 2018, please advise if this is overdue and arrange if it is. | NULL
5602 | Hancock Court | HANCOCK_S001 | H21 | Scheme | 2022-06-10 17:30 | FRA_5602100620220800.pdf | mitchellj1 | 5602100620220800 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 7 | rs545miswhbl48aclxt | Low Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45093 | Low | Court Manager | Court Manager is required to complete the fire safety manager refresher training, to be booked on. | NULL
5605 | Willow Bank Court | WILLOWBANK_S001 | H21 | Scheme | 2022-07-29 12:54 | FRA_5605290720221219.pdf | JohnsonD | 5605290720221210 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 7 | rdcdricm69rl66e7pr6 | Low Risk to be actioned | Risk Open | NULL | Obs15 | Management Of Fire Safety | 45502 | Low | Court Manager | Local frs to visit to give residents fire safety talks. | NULL
5606 | Mendell Court | MENDELL_S001 | H21 | Scheme | 2022-06-22 06:53 | FRA_5606210620222304.pdf | mitchellj1 | 5606210620222300 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 7 | pv8gzlwhh5il4oprydb | Medium Risk closed | Risk Closed | 44886.4003 | Obs8 | Measures To Limit Fire Spread And Development | 45098 | Medium | Court Manager | Flat 1 and 42:Intumescent strips missing, please arrange for these to be installed. | All strips replaced
5606 | Mendell Court | MENDELL_S001 | H21 | Scheme | 2022-06-22 06:53 | FRA_5606210620222304.pdf | mitchellj1 | 5606210620222300 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 7 | k891loz0cljl4oprybi | Low Risk closed | Risk Closed | 44812.4838 | Obs6 | Fire Hazards - Elimination & Control | 45464 | Low | Court Manager | Please dispose of redundant mobility scooter as discussed. | Scooter has been removed
5606 | Mendell Court | MENDELL_S001 | H21 | Scheme | 2022-06-22 06:53 | FRA_5606210620222304.pdf | mitchellj1 | 5606210620222300 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 7 | for56jb9u4l4opryej | Observation Only | Risk Closed | 44886.4001 | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | See previous notes for training of third party care staff. | Asnot our staff unable to do on line training but trained existing staff and its now been added to their induction
5606 | Mendell Court | MENDELL_S001 | H21 | Scheme | 2022-06-22 06:53 | FRA_5606210620222304.pdf | mitchellj1 | 5606210620222300 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 7 | 4r4b0d2270pl4opryap | Low Risk closed | Risk Closed | 44886.4007 | Obs6 | Fire Hazards - Elimination & Control | 45464 | Low | Court Manager | Please arrange for interim visual checks to be completed to the kitchen and on egress routes to prevent stored items and clutter building up. | This happens weekly
5606 | Mendell Court | MENDELL_S001 | H21 | Scheme | 2022-06-22 06:53 | FRA_5606210620222304.pdf | mitchellj1 | 5606210620222300 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 7 | 6vjaigvxjdvl4opry8w | Low Risk closed | Risk Closed | 44886.4115 | Obs5 | Evacuation Strategy And Training | 45464 | Low | Court Manager | Please confirm care staff have completed fire warden e-learning. | Not H21 staff but have completed their own companies training
5606 | Mendell Court | MENDELL_S001 | H21 | Scheme | 2022-06-22 06:53 | FRA_5606210620222304.pdf | mitchellj1 | 5606210620222300 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 7 | epfajzmf639l4oprycb | Observation Only | Risk Open | NULL | Obs7 | Fire Protection Measures | NULL | N/A | Court Manager | Where doors are thumb turn operated, please consider the suitability of this operates based on resident's needs. | NULL
5606 | Mendell Court | MENDELL_S001 | H21 | Scheme | 2022-06-22 06:53 | FRA_5606210620222304.pdf | mitchellj1 | 5606210620222300 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 7 | a8mnh81s7khl4opryga | Low Risk to be actioned | Risk Open | NULL | Obs16 | Testing And Maintenance | 45464 | Low | M&E Team | Please arrange for the lightning protection system to be tested | NULL
5606 | Mendell Court | MENDELL_S001 | H21 | Scheme | 2022-06-22 06:53 | FRA_5606210620222304.pdf | mitchellj1 | 5606210620222300 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 7 | 9f7lyerndp7l4opryf7 | Low Risk closed | Risk Closed | 44886.4005 | Obs15 | Management Of Fire Safety | 45464 | Low | Court Manager | Evacuation strategy : please include information regarding the evacuation strategy in residents newsletter periodically. | Every 3 months
5608 | Granville Court (Wallasey) | GRANVILLE_S001 | H21 | Scheme | 2022-05-25 16:29 | FRA_5608250520221328.pdf | mitchellj1 | 5608250520221320 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 7 | h21zi8yncz5l3lkbc8w | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45437 | Low | Court Manager | No evidence mobility scooters have been PAT tested, please ensure this has been done. | NULL
5608 | Granville Court (Wallasey) | GRANVILLE_S001 | H21 | Scheme | 2022-05-25 16:29 | FRA_5608250520221328.pdf | mitchellj1 | 5608250520221320 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 7 | jrsvjj5ge1l3lkbc7k | Medium Risk closed | Risk Closed | 44853.4227 | Obs6 | Fire Hazards - Elimination & Control | 45071 | Medium | Court Manager | Can combustible items in electric cupboard be removed/relocated Please? | Handyman completed
5608 | Granville Court (Wallasey) | GRANVILLE_S001 | H21 | Scheme | 2022-05-25 16:29 | FRA_5608250520221328.pdf | mitchellj1 | 5608250520221320 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 7 | q136g5nvqbl3lkcn0j | Low Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45437 | Low | Court Manager | Third party care staff to receive training. | NULL
5608 | Granville Court (Wallasey) | GRANVILLE_S001 | H21 | Scheme | 2022-05-25 16:29 | FRA_5608250520221328.pdf | mitchellj1 | 5608250520221320 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 7 | q0otwnnj45l3lkbc88 | Low Risk closed | Risk Closed | 44817.4887 | Obs6 | Fire Hazards - Elimination & Control | 45437 | Low | Court Manager | Can combustible in 1st floor store cupboard be stored neatly | Completed today 13.09.22
5608 | Granville Court (Wallasey) | GRANVILLE_S001 | H21 | Scheme | 2022-05-25 16:29 | FRA_5608250520221328.pdf | mitchellj1 | 5608250520221320 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 7 | ov5ctngmfil3lkbc9v | Low Risk closed | Risk Closed | 44872.5361 | Obs7 | Fire Protection Measures | 45437 | Low | Court Manager | Please arrange for holes in wall in scooter store to be repaired. | Completed boards fitted around room to protect from further damage
5608 | Granville Court (Wallasey) | GRANVILLE_S001 | H21 | Scheme | 2022-05-25 16:29 | FRA_5608250520221328.pdf | mitchellj1 | 5608250520221320 | Extra Care | Extra Care Central | EC Central 4 | North | North Patch 7 | w08vuowquhql3lkbcbl | Low Risk closed | Risk Closed | 44890.4123 | Obs10 | Fire Safety And Notices | 45437 | Low | Court Manager | Please introduce fire action notices near each call point. | New notices put in place
5701 | Normanby Court | NORMANBY_S001 | H21 | Scheme | 2022-03-01 17:23 | FRA_5701010320221603.pdf | whitek2 | 5701010320221600 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 8 | w0gyaqpp269l08bk13b | Medium Risk closed | Risk Closed | 44628.4536 | Obs7 | Fire Protection Measures | 44986 | Medium | Court Manager | Laundry room door fit sonically operated door restraint as the door is constantly being vedge open | Job loaded and completed 3/3
5701 | Normanby Court | NORMANBY_S001 | H21 | Scheme | 2022-03-01 17:23 | FRA_5701010320221603.pdf | whitek2 | 5701010320221600 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 8 | v8wp1kl3gxl08bk10n | Low Risk closed | Risk Closed | 44635.4831 | Obs6 | Fire Hazards - Elimination & Control | 45352 | Low | Court Manager | Remove and correctly dispose of paint tins stored in cupboard in the lounge | Tins now removed 15.03.22
5701 | Normanby Court | NORMANBY_S001 | H21 | Scheme | 2022-03-01 17:23 | FRA_5701010320221603.pdf | whitek2 | 5701010320221600 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 8 | y69ewbs8gnl08du5ih | Medium Risk closed | Risk Closed | 44628.4544 | Obs7 | Fire Protection Measures | 44986 | Medium | Court Manager | I have been advised that the resident of flat 35 has been keeping a mobility scooter under the block fire staircase I found no evidence of this during my inspection However I have requested that the scheme manager investigates this | Letter sent to resident advising to keep scooter in flat and not in corridor. Alternative storage options to be discussed. Will monitor and pass to new CM to check on.
5701 | Normanby Court | NORMANBY_S001 | H21 | Scheme | 2022-03-01 17:23 | FRA_5701010320221603.pdf | whitek2 | 5701010320221600 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 8 | jp6d8psc1vkl08bk124 | Medium Risk closed | Risk Closed | 44635.4199 | Obs6 | Fire Hazards - Elimination & Control | 44986 | Medium | Court Manager | Scheme Mangers Office tide up cabling possible risk of overloading electrical circuit | New extension purchased- completed 15.03.22
5701 | Normanby Court | NORMANBY_S001 | H21 | Scheme | 2022-03-01 17:23 | FRA_5701010320221603.pdf | whitek2 | 5701010320221600 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 8 | dw5cb7wj926l08bk12t | Low Risk closed | Risk Closed | 44628.4906 | Obs7 | Fire Protection Measures | 45352 | Low | Court Manager | Communal lounge door adjust door closure speed the door is slamming closed risk to elderly residents | Job raised and completed
5701 | Normanby Court | NORMANBY_S001 | H21 | Scheme | 2022-03-01 17:23 | FRA_5701010320221603.pdf | whitek2 | 5701010320221600 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 8 | 50lx9e0eu7al08bk11h | Low Risk closed | Risk Closed | 44635.4843 | Obs6 | Fire Hazards - Elimination & Control | 45352 | Low | Court Manager | Fix carbon monoxide detector on wall adjacent to gas boiler risk it could be removed/stolen | Completed 15.3.22
5703 | Hollis Court (Middlesbrough) | HOLLISMIDD_S001 | H21 | Scheme | 2022-03-01 16:02 | FRA_5703010320221010.pdf | whitek2 | 5703010320221010 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 8 | 05p0n76k83eal07ztebq | Medium Risk closed | Risk Closed | 44624.5566 | Obs8 | Measures To Limit Fire Spread And Development | 44986 | Medium | Court Manager | Flat 30 Door requires adjustment at bottom edge not closing | Job loaded and completed 4 March 2022
5704 | Cohen Court | COHEN_S001 | H21 | Scheme | 2022-01-17 12:28 | FRA_5704170120221150.pdf | whitek2 | 5704170120221150 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 8 | xg24jklklxkyimljms | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45308 | Low | Court Manager | Guest room fire door needs keep adjusting not latching | NULL
5704 | Cohen Court | COHEN_S001 | H21 | Scheme | 2022-01-17 12:28 | FRA_5704170120221150.pdf | whitek2 | 5704170120221150 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 8 | wzfxcset6dokyimljlf | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 44943 | Medium | Court Manager | Door (19) adjacent to flat 21 requires adjustment to close into rebate | NULL
5704 | Cohen Court | COHEN_S001 | H21 | Scheme | 2022-01-17 12:28 | FRA_5704170120221150.pdf | whitek2 | 5704170120221150 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 8 | vt3r4kz1rzkyimljnl | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44943 | Medium | Court Manager | Flat 34 requires missing seals replacing | NULL
5705 | Major Cooper Court | MAJORCOOP_S001 | H21 | Scheme | 2022-02-03 16:17 | FRA_5705030220221129.pdf | whitek2 | 5705030220221120 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 8 | yei69gsnblnkz6wbjff | Medium Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 44960 | Medium | Court Manager | External fire exit leading directly onto carpark re-fix fire action sign and mark clearly assembly point | NULL
5705 | Major Cooper Court | MAJORCOOP_S001 | H21 | Scheme | 2022-02-03 16:17 | FRA_5705030220221129.pdf | whitek2 | 5705030220221120 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 8 | 0phk8kkegnihkz6wbjee | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 44960 | Medium | Court Manager | Corridor fire door between flat 12 and 9 small side panel door top shoot bolt requires adjustment to hold door into rebate | NULL
5705 | Major Cooper Court | MAJORCOOP_S001 | H21 | Scheme | 2022-02-03 16:17 | FRA_5705030220221129.pdf | whitek2 | 5705030220221120 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 8 | 1n2bl7jojg2kz6wbjdm | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 44960 | Medium | Court Manager | Corridor fire door small side panel between flats 23 and 22 requires top shoot bolt adjusting to restrain panel into rebate | NULL
5705 | Major Cooper Court | MAJORCOOP_S001 | H21 | Scheme | 2022-02-03 16:17 | FRA_5705030220221129.pdf | whitek2 | 5705030220221120 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 8 | 29nmkfs6iiokz6y1w52 | Medium Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 44960 | Medium | Court Manager | Double fire doors in entrance lobby leading to lift and managers office door closer requires adjustment to ensure the doors close into rebate | NULL
5705 | Major Cooper Court | MAJORCOOP_S001 | H21 | Scheme | 2022-02-03 16:17 | FRA_5705030220221129.pdf | whitek2 | 5705030220221120 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 8 | 7p2g3btjkcmkz6wy3ku | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44960 | Medium | Court Manager | Flat 18 Door closer has been adjusted a number of times and still not latching closed the door Replace the closer | NULL
5890 | Rosaire Court and Gardens,Rosaire Court | ROSAIRE_S001 | H21 | Scheme | 2022-09-12 14:01 | FRA_5890120920221151.pdf | ComleyB | 5890120920221150 | Extra Care | Guernsey Managed Service | Guernsey Managed Service | South | South Patch 5 | 2npj6sjolnrl7yr45b9 | Low Risk closed | Risk Closed | 44819.5204 | Obs10 | Fire Safety And Notices | 45547 | Low | Court Manager | Fire exit sign to direct to nearest stairwell and exit, by flat 59. | Corrected by contractor on site.
5890 | Rosaire Court and Gardens,Rosaire Court | ROSAIRE_S001 | H21 | Scheme | 2022-09-12 14:01 | FRA_5890120920221151.pdf | ComleyB | 5890120920221150 | Extra Care | Guernsey Managed Service | Guernsey Managed Service | South | South Patch 5 | 1da7rfk4i7pil7yomxqp | Low Risk closed | Risk Closed | 44819.5146 | Obs15 | Management Of Fire Safety | 45547 | Low | Court Manager | Out of date FRA to be removed from folder. | Replaced with current FAR completed on 12.09.22
5890 | Rosaire Court and Gardens,Rosaire Court | ROSAIRE_S001 | H21 | Scheme | 2022-09-12 14:01 | FRA_5890120920221151.pdf | ComleyB | 5890120920221150 | Extra Care | Guernsey Managed Service | Guernsey Managed Service | South | South Patch 5 | evbud3ahwwul7yquqjj | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45181 | Medium | Court Manager | Stairwell door not fully closing by flat 32. | NULL
5890 | Rosaire Court and Gardens,Rosaire Court | ROSAIRE_S001 | H21 | Scheme | 2022-09-12 14:01 | FRA_5890120920221151.pdf | ComleyB | 5890120920221150 | Extra Care | Guernsey Managed Service | Guernsey Managed Service | South | South Patch 5 | d7qn5c8jd0al7yrhpaw | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45547 | Low | Court Manager | Missing smoke seal to cross-corridor doors by communal lounge. | NULL
5890 | Rosaire Court and Gardens,Rosaire Court | ROSAIRE_S001 | H21 | Scheme | 2022-09-12 14:01 | FRA_5890120920221151.pdf | ComleyB | 5890120920221150 | Extra Care | Guernsey Managed Service | Guernsey Managed Service | South | South Patch 5 | amht78trsepl7yr9r18 | Low Risk closed | Risk Closed | 44819.5195 | Obs6 | Fire Hazards - Elimination & Control | 45547 | Low | Court Manager | Collapsible wheelchair stored in communal corridor. Must remain tucked away and free from obstructing doorway or corridor. | Care staff informed that chair must remain folded and under parcel shelf and not cause obstruction but available for evacuation if needed.
5890 | Rosaire Court and Gardens,Rosaire Court | ROSAIRE_S001 | H21 | Scheme | 2022-09-12 14:01 | FRA_5890120920221151.pdf | ComleyB | 5890120920221150 | Extra Care | Guernsey Managed Service | Guernsey Managed Service | South | South Patch 5 | k5p4glgz67l7yq9u5d | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45547 | Low | Court Manager | Flat 31 front door not fully closing in rebate of frame, may require ease and adjusting. | NULL
5890 | Rosaire Court and Gardens,Rosaire Court | ROSAIRE_S001 | H21 | Scheme | 2022-09-12 14:01 | FRA_5890120920221151.pdf | ComleyB | 5890120920221150 | Extra Care | Guernsey Managed Service | Guernsey Managed Service | South | South Patch 5 | i1zsz5oh9jl7yqsgll | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45547 | Low | Court Manager | Flat 41 front door has large gap to the bottom, drop plate to be installed. | NULL
5890 | Rosaire Court and Gardens,Rosaire Court | ROSAIRE_S001 | H21 | Scheme | 2022-09-12 14:01 | FRA_5890120920221151.pdf | ComleyB | 5890120920221150 | Extra Care | Guernsey Managed Service | Guernsey Managed Service | South | South Patch 5 | o5t1vas5kjsl7yqdwcs | Low Risk closed | Risk Closed | 44819.5151 | Obs10 | Fire Safety And Notices | 45547 | Low | Court Manager | Fire exit sign to be directed to nearest stairwell, by flat 32. | Completed by contractor on 15.09.22.
5890 | Rosaire Court and Gardens,Rosaire Court | ROSAIRE_S001 | H21 | Scheme | 2022-09-12 14:01 | FRA_5890120920221151.pdf | ComleyB | 5890120920221150 | Extra Care | Guernsey Managed Service | Guernsey Managed Service | South | South Patch 5 | o6vj57uq5xsl7ypdcxn | Low Risk closed | Risk Closed | 44819.518 | Obs5 | Evacuation Strategy And Training | 45547 | Low | Court Manager | Staff training to be updated. | Last sessions completed on 21 & 22 October 21. This years sessions scheduled for 20th & 25th October 2022.
5890 | Rosaire Court and Gardens,Rosaire Court | ROSAIRE_S001 | H21 | Scheme | 2022-09-12 14:01 | FRA_5890120920221151.pdf | ComleyB | 5890120920221150 | Extra Care | Guernsey Managed Service | Guernsey Managed Service | South | South Patch 5 | ph6mesocj79l7yntdru | Medium Risk to be actioned | Risk Open | NULL | Obs1 | The Building | 45181 | Medium | Surveyor | It has been identified that there is concern of suitability of existing fire stopping. Contractor has been instructed to review alll pentrations and adequately fire stop where necessary. | NULL
5890 | Rosaire Court and Gardens,Rosaire Court | ROSAIRE_S001 | H21 | Scheme | 2022-09-12 14:01 | FRA_5890120920221151.pdf | ComleyB | 5890120920221150 | Extra Care | Guernsey Managed Service | Guernsey Managed Service | South | South Patch 5 | yrwecz7vtnl7yq2tob | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45547 | Low | Court Manager | Flat 26 front door to be replaced | NULL
5890 | Rosaire Court and Gardens,Rosaire Court | ROSAIRE_S001 | H21 | Scheme | 2022-09-12 14:01 | FRA_5890120920221151.pdf | ComleyB | 5890120920221150 | Extra Care | Guernsey Managed Service | Guernsey Managed Service | South | South Patch 5 | wva60zh1mrl7yqjwzd | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45547 | Low | Court Manager | Flat 36 front door not fully closing, may need ease and adjusting . | NULL
5890 | Rosaire Court and Gardens,Rosaire Court | ROSAIRE_S001 | H21 | Scheme | 2022-09-12 14:01 | FRA_5890120920221151.pdf | ComleyB | 5890120920221150 | Extra Care | Guernsey Managed Service | Guernsey Managed Service | South | South Patch 5 | vgtqo0nmajjl7yqlct2 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45547 | Low | Court Manager | Flat 37 missing smoke strip. | NULL
5890 | Rosaire Court and Gardens,Rosaire Court | ROSAIRE_S001 | H21 | Scheme | 2022-09-12 14:01 | FRA_5890120920221151.pdf | ComleyB | 5890120920221150 | Extra Care | Guernsey Managed Service | Guernsey Managed Service | South | South Patch 5 | w459sqf6vrl7yq51t8 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45547 | Low | Court Manager | Flat 28 front door automatic closure not operating. Closure may need replacing. | NULL
5890 | Rosaire Court and Gardens,Rosaire Court | ROSAIRE_S001 | H21 | Scheme | 2022-09-12 14:01 | FRA_5890120920221151.pdf | ComleyB | 5890120920221150 | Extra Care | Guernsey Managed Service | Guernsey Managed Service | South | South Patch 5 | ws2iddxavtl7yqno3a | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45547 | Low | Court Manager | Flat 40 front door requires drop plate to cover large gap at the bottom. | NULL
5901 | Inglis Court | INGLIS_S001 | H21 | Scheme | 2022-08-31 08:45 | FRA_5901310820220844.pdf | taylors1 | 5901310820220840 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 2 | 97n72ce3recl7hbbpin | Low Risk closed | Risk Closed | 44816.4781 | Obs10 | Fire Safety And Notices | 45535 | Low | Court Manager | Provide fire action notices to lobby, rear lobby, rear guest room door | fire action plans out up around communal areas
5901 | Inglis Court | INGLIS_S001 | H21 | Scheme | 2022-08-31 08:45 | FRA_5901310820220844.pdf | taylors1 | 5901310820220840 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 2 | btb884nyoo7l7hbbpjj | Low Risk closed | Risk Closed | 44804.4123 | Obs15 | Management Of Fire Safety | 45535 | Low | Court Manager | Add copy of fire zone plan into fire box folder | Photocopied fire zone plan off the wall and placed a copy in the red fire box folder.
5901 | Inglis Court | INGLIS_S001 | H21 | Scheme | 2022-08-31 08:45 | FRA_5901310820220844.pdf | taylors1 | 5901310820220840 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 2 | 0a4sgk315ycel7hbbpgn | Low Risk closed | Risk Closed | 44804.4552 | Obs8 | Measures To Limit Fire Spread And Development | 45535 | Low | Court Manager | Adjust closer to flat 9 | Raised a job for PPM to adjust closer to flat 9.
5901 | Inglis Court | INGLIS_S001 | H21 | Scheme | 2022-08-31 08:45 | FRA_5901310820220844.pdf | taylors1 | 5901310820220840 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 2 | 6vw1rr8jl0il7hbbphm | Medium Risk closed | Risk Closed | 44811.6776 | Obs9 | Escape Lighting | 44807 | Medium | Surveyor | Emergency lighting required throughout the communal areas | Lighting is being tied in with internal alterations due to SOS early oct
5902 | Lonsdale Court | LONSDALE_S001 | H21 | Scheme | 2022-09-20 14:38 | FRA_5902200920221424.pdf | taylors1 | 5902200920221420 | Extra Care | Extra Care North | EC North 4 | North | North Patch 2 | 6ckiu546cd5l8a89m1x | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45555 | Low | Court Manager | Adjust door closer to shut onto frame cross corridor door adjacent to flat 17 | NULL
5902 | Lonsdale Court | LONSDALE_S001 | H21 | Scheme | 2022-09-20 14:38 | FRA_5902200920221424.pdf | taylors1 | 5902200920221420 | Extra Care | Extra Care North | EC North 4 | North | North Patch 2 | 1gcf2m3u55jl8a89m31 | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45555 | Low | Court Manager | Pack bottom hinge to reduce closing edge gap flat 27 | NULL
5902 | Lonsdale Court | LONSDALE_S001 | H21 | Scheme | 2022-09-20 14:38 | FRA_5902200920221424.pdf | taylors1 | 5902200920221420 | Extra Care | Extra Care North | EC North 4 | North | North Patch 2 | 1jdumydn817l8a89m1a | Medium Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45189 | Medium | Court Manager | Petrol lawnmower and strimmer stored in refuse room with half full petrol container must be removed to external store or off site | NULL
5902 | Lonsdale Court | LONSDALE_S001 | H21 | Scheme | 2022-09-20 14:38 | FRA_5902200920221424.pdf | taylors1 | 5902200920221420 | Extra Care | Extra Care North | EC North 4 | North | North Patch 2 | ktjzawt39drl8a89m2i | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45189 | Medium | Court Manager | S&F intumescent vent to replace existing vent in door leading into kitchen from dining room | NULL
5903 | John Gaskell Court | JOHNGASK_S001 | H21 | Scheme | 2022-01-10 17:14 | FRA_5903100120221700.pdf | taylors1 | 5903100120221700 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 1 | jw7np0q9igkky8xl901 | Low Risk closed | Risk Closed | 44875.6192 | Obs8 | Measures To Limit Fire Spread And Development | 45301 | Low | Court Manager | Flat 26 adjust keep to door to close tight to rebate pack with intumescent packers to reduce gap on closing edge | New fire door fitted 01/11/2022
5903 | John Gaskell Court | JOHNGASK_S001 | H21 | Scheme | 2022-01-10 17:14 | FRA_5903100120221700.pdf | taylors1 | 5903100120221700 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 1 | n1k4rgct0xsky8xl94c | Medium Risk closed | Risk Closed | 44572.4838 | Obs10 | Fire Safety And Notices | 44936 | Medium | Court Manager | Assembly point requires 're writing onto fire action notices throughout the building | All Assembly points have been re written on with top of car park
5903 | John Gaskell Court | JOHNGASK_S001 | H21 | Scheme | 2022-01-10 17:14 | FRA_5903100120221700.pdf | taylors1 | 5903100120221700 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 1 | p6cvx819c9iky8xl93a | Low Risk closed | Risk Closed | 44574.4433 | Obs8 | Measures To Limit Fire Spread And Development | 45301 | Low | Court Manager | Adjust door closer to ensure door closes into rebate on cross corridor door adjacent to flat 18 | Joiner attended and adjusted to ensure the door closes into rebate
5903 | John Gaskell Court | JOHNGASK_S001 | H21 | Scheme | 2022-01-10 17:14 | FRA_5903100120221700.pdf | taylors1 | 5903100120221700 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 1 | o4wfl6zlkinky8xl8yh | High Risk Closed | Risk Closed | 44629.6582 | Obs8 | Measures To Limit Fire Spread And Development | 44333 | High | Surveyor | Full bolster survey of roof void area required following initial finding from this a previous FRA | Order placed with CLC survey completed 4.3.22
5903 | John Gaskell Court | JOHNGASK_S001 | H21 | Scheme | 2022-01-10 17:14 | FRA_5903100120221700.pdf | taylors1 | 5903100120221700 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 1 | nbvm7u1q41ky8xl91g | High Risk Closed | Risk Closed | 44680.6776 | Obs8 | Measures To Limit Fire Spread And Development | 44661 | High | Surveyor | No fire break above cross corridor frame head above ceiling adj flat 32 | Full bolster survey ordered via CLC
5903 | John Gaskell Court | JOHNGASK_S001 | H21 | Scheme | 2022-01-10 17:14 | FRA_5903100120221700.pdf | taylors1 | 5903100120221700 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 1 | 1jhiyw99z74jky8xl8z7 | High Risk Closed | Risk Closed | 44629.6593 | Obs8 | Measures To Limit Fire Spread And Development | 44333 | High | Surveyor | Above all cross corridor door sets leading to staircase Moe adjacent to flat 38 no compartmentation above frame | Full bolster survey has been ordered with CLC survey element completed further inspection arranged on site with B.S. and CLC 18.3.22
5903 | John Gaskell Court | JOHNGASK_S001 | H21 | Scheme | 2022-01-10 17:14 | FRA_5903100120221700.pdf | taylors1 | 5903100120221700 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 1 | 3ftn75qmnk2ky8xl90o | High Risk Closed | Risk Closed | 44624.3687 | Obs8 | Measures To Limit Fire Spread And Development | 44661 | High | Court Manager | Refix perko closer screws missing from all three hinges | Screws replaced on the 03/03/2022
5903 | John Gaskell Court | JOHNGASK_S001 | H21 | Scheme | 2022-01-10 17:14 | FRA_5903100120221700.pdf | taylors1 | 5903100120221700 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 1 | 544b4u23sinky8xl92q | Low Risk closed | Risk Closed | 44574.4423 | Obs8 | Measures To Limit Fire Spread And Development | 45301 | Low | Court Manager | Flat 17 pack with intumescent packers to reduce gap on closing edge | Job raised, joiner attended same day gap reduced with intumescent packers.
5903 | John Gaskell Court | JOHNGASK_S001 | H21 | Scheme | 2022-01-10 17:14 | FRA_5903100120221700.pdf | taylors1 | 5903100120221700 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 1 | xiaw8ni287pky8xl926 | Medium Risk closed | Risk Closed | 44657.3922 | Obs8 | Measures To Limit Fire Spread And Development | 44936 | Medium | Court Manager | Refix smoke seal to cross corridor door adjacent to flat 32 on closing edge | Job completed on the 06/04/2022 delay due to parts needing to be ordered.
5903 | John Gaskell Court | JOHNGASK_S001 | H21 | Scheme | 2022-01-10 17:14 | FRA_5903100120221700.pdf | taylors1 | 5903100120221700 | Retirement Housing | North East | Durham Cleveland and Cumbria | North | North Patch 1 | xsjpypvuupky8xl8wa | Low Risk closed | Risk Closed | 44574.6738 | Obs2 | Means Of Giving Warning In Case Of Fire | 45301 | Low | Surveyor | Has rezoning been completed ? A clear Fire zone plan is required | Court manager arranging with contractor directly open view
5905 | Newton House | NEWTONHOUSE_S001 | H21 | Scheme | 2022-09-27 11:15 | FRA_5905270920221105.pdf | taylors1 | 5905270920221100 | Extra Care | Extra Care North | EC North 4 | North | North Patch 1 | eqrt2a8lswwl8k19iml | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45562 | Low | Court Manager | Refix closing edge stop lath to frame to laundry | NULL
5905 | Newton House | NEWTONHOUSE_S001 | H21 | Scheme | 2022-09-27 11:15 | FRA_5905270920221105.pdf | taylors1 | 5905270920221100 | Extra Care | Extra Care North | EC North 4 | North | North Patch 1 | oypclmqsf7al8k1a6s8 | Observation Only | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | NULL | N/A | Court Manager | HCM advised to include copy of zone plan into fire box | NULL
8401 | Bechers Court | BECHERSCOURT_S001 | H21 | Scheme | 2022-03-03 12:04 | FRA_8401030320220821.pdf | ClarkG | 8401030320220820 | Retirement Housing | Mid East | Merseyside | North | North Patch 3 | 8fj0w143nucl0aqhrzs | Observation Only | Risk Closed | 44664.6556 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire Alarm is reported via the Tunstall system. | No action required
8402 | Beechcroft | BEECHCROFT_S001 | H21 | Scheme | 2022-03-04 13:04 | FRA_8402040320220832.pdf | ClarkG | 8402040320220830 | Retirement Housing | Mid East | Merseyside | North | North Patch 3 | kb9ht7fjyhnl0c6ea8c | Observation Only | Risk Closed | 44664.6558 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire Alarm is linked to the Warden Call system. | No action required
8403 | Brookview | BROOKVIEW_S001 | H21 | Scheme | 2022-10-26 16:14 | FRA_8403261020221520.pdf | ClarkG | 8403261020221520 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 3 | hvi1ax8c18rl9pqr5di | Low Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45591 | Low | Court Manager | Install break glass to hold key for red fire box. | NULL
8403 | Brookview | BROOKVIEW_S001 | H21 | Scheme | 2022-10-26 16:14 | FRA_8403261020221520.pdf | ClarkG | 8403261020221520 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 3 | hu60dic139tl9pqkmjq | Observation Only | Risk Closed | 44861.5858 | Obs2 | Means Of Giving Warning In Case Of Fire | NULL | N/A | Surveyor | Fire Alarm System is currently having repairs to the board organised with Openview to allow connection with Appello. | No action required
8403 | Brookview | BROOKVIEW_S001 | H21 | Scheme | 2022-10-26 16:14 | FRA_8403261020221520.pdf | ClarkG | 8403261020221520 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 3 | nk9n36nihdl9pqoih9 | Low Risk to be actioned | Risk Open | NULL | Obs5 | Evacuation Strategy And Training | 45591 | Low | Court Manager | Leaseholders and Court fire plan to be revised of the fire strategy. | NULL
8403 | Brookview | BROOKVIEW_S001 | H21 | Scheme | 2022-10-26 16:14 | FRA_8403261020221520.pdf | ClarkG | 8403261020221520 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 3 | c1yb9w3ypurl9prxvg4 | Observation Only | Risk Open | NULL | Obs16 | Testing And Maintenance | NULL | N/A | Court Manager | Smoke Extraction system is checked each week when the fire alarm system are checked. | NULL
8403 | Brookview | BROOKVIEW_S001 | H21 | Scheme | 2022-10-26 16:14 | FRA_8403261020221520.pdf | ClarkG | 8403261020221520 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 3 | zbzhm0iz6eal9prbsvk | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45591 | Low | Court Manager | Remove wedge to communal lounge door and install a battery operated door guard. | NULL
8407 | Chevin Court | CHEVINCOURT_S001 | H21 | Scheme | 2021-08-11 14:50 | FRA_8407110820210930.pdf | lofthousei | 8407110820210930 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 4 | zb57y6jz1qks7jjo70 | Observation Only | Risk Open | NULL | Obs7 | Fire Protection Measures | NULL | N/A | Surveyor | NB first floor flats in block 1 (flats 5 to 8) only escape route is via bridge link to block 2. Distance of travel is acceptable. , but no alternative MoE other than via windows. | NULL
8407 | Chevin Court | CHEVINCOURT_S001 | H21 | Scheme | 2021-08-11 14:50 | FRA_8407110820210930.pdf | lofthousei | 8407110820210930 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 4 | ytkkkpyk49dks7dk357 | Low Risk closed | Risk Closed | 44420.4637 | Obs8 | Measures To Limit Fire Spread And Development | 45149 | Low | Court Manager | Doorvto Guest Room wedged open | Removed wedge
8407 | Chevin Court | CHEVINCOURT_S001 | H21 | Scheme | 2021-08-11 14:50 | FRA_8407110820210930.pdf | lofthousei | 8407110820210930 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 4 | d99b6pwtx7sks7jpfxt | Observation Only | Risk Closed | 44420.4645 | Obs11 | Fire Fighting Equipment | NULL | N/A | Court Manager | Provision of Fire Extinguishers is excessive. Only required in hazard areas and at final exit locations. Do not need to double up water and foam type - consider reducing numbers and disposing of water type | I have spoken to Chevin courts directors and we will investigate which extinguishers we can remove.
8407 | Chevin Court | CHEVINCOURT_S001 | H21 | Scheme | 2021-08-11 14:50 | FRA_8407110820210930.pdf | lofthousei | 8407110820210930 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 4 | ekird0mklcuks7d3qdf | Observation Only | Risk Closed | 44420.4654 | Obs10 | Fire Safety And Notices | NULL | N/A | Court Manager | Mixture of Fire Action Notices, consider standardising to the simple red, blue and white sign. See photos. Supply and fit recommended FAN at all manual call points. | I have spoken with our directors and we will order new signs.
8407 | Chevin Court | CHEVINCOURT_S001 | H21 | Scheme | 2021-08-11 14:50 | FRA_8407110820210930.pdf | lofthousei | 8407110820210930 | Retirement Housing | Yorks Lancs | West Yorkshire | North | North Patch 4 | 41orgiocz9wks7cn6k2 | Low Risk to be actioned | Risk Open | NULL | Obs11 | Fire Fighting Equipment | 45149 | Low | M&E Team | FEE not Housing 21 P50 specification, and previously serviced under contract via GEL service. M&E team to arrange service or advise CM to replace with P50 type. | NULL
8409 | Fitzwarren House | FITZWARREN_S001 | H21 | Scheme | 2022-07-01 10:46 | FRA_8409010720220820.pdf | mayesd | 8409010720220820 | Retirement Housing | London Kent | North and East London | Central | Central Patch 1 | 4zn5ja9rufwl526dc7n | Medium Risk closed | Risk Closed | 44880.4116 | Obs5 | Evacuation Strategy And Training | 45108 | Medium | Court Manager | Training needs to be completed by the court managers asap | completed
8409 | Fitzwarren House | FITZWARREN_S001 | H21 | Scheme | 2022-07-01 10:46 | FRA_8409010720220820.pdf | mayesd | 8409010720220820 | Retirement Housing | London Kent | North and East London | Central | Central Patch 1 | 6vo7gpquvldl5276g0c | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45108 | Medium | Court Manager | Flat 11 requires a smoke seal at the base of the door | NULL
8409 | Fitzwarren House | FITZWARREN_S001 | H21 | Scheme | 2022-07-01 10:46 | FRA_8409010720220820.pdf | mayesd | 8409010720220820 | Retirement Housing | London Kent | North and East London | Central | Central Patch 1 | 7gqhudcyjgxl528hhjz | Medium Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45108 | Medium | Court Manager | On completion of the fire alarm upgrade the fire action notices require updating to the correct version | NULL
8409 | Fitzwarren House | FITZWARREN_S001 | H21 | Scheme | 2022-07-01 10:46 | FRA_8409010720220820.pdf | mayesd | 8409010720220820 | Retirement Housing | London Kent | North and East London | Central | Central Patch 1 | f9872najunml5278xbz | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45108 | Medium | Court Manager | Generally all communal doors and flat entrance doors require a smoke seal at the base of the door | NULL
8409 | Fitzwarren House | FITZWARREN_S001 | H21 | Scheme | 2022-07-01 10:46 | FRA_8409010720220820.pdf | mayesd | 8409010720220820 | Retirement Housing | London Kent | North and East London | Central | Central Patch 1 | d8j6r35kmnwl529kz8e | Medium Risk to be actioned | Risk Open | NULL | Obs2 | Means Of Giving Warning In Case Of Fire | 45108 | Medium | Surveyor | The cause and effect will need to be considered to alert flats directly above the basement rooms in the event of an a activation | NULL
8409 | Fitzwarren House | FITZWARREN_S001 | H21 | Scheme | 2022-07-01 10:46 | FRA_8409010720220820.pdf | mayesd | 8409010720220820 | Retirement Housing | London Kent | North and East London | Central | Central Patch 1 | 9j24n8bybngl5274kr0 | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45108 | Medium | Court Manager | Flat 12 requires a smoke seal at the base of the door | NULL
8409 | Fitzwarren House | FITZWARREN_S001 | H21 | Scheme | 2022-07-01 10:46 | FRA_8409010720220820.pdf | mayesd | 8409010720220820 | Retirement Housing | London Kent | North and East London | Central | Central Patch 1 | sm3ug3mefokl528co4f | Observation Only | Risk Open | NULL | Obs11 | Fire Fighting Equipment | NULL | N/A | Court Manager | Fire extinguishers have been serviced and functional but do are not aligned to the P50 type. Consider updating the extinguishers in the future | NULL
8409 | Fitzwarren House | FITZWARREN_S001 | H21 | Scheme | 2022-07-01 10:46 | FRA_8409010720220820.pdf | mayesd | 8409010720220820 | Retirement Housing | London Kent | North and East London | Central | Central Patch 1 | hnkjmsq37esl5269pxy | Medium Risk to be actioned | Risk Open | NULL | Obs4 | The Occupant - Information Provided By The Court Manager | 45108 | Medium | Court Manager | Fire safety management documents requires updating to current version | NULL
8409 | Fitzwarren House | FITZWARREN_S001 | H21 | Scheme | 2022-07-01 10:46 | FRA_8409010720220820.pdf | mayesd | 8409010720220820 | Retirement Housing | London Kent | North and East London | Central | Central Patch 1 | kyvm8vqt0ul526yz77 | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45108 | Medium | Court Manager | Flat 9 requires a smoke seal at the base of the door | NULL
8409 | Fitzwarren House | FITZWARREN_S001 | H21 | Scheme | 2022-07-01 10:46 | FRA_8409010720220820.pdf | mayesd | 8409010720220820 | Retirement Housing | London Kent | North and East London | Central | Central Patch 1 | m5kk4k7hkpnl526x21t | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45108 | Medium | Court Manager | Flat 8 front door requires a smoke seal at the base | NULL
8409 | Fitzwarren House | FITZWARREN_S001 | H21 | Scheme | 2022-07-01 10:46 | FRA_8409010720220820.pdf | mayesd | 8409010720220820 | Retirement Housing | London Kent | North and East London | Central | Central Patch 1 | lgwpjo0zug9l527kudk | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45108 | Medium | Court Manager | Flat 17 requires a smoke seal at the base of the door | NULL
8411 | Hamilton Court | HAMILTON_S001 | H21 | Scheme | 2022-03-25 12:56 | FRA_8411250320221125.pdf | ClarkG | 8411250320221120 | Retirement Housing | Mid East | Merseyside | North | North Patch 3 | m5uues7m8rbl16dwj07 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45376 | Low | Court Manager | Fire stopping required in first floor switch room | NULL
8411 | Hamilton Court | HAMILTON_S001 | H21 | Scheme | 2022-03-25 12:56 | FRA_8411250320221125.pdf | ClarkG | 8411250320221120 | Retirement Housing | Mid East | Merseyside | North | North Patch 3 | j0myx7s5b6ql16dh8wz | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 44997 | Low | Court Manager | Pink fire foam above communal fire doors. Pink fire foam to be raked out and replaced with correct fire stopping materials. Link Fire Safety to assess and provide quote for works. | NULL
8411 | Hamilton Court | HAMILTON_S001 | H21 | Scheme | 2022-03-25 12:56 | FRA_8411250320221125.pdf | ClarkG | 8411250320221120 | Retirement Housing | Mid East | Merseyside | North | North Patch 3 | fmallv7fixhl16d3c0e | Observation Only | Risk Open | NULL | Obs15 | Management Of Fire Safety | NULL | N/A | Court Manager | All weekly and monthly checks are being completed on the tablet and recorded electronically. We would recommend that the forms in the Red Fire folder are also completed with these checks. | NULL
8411 | Hamilton Court | HAMILTON_S001 | H21 | Scheme | 2022-03-25 12:56 | FRA_8411250320221125.pdf | ClarkG | 8411250320221120 | Retirement Housing | Mid East | Merseyside | North | North Patch 3 | u9318bak3qll16c7bnc | Observation Only | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Surveyor | A full fire risk inspection of all the flat doors has been instructed to be carried out by Link Fire Safety to confirm if these are 30 minute fire doors. As requested by Cheshire Fire and Rescue. | NULL
8411 | Hamilton Court | HAMILTON_S001 | H21 | Scheme | 2022-03-25 12:56 | FRA_8411250320221125.pdf | ClarkG | 8411250320221120 | Retirement Housing | Mid East | Merseyside | North | North Patch 3 | cuu0hkofgdvl16dzrgd | Observation Only | Risk Open | NULL | Obs7 | Fire Protection Measures | NULL | N/A | Court Manager | Items stored outside residents flats. We would recommend that these are left sterile or items are non-flammable or possible trip hazards. | NULL
8411 | Hamilton Court | HAMILTON_S001 | H21 | Scheme | 2022-03-25 12:56 | FRA_8411250320221125.pdf | ClarkG | 8411250320221120 | Retirement Housing | Mid East | Merseyside | North | North Patch 3 | exox8j57q4ul16c7bmj | Observation Only | Risk Open | NULL | Obs1 | The Building | NULL | N/A | Surveyor | A full fire risk compartmentation survey has been organised with Link Fire Safety to ensure all compartmentation wall are correctly fire stopped, as requested by Cheshire Fire & Rescue services. | NULL
8411 | Hamilton Court | HAMILTON_S001 | H21 | Scheme | 2022-03-25 12:56 | FRA_8411250320221125.pdf | ClarkG | 8411250320221120 | Retirement Housing | Mid East | Merseyside | North | North Patch 3 | 0y63tfxilw6l16dqmk6 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45376 | Low | Court Manager | Internal Glass Windows to communal lounge and managers office is not fire rated. Need to remove and replaced with fire rated glass. | NULL
8411 | Hamilton Court | HAMILTON_S001 | H21 | Scheme | 2022-03-25 12:56 | FRA_8411250320221125.pdf | ClarkG | 8411250320221120 | Retirement Housing | Mid East | Merseyside | North | North Patch 3 | 0kj3rl047kql16e4i59 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45376 | Low | Court Manager | Foam in second floor switch room requires removing and replacing with fire rated materials | NULL
8411 | Hamilton Court | HAMILTON_S001 | H21 | Scheme | 2022-03-25 12:56 | FRA_8411250320221125.pdf | ClarkG | 8411250320221120 | Retirement Housing | Mid East | Merseyside | North | North Patch 3 | zhvj8vgi6o7l16er8a2 | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45376 | Low | Court Manager | Fire stopping required in Bin store room | NULL
8413 | Parkside Court | PARKSIDECOURT_S001 | H21 | Scheme | 2022-05-18 13:33 | FRA_8413180520221111.pdf | ClarkG | 8413180520221110 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 3 | 4v44b59f7yql3bigg75 | Low Risk closed | Risk Closed | 44778.4138 | Obs7 | Fire Protection Measures | 45067 | Low | Court Manager | Lift motor room - Fire stopping by expandable foam, needs racking out and replacing with fire rated materials. Job raised with CLC | CLC completed the job
8413 | Parkside Court | PARKSIDECOURT_S001 | H21 | Scheme | 2022-05-18 13:33 | FRA_8413180520221111.pdf | ClarkG | 8413180520221110 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 3 | 449z8pxx96sl3bim9ft | Low Risk closed | Risk Closed | 44778.4141 | Obs7 | Fire Protection Measures | 45430 | Low | Court Manager | Door closers required to the kitchen and Electrical meter room. | Completed by CLC
8413 | Parkside Court | PARKSIDECOURT_S001 | H21 | Scheme | 2022-05-18 13:33 | FRA_8413180520221111.pdf | ClarkG | 8413180520221110 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 3 | 9cvs6jepluwl3bi8omv | Low Risk closed | Risk Closed | 44746.4076 | Obs7 | Fire Protection Measures | 45067 | Low | Court Manager | Fire stopping above communal doors is with expandable foam, this needs racking out and replacing with fire rated materials. An order has been raised with CLC. | This was replaced by CLC
8413 | Parkside Court | PARKSIDECOURT_S001 | H21 | Scheme | 2022-05-18 13:33 | FRA_8413180520221111.pdf | ClarkG | 8413180520221110 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 3 | nhooab58u6l3bjzcnq | Low Risk closed | Risk Closed | 44746.4108 | Obs1 | The Building | 45430 | Low | Court Manager | Fire stopping in loft space with expandable foam, this needs racking out and replacing with fire rated materials. | This was replaced by CLC WORK COMPLETE
8413 | Parkside Court | PARKSIDECOURT_S001 | H21 | Scheme | 2022-05-18 13:33 | FRA_8413180520221111.pdf | ClarkG | 8413180520221110 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 3 | pvrmbzbnxkl3bj40im | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45430 | Low | Court Manager | Flat 36, 35, 52 - Re-fix perko detection | NULL
8413 | Parkside Court | PARKSIDECOURT_S001 | H21 | Scheme | 2022-05-18 13:33 | FRA_8413180520221111.pdf | ClarkG | 8413180520221110 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 3 | fl5es6299qsl3bgsu2d | Low Risk closed | Risk Closed | 44729.6417 | Obs4 | The Occupant - Information Provided By The Court Manager | 45430 | Low | Court Manager | Scheme manager to have PCFRA training on the 9th June 2022 | Attended training with my OM
8413 | Parkside Court | PARKSIDECOURT_S001 | H21 | Scheme | 2022-05-18 13:33 | FRA_8413180520221111.pdf | ClarkG | 8413180520221110 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 3 | iip9omzda8ql3bjpply | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45430 | Low | Court Manager | Flat 25 - Re-install Overhead self closing device installed | NULL
8414 | Penrhyn Court | PENRHYNCOURT_S001 | H21 | Scheme | 2022-03-11 12:29 | FRA_8414100320221438.pdf | JohnsonD | 8414100320221430 | Retirement Housing | Mid West | Cheshire and Lancashire | North | North Patch 3 | 2q6wvru5m95l0ma9763 | Medium Risk closed | Risk Closed | 44670.3861 | Obs8 | Measures To Limit Fire Spread And Development | 44996 | Medium | Court Manager | There are a number of flats where Leaseholders have removed the self closers due to weight. Please write to Leaseholders to advise them to have these re fitted. | I have the Residents to replace the self closers
8415 | Renaissance | RENAISSANCE_S001 | H21 | Scheme | 2022-03-10 14:24 | FRA_8415100320221359.pdf | JohnsonD | 8415100320221350 | Retirement Housing | Mid East | Merseyside | North | North Patch 3 | z40eu4adaxl0l2qq39 | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44995 | Medium | Court Manager | A number of flat doors have had door closers removed by Leaseholders. I have advised the Court Manager to request these are refitted. | NULL
8416 | Southlands | SOUTHLANDS_S001 | H21 | Scheme | 2022-08-23 11:40 | FRA_8416230820220943.pdf | lofthousei | 8416230820220940 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 4 | 271ujihaccql75xwq4o | Medium Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45161 | Medium | Court Manager | Door to lift motor room not adequately fire rated, requires upgrade to FD60S | NULL
8416 | Southlands | SOUTHLANDS_S001 | H21 | Scheme | 2022-08-23 11:40 | FRA_8416230820220943.pdf | lofthousei | 8416230820220940 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 4 | 0llto1puf29l75xwq3n | Medium Risk Overdue | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 44817 | Medium | Court Manager | No compartmentation between external store and internal electric meter cupboard. | NULL
8416 | Southlands | SOUTHLANDS_S001 | H21 | Scheme | 2022-08-23 11:40 | FRA_8416230820220943.pdf | lofthousei | 8416230820220940 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 4 | hk0l35l89bkl75xwq5g | Medium Risk Overdue | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44817 | Medium | Court Manager | No compartmentation between external store and internal electric meter cupboard | NULL
8416 | Southlands | SOUTHLANDS_S001 | H21 | Scheme | 2022-08-23 11:40 | FRA_8416230820220943.pdf | lofthousei | 8416230820220940 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 4 | kopyax9z2yal75xx0lx | Low Risk to be actioned | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 45527 | Low | Court Manager | Evidence self closers to flat entrance doors have been removed or disabled. Residents to be advised all doors opening onto protected escape route must have a working self closer and not wedged open. | NULL
8417 | Stansfield Court | STANSFIELD_S001 | H21 | Scheme | 2022-08-17 13:35 | FRA_8417170820220855.pdf | lofthousei | 8417170820220850 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 4 | 4j2gpxkxmv3l6xezcnx | Low Risk closed | Risk Closed | 44827.74 | Obs6 | Fire Hazards - Elimination & Control | 45171 | Low | Court Manager | Furniture and clothes aired in stairwells serving flats 8 to 10, should be removed due to fire load on escape route | letter posted 34/09/22 to residents asking for items to be removed J Robson OM
8417 | Stansfield Court | STANSFIELD_S001 | H21 | Scheme | 2022-08-17 13:35 | FRA_8417170820220855.pdf | lofthousei | 8417170820220850 | Retirement Housing | North East | North and East Yorkshire and NE Lincs | North | North Patch 4 | d8867pvihfkl6xeqlex | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45171 | Low | Court Manager | Electric meter cupboards on escape route not fire resistant construction | NULL
8418 | Stoneygate Court | STONEYGATE_S001 | H21 | Scheme | 2022-05-19 14:55 | FRA_8418190520221321.pdf | ClarkG | 8418190520221320 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 9 | c8j2rsc5wwnl3d0nbn6 | Observation Only | Risk Closed | 44707.7077 | Obs9 | Escape Lighting | NULL | N/A | Surveyor | No Emergency Lighting in the communal areas. | No action required
8418 | Stoneygate Court | STONEYGATE_S001 | H21 | Scheme | 2022-05-19 14:55 | FRA_8418190520221321.pdf | ClarkG | 8418190520221320 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 9 | 75tmdm75sfyl3czpyiv | Observation Only | Risk Closed | 44707.7079 | Obs1 | The Building | NULL | N/A | Surveyor | No Communal Roof voids. | No action required
8418 | Stoneygate Court | STONEYGATE_S001 | H21 | Scheme | 2022-05-19 14:55 | FRA_8418190520221321.pdf | ClarkG | 8418190520221320 | Retirement Housing | Yorks Lancs | Lancashire | North | North Patch 9 | pmle6ujsjfrl3d0l0p9 | Observation Only | Risk Closed | 44700.6695 | Obs8 | Measures To Limit Fire Spread And Development | NULL | N/A | Surveyor | No Flat Doors on this scheme. | No action required
8419 | The Highlands | HIGHLANDS_S001 | H21 | Scheme | 2022-03-30 17:33 | FRA_8419300320221711.pdf | mitchellj1 | 8419300320221710 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 7 | qksyv6ddvktl1drmwyu | Low Risk to be actioned | Risk Open | NULL | Obs7 | Fire Protection Measures | 45022 | Low | Other | Fire exit at bottom of central stairwell leads to a short flight of steps, a safer egress route would be a protected ramp, Leasehold management team to discuss with leaseholders. | NULL
8419 | The Highlands | HIGHLANDS_S001 | H21 | Scheme | 2022-03-30 17:33 | FRA_8419300320221711.pdf | mitchellj1 | 8419300320221710 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 7 | i6410ephd9ml1drmx0a | Medium Risk Overdue | Risk Open | NULL | Obs8 | Measures To Limit Fire Spread And Development | 44658 | Medium | Other | Flats 12, 29, 31 have no door closer, it should be arranged for all flat entrance doors to have closers installed. | NULL
8419 | The Highlands | HIGHLANDS_S001 | H21 | Scheme | 2022-03-30 17:33 | FRA_8419300320221711.pdf | mitchellj1 | 8419300320221710 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 7 | fwzwoe266bl1drmx1w | Low Risk to be actioned | Risk Open | NULL | Obs16 | Testing And Maintenance | 45381 | Low | M&E Team | Storage heaters in communal areas have PAT test label indicating they were last PAT tested in 2019, please arrange for this to be done. | NULL
8419 | The Highlands | HIGHLANDS_S001 | H21 | Scheme | 2022-03-30 17:33 | FRA_8419300320221711.pdf | mitchellj1 | 8419300320221710 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 7 | exgzefkerekl1ds50o2 | Low Risk to be actioned | Risk Open | NULL | Obs10 | Fire Safety And Notices | 45381 | Low | Court Manager | Fire action notices to be changed as they don't support the alarm configuration as they instruct residents to leave if they hear the alarm in their flat. | NULL
8419 | The Highlands | HIGHLANDS_S001 | H21 | Scheme | 2022-03-30 17:33 | FRA_8419300320221711.pdf | mitchellj1 | 8419300320221710 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 7 | 8o106ukvm9ql1drmwzh | Observation Only | Risk Open | NULL | Obs7 | Fire Protection Measures | NULL | N/A | Surveyor | Fire exit door to side car park opens inwards. | NULL
8419 | The Highlands | HIGHLANDS_S001 | H21 | Scheme | 2022-03-30 17:33 | FRA_8419300320221711.pdf | mitchellj1 | 8419300320221710 | Retirement Housing | Mid East | South Yorkshire and South Manchester | North | North Patch 7 | vw176wzgrwl1drmwxu | Low Risk to be actioned | Risk Open | NULL | Obs6 | Fire Hazards - Elimination & Control | 45023 | Low | Other | Bins are being stored under Timber soffit to the side of the building, the bins should be relocated away from the building. | NULL